## GCS Assessment
GCS Assessment | [14 empty] | GCS PARAMETERS
[16 empty] | Low Lim | Middle Lim | High Lim | Oxygen | Nitrogen
[12 empty] | Wells Offline | 71 |  | Methane | 35 | 50 | 55 | 21 | 79
[12 empty] | Wells Shut In | 31 |  | Oxygen | 1 | 5 | 15 | Ratio | 3.7619
[12 empty] | Wells Blocked | 40 |  | Vacuum | -10 | -2
Previous Readings | [11 empty] | Wells Damaged | 0 |  | Differential | 0.5 | 10 | 20
Date: | [11 empty] | Choose File Type for Balancing Plan: |  |  | Flow | 10 | 20 | 30
[12 empty] | CV Reads |  |  | Valve Pos | 10 |  | 75
ID | DATE | CH4 | CO2 | O2 | BALANCE | INI-SP | INI-DP | INI-FLOW | ANSWER 2 | CHOSEN 1 | WELL BALANCE RATIO |  |  | rungas Export
BGW2E356 | 2019-03-18 10:01 | 36.4 | 27.1 | 5.5 | 31 | -0.5 | 0.442 | 5.8 | 5 | Adjusted Decrease | 5.6364 |  |  | rungas Import
BGW2E357 | 2019-03-18 10:06 | 45.4 | 33.1 | 2.1 | 19.4 | -1.6 | 2.567 | 14 | 5 | Adjusted Decrease | 9.2381 |  |  | CV Reads
BHW2F416 | 2019-03-18 10:08 | 47.4 | 36.9 | 0.4 | 15.3 | -26.3 | 1.817 | 40.4 | 50 | Surge | 38.25 |  |  | Header Reads
BGW2F358 | 2019-03-18 10:10 | 36.5 | 32.9 | 1.4 | 29.2 | -0.9 | 0.799 | 7.6 | 5 | Adjusted Decrease | 20.8571 |  |  | Well Reads
BGW2C355 | 2019-03-18 10:14 | 48.6 | 36.1 | 1.7 | 13.6 | -17.9 | 12.286 | 106.2 | 70 | Adjusted Decrease | 8
BGW2C394 | 2019-03-18 10:15 | 47.6 | 35.7 | 0 | 16.7 | -13.8 | 3.673 | 58.5 | 50 | OK- No Action Required | #DIV/0!
BHW2C403 | 2019-03-18 10:16 | 2.4 | 1.4 | 20 | 76.2 | -6.1 | -0.42 | N/A | 0 | Shut/Shut | 3.81
BHW2C404 | 2019-03-18 10:18 | 49.5 | 36.7 | 0 | 13.8 | -6 | 2.397 | 47.6 | 50 | OK- No Action Required | #DIV/0!
BHW3A451 | 2019-03-18 10:21 | 51.9 | 32.7 | 4.1 | 11.3 | -8.7 | -0.289 | N/A | 0 | Shut/Shut | 2.7561
BHW3A452 | 2019-03-18 10:24 | 55.3 | 40.8 | 0 | 3.9 | -10.8 | 11.423 | 63.8 | 55 | Surge | #DIV/0!
BHW3A453 | 2019-03-18 10:27 | 62.2 | 41.9 | 0 | 0 | -68.3 | 9.184 | 91.8 | 99 | OK- No Action Required | #DIV/0!
BHW3A454 | 2019-03-18 10:28 | 60.5 | 41.4 | 0 | 0 | -71.2 | 3.874 | 36.1 | 99 | OK- No Action Required | #DIV/0!
BHW3A455 | 2019-03-18 10:29 | 61.8 | 41.4 | 0 | 0 | -59.4 | 12.517 | 65.1 | 99 | OK- No Action Required | #DIV/0!
BGW2V255 | 2019-03-18 10:38 | 17.7 | 12.2 | 14.9 | 55.2 | -62 | 0.001 | 0.3 | 99 | Blocked-Investigation Required | 3.7047
BGW2V262 | 2019-03-18 10:39 | 56 | 41.9 | 0.4 | 1.7 | -62.5 | 0.552 | 13.7 | 99 | Blocked-Investigation Required | 4.25
BGW2V390 | 2019-03-18 10:41 | 52.1 | 38.9 | 0.7 | 8.3 | -2.4 | 0.628 | 14.7 | 15 | OK- No Action Required | 11.8571
BGW2V379 | 2019-03-18 10:42 | 45.4 | 36.1 | 0.7 | 17.8 | -0.6 | 8.952 | 6.5 | 10 | Adjusted Decrease | 25.4286
BHW2V413 | 2019-03-18 10:44 | 50.5 | 38.6 | 0.2 | 10.7 | -0.1 | -0.107 | N/A | 0 | Shut/Shut | 53.5
BGW2V244 | 2019-03-18 10:47 | 4.9 | 4.9 | 18.2 | 72 | 0 | 0.023 | 1.3 | 0 | Shut/Shut | 3.956
BHW2V415 | 2019-03-18 10:48 | 58.4 | 41.4 | 0 | 0.2 | -60.7 | 0.65 | 23.7 | 99 | Blocked-Investigation Required | #DIV/0!
BGW2V267 | 2019-03-18 10:49 | 1.3 | 0.9 | 20.1 | 77.7 | -5.6 | 0.017 | 1.1 | 0 | Shut/Shut | 3.8657
BGW2W257 | 2019-03-18 10:52 | 45.5 | 38.6 | 0.1 | 15.8 | -0.2 | 1.101 | 8.9 | 15 | OK- No Action Required | 158
BGW2W242 | 2019-03-18 10:53 | 49.3 | 37.5 | 0.2 | 13 | -32.3 | 0.695 | 25.2 | 40 | OK- No Action Required | 65
BGW2W246 | 2019-03-18 10:55 | 42.3 | 35.7 | 0 | 22 | -1.2 | 1.167 | 9.3 | 15 | OK- No Action Required | #DIV/0!
BGW2W256 | 2019-03-18 10:56 | 56.6 | 41.4 | 0 | 2 | -47.4 | 1.412 | 35.5 | 40 | Surge | #DIV/0!
BGW2W261 | 2019-03-18 10:58 | 54.7 | 39.3 | 0 | 6 | -1.3 | 1.589 | 11 | 20 | OK- No Action Required | #DIV/0!
BGW2N145 | 2019-03-18 11:03 | 50.5 | 38.5 | 0 | 11 | -1 | 2.071 | 12.6 | 20 | OK- No Action Required | #DIV/0!
BGW2N146 | 2019-03-18 11:05 | 57 | 41.1 | 0 | 1.9 | -7.1 | 0.762 | 16.6 | 25 | Surge | #DIV/0!
BGW2N143 | 2019-03-18 11:06 | 52.8 | 39.5 | 0 | 7.7 | -1.2 | 0.178 | 8 | 15 | OK- No Action Required | #DIV/0!
BGW2N144 | 2019-03-18 11:08 | 54 | 38.9 | 0.6 | 6.5 | -4.3 | 3.777 | 8.5 | 15 | Damaged | 10.8333
BGW2X163 | 2019-03-18 11:10 | 47.2 | 36.5 | 1 | 15.3 | -1.1 | 1.758 | 25 | 40 | OK- No Action Required | 15.3
BGW2H424 | 2019-03-18 13:08 | 55.4 | 39.3 | 0.2 | 5.1 | 0 | -0.263 | N/A | 25 | Blocked-Investigation Required | 25.5
BGW2H059 | 2019-03-18 13:10 | 52.4 | 39.5 | 0 | 8.1 | 0 | 6.555 | 5.6 | 15 | OK- No Action Required | #DIV/0!
BGW2H402 | 2019-03-18 13:11 | 53.1 | 39.3 | 0.2 | 7.4 | -0.7 | 6.243 | 10.8 | 25 | OK- No Action Required | 37
BGW2H064 | 2019-03-18 13:12 | 45.2 | 35.4 | 0.6 | 18.8 | -0.6 | 6.039 | 10.6 | 12 | Adjusted Decrease | 31.3333
BGW2H423 | 2019-03-18 13:15 | 46.4 | 35.9 | 0 | 17.7 | -4.1 | 16.897 | 35.7 | 50 | OK- No Action Required | #DIV/0!
BGW2H363 | 2019-03-18 13:17 | 53.3 | 38 | 0.4 | 8.3 | -0.5 | 0.844 | 17.5 | 25 | OK- No Action Required | 20.75
BGW2H365 | 2019-03-18 13:18 | 49.9 | 37 | 0 | 13.1 | -3.5 | 0.424 | 12.3 | 25 | OK- No Action Required | #DIV/0!
BGW2H361 | 2019-03-18 13:19 | 55.9 | 40.4 | 0 | 3.7 | -0.2 | 5.913 | 10.6 | 25 | OK- No Action Required | #DIV/0!
BGW2H360 | 2019-03-18 13:20 | 51.5 | 37.4 | 0 | 11.1 | -0.2 | 4.372 | 4.6 | 20 | OK- No Action Required | #DIV/0!
BGW2H366 | 2019-03-18 13:22 | 55.2 | 36.1 | 0.6 | 8.1 | 0 | 2.684 | 7.2 | 20 | Damaged | 13.5
BGW2H362 | 2019-03-18 13:23 | 47.5 | 36.3 | 1.2 | 15 | -0.7 | 4.254 | 8.9 | 7 | Adjusted Decrease | 12.5
BGW2H058 | 2019-03-18 13:25 | 49.2 | 36.2 | 2.4 | 12.2 | -5.2 | -0.152 | N/A | 10 | Blocked-Investigation Required | 5.0833
BGW2H412 | 2019-03-18 13:26 | 20.1 | 21.9 | 4.9 | 53.1 | 0 | 0.439 | 5.7 | 10 | Blocked-Investigation Required | 10.8367
BGW2H102 | 2019-03-18 13:27 | 50.9 | 36 | 1.4 | 11.7 | -29.4 | 0.129 | 1.5 | 5 | OK- No Action Required | 8.3571
BGW2H422 | 2019-03-18 13:28 | 7.9 | 7.3 | 15.1 | 69.7 | 0 | 6.21 | 1.1 | 10 | OK- No Action Required | 4.6159
BGW2G052 | 2019-03-18 13:38 | 53.8 | 37 | 0.3 | 8.9 | 0.1 | -0.054 | N/A | 15 | Blocked-Investigation Required | 29.6667
BGW2G054 | 2019-03-18 13:39 | 47.2 | 36.6 | 0.5 | 15.7 | -55.3 | 15.562 | 70.9 | 70 | OK- No Action Required | 31.4
BGW2G418 | 2019-03-18 13:41 | 48.1 | 35.1 | 0 | 16.8 | 0 | -0.076 | N/A | 20 | Blocked-Investigation Required | #DIV/0!
BGW2G419 | 2019-03-18 13:42 | 52.9 | 37.1 | 0.1 | 9.9 | -3.2 | 1.954 | 26.4 | 40 | OK- No Action Required | 99
BGW2G421 | 2019-03-18 13:44 | 54.5 | 36.2 | 1 | 8.3 | -0.5 | 0.442 | 12.7 | 25 | OK- No Action Required | 8.3
BGW2M435 | 2019-03-18 14:18 | 0.1 | 0 | 19.8 | 80.1 | -0.9 | -0.042 | N/A | 0 | Shut/Shut | 4.0455
BGW2M450 | 2019-03-18 14:19 | 56.6 | 40.5 | 0.1 | 2.8 | -57.2 | 6.933 | 5.6 | 99 | OK- No Action Required | 28
BGW2M381 | 2019-03-18 14:21 | 47.8 | 36.8 | 0.2 | 15.2 | -17 | 21.437 | 39.1 | 42 | Adjusted Decrease | 76
BGW2M124 | 2019-03-18 14:22 | 54.1 | 38.6 | 0.4 | 6.9 | -1.6 | -0.111 | N/A | 25 | Blocked-Investigation Required | 17.25
BGW2M397 | 2019-03-18 14:23 | 50.9 | 39.1 | 0 | 10 | -45.4 | 10.01 | 26.2 | 50 | OK- No Action Required | #DIV/0!
BGW2M432 | 2019-03-18 14:24 | 50.5 | 38.9 | 0 | 10.6 | -1.9 | 10.313 | 7 | 15 | OK- No Action Required | #DIV/0!
BGW2M131 | 2019-03-18 14:25 | 43.5 | 34.8 | 0 | 21.7 | 0 | 3.588 | 8.1 | 15 | OK- No Action Required | #DIV/0!
BGW2M434 | 2019-03-18 14:26 | 43 | 34.7 | 0 | 22.3 | -1.8 | 12.928 | 31 | 30 | OK- No Action Required | #DIV/0!
BGW2M083 | 2019-03-18 14:27 | 56.7 | 39.9 | 0.2 | 3.2 | -3.5 | -0.149 | N/A | 10 | Blocked-Investigation Required | 16
BGW2M128 | 2019-03-18 14:28 | 51.5 | 35.5 | 1.9 | 11.1 | -29.5 | 0.075 | 2.3 | 10 | Blocked-Investigation Required | 5.8421
BGW2L380 | 2019-03-18 14:37 | 33.2 | 29.6 | 3.3 | 33.9 | -0.1 | 15.616 | 1.8 | 5 | Adjusted Decrease | 10.2727
BGW2L134 | 2019-03-18 14:39 | 49 | 36.6 | 0.4 | 14 | -0.3 | 0.407 | 11.9 | 25 | Damaged | 35
BGW2L133 | 2019-03-18 14:40 | 49.3 | 37.8 | 0 | 12.9 | -0.8 | 5.31 | 9.8 | 15 | OK- No Action Required | #DIV/0!
BGW2L431 | 2019-03-18 14:41 | 51.1 | 37.2 | 0 | 11.7 | -47.3 | 20.575 | 133.2 | 90 | OK- No Action Required | #DIV/0!
BGW2L378 | 2019-03-18 14:42 | 47.4 | 37.2 | 0 | 15.4 | -0.6 | 2.985 | 14.6 | 20 | OK- No Action Required | #DIV/0!
BGW2L140 | 2019-03-18 14:43 | 52.8 | 39.9 | 0 | 7.3 | -47.2 | 4.542 | 4.5 | 50 | OK- No Action Required | #DIV/0!
BGW2L377 | 2019-03-18 14:44 | 50.3 | 38.1 | 0 | 11.6 | -0.1 | 1.655 | 11.1 | 20 | OK- No Action Required | #DIV/0!
BGW2L420 | 2019-03-18 14:45 | 36.1 | 26.9 | 6.1 | 30.9 | 0 | 1.224 | 2.4 | 5 | Damaged | 5.0656
BGW2L359 | 2019-03-18 14:46 | 25.9 | 24.3 | 4.5 | 45.3 | -0.2 | 1.736 | 2.8 | 5 | Adjusted Decrease | 10.0667
BGW2L101 | 2019-03-18 14:47 | 2.5 | 1.4 | 18.1 | 78 | 0 | -0.013 | N/A | 0 | Shut/Shut | 4.3094
BGW2L137 | 2019-03-18 14:49 | 47.3 | 36.7 | 0.3 | 15.7 | -23.7 | 2.29 | 46.2 | 40 | OK- No Action Required | 52.3333
BGW2L417 | 2019-03-18 14:51 | 52.3 | 37.4 | 1.4 | 8.9 | 1 | 0.796 | 16.9 | 20 | Surge | 6.3571
BGW2L056 | 2019-03-18 14:51 | 36.1 | 33.3 | 0 | 30.6 | -0.2 | 13.414 | 7.9 | 15 | OK- No Action Required | #DIV/0!
BGW2L082 | 2019-03-18 14:52 | 55.1 | 39.3 | 0 | 5.6 | -38 | 18.575 | 37.1 | 99 | OK- No Action Required | #DIV/0!
BGW2L448 | 2019-03-18 14:54 | 46.9 | 36.3 | 0 | 16.8 | -24.2 | 15.791 | 73.1 | 60 | OK- No Action Required | #DIV/0!
BGW2L150 | 2019-03-18 14:55 | 50.3 | 37.9 | 0 | 11.8 | -56 | 9.422 | 90.9 | 99 | OK- No Action Required | #DIV/0!
BGW2L376 | 2019-03-18 14:56 | 43.3 | 34.8 | 0.8 | 21.1 | -0.5 | 5.684 | 5.2 | 5 | Adjusted Decrease | 26.375
BGW2L433 | 2019-03-18 14:58 | 36.2 | 28.8 | 4.6 | 30.4 | -0.4 | 1.97 | 12.2 | 10 | Adjusted Decrease | 6.6087
BGW2L053 | 2019-03-18 14:59 | 55.8 | 39.2 | 0 | 5 | -65.9 | 0.143 | 11.4 | 99 | Blocked-Investigation Required | #DIV/0!
BGW2J090 | 2019-03-19 08:30 | 53.4 | 38.4 | 0.6 | 7.6 | -3.3 | 9.066 | 26.4 | 30 | OK- No Action Required | 12.6667
BGW2J087 | 2019-03-19 08:31 | 50.8 | 39.5 | 0.2 | 9.5 | -3.2 | 3.762 | 8.4 | 20 | OK- No Action Required | 47.5
BGW2J091 | 2019-03-19 08:33 | 46.3 | 36 | 1.4 | 16.3 | -1.1 | 25.056 | 21.6 | 22 | Adjusted Decrease | 11.6429
BGW2J401 | 2019-03-19 08:34 | 51.3 | 37.9 | 0.7 | 10.1 | -44.3 | 3.125 | 15.2 | 40 | OK- No Action Required | 14.4286
BGW2J089 | 2019-03-19 08:36 | 31.5 | 30.8 | 1.8 | 35.9 | 0 | 1.693 | 11.1 | 15 | Damaged | 19.9444
BGW2J430 | 2019-03-19 08:37 | 44.7 | 36.5 | 0 | 18.8 | -2.7 | 1.226 | 9.6 | 20 | OK- No Action Required | #DIV/0!
BGW2J408 | 2019-03-19 08:39 | 43.5 | 34.9 | 2.2 | 19.4 | -0.1 | 5.89 | 5.3 | 20 | Damaged | 8.8182
BGW2J400 | 2019-03-19 08:40 | 38.2 | 35.5 | 0.4 | 25.9 | -0.1 | 2.107 | 12.4 | 22 | Adjusted Decrease | 64.75
BGW2K429 | 2019-03-19 08:50 | 30 | 31.5 | 0.6 | 37.9 | -0.6 | 9.305 | 6.5 | 7 | Adjusted Decrease | 63.1667
BGW2K372 | 2019-03-19 08:52 | 39 | 33.8 | 1.5 | 25.7 | -0.8 | 5.833 | 5.2 | 7 | Adjusted Decrease | 17.1333
BGW2K375 | 2019-03-19 08:55 | 47.9 | 37.7 | 0.2 | 14.2 | -27 | 16.266 | 73.6 | 72 | Adjusted Decrease | 71
BGW2K428 | 2019-03-19 08:56 | 45.2 | 35.2 | 0.9 | 18.7 | -0.9 | 3.648 | 16.5 | 25 | Adjusted Decrease | 20.7778
BGW2K427 | 2019-03-19 08:57 | 45.3 | 35.6 | 0 | 19.1 | -1.6 | 11.691 | 7.5 | 10 | OK- No Action Required | #DIV/0!
BGW2K426 | 2019-03-19 09:00 | 47.6 | 37 | 0.1 | 15.3 | -0.4 | 27.113 | 11.6 | 22 | Adjusted Decrease | 153
BGW2K373 | 2019-03-19 09:01 | 44.7 | 36.3 | 0 | 19 | -5.1 | 1.46 | 22.6 | 25 | OK- No Action Required | #DIV/0!
BGW2K374 | 2019-03-19 09:02 | 47.8 | 37.2 | 0.1 | 14.9 | -1.2 | 0.523 | 13.6 | 25 | OK- No Action Required | 149
BGW2K093 | 2019-03-19 09:04 | 39.3 | 35.1 | 0 | 25.6 | -1.9 | 3.836 | 4.1 | 25 | OK- No Action Required | #DIV/0!
BGW2K095 | 2019-03-19 09:05 | 16.8 | 12.7 | 14.1 | 56.4 | -60 | -0.236 | N/A | 99 | Blocked-Investigation Required | 4
BGW2K094 | 2019-03-19 09:07 | 45.9 | 35.9 | 0.9 | 17.3 | -2.7 | 2.181 | 27.3 | 40 | Damaged | 19.2222
BGW2I367 | 2019-03-19 09:12 | 33.3 | 31.2 | 0.8 | 34.7 | -0.4 | 9.803 | 6.7 | 22 | Adjusted Decrease | 43.375
BGW2I368 | 2019-03-19 09:13 | 12.5 | 10.3 | 14.4 | 62.8 | 0 | 1.719 | 5.6 | 3 | Adjusted Decrease | 4.3611
BGW2I370 | 2019-03-19 09:14 | 53.7 | 38.7 | 0.1 | 7.5 | -0.2 | >>>> | N/A | 40 | Change Orife Plate Required | 75
BGW2I445 | 2019-03-19 09:16 | 24.2 | 18.2 | 10.7 | 46.9 | -0.6 | 11.58 | 14.8 | 20 | Adjusted Decrease | 4.3832
BGW2I081 | 2019-03-19 09:18 | 59.7 | 39.2 | 0 | 1.1 | -20.7 | 0.739 | 16.4 | 27 | Adjusted Increase | #DIV/0!
BGW2I371 | 2019-03-19 09:19 | 49 | 36.6 | 0 | 14.4 | -2.9 | 1.103 | 19.6 | 25 | OK- No Action Required | #DIV/0!
BGW2I369 | 2019-03-19 09:20 | 48.1 | 37.1 | 0.2 | 14.6 | -0.5 | 15.208 | 8.5 | 25 | OK- No Action Required | 73
BGW2I396 | 2019-03-19 09:21 | 55.8 | 38.8 | 0 | 5.4 | -9.3 | 3.48 | 35.2 | 40 | OK- No Action Required | #DIV/0!
BGW2I442 | 2019-03-19 09:23 | 15.5 | 23.6 | 1.4 | 59.5 | -0.3 | 28.387 | 2.5 | 5 | Adjusted Decrease | 42.5
BLW2X460 | 2019-03-19 12:55 | 0.2 | 0.4 | 20.6 | 78.8 | -65.4 | -0.053 | N/A | 0 | Shut/Shut | 3.8252
BLW2X461 | 2019-03-19 12:58 | 59.3 | 39.8 | 0 | 0.9 | -65.9 | 0.793 | 27.3 | 30 | OK- No Action Required | #DIV/0!
BLW2X462 | 2019-03-19 13:00 | 0.3 | 0.2 | 20.6 | 78.9 | -65.1 | -0.024 | N/A | 0 | Shut/Shut | 3.8301
BLW2X463 | 2019-03-19 13:02 | 0.7 | 0.5 | 20.5 | 78.3 | -65.9 | 0.133 | 10.8 | 0 | Shut/Shut | 3.8195
BGW2X456 | 2019-03-19 13:05 | 62.1 | 38.3 | 0 | 0 | 0 | 0.453 | 6 | 7 | Adjusted Increase | #DIV/0!
BGW2X457 | 2019-03-19 13:08 | 56.6 | 38.4 | 0 | 5 | -8.6 | 22.745 | 41.9 | 40 | OK- No Action Required | #DIV/0!
BGW2K115 | 2019-03-19 13:10 | 56.5 | 38.9 | 0 | 4.6 | 0.1 | -0.085 | N/A | 7 | Adjusted Increase | #DIV/0!
BGW2K117 | 2019-03-19 13:12 | 44.8 | 35.1 | 0 | 20.1 | -4.1 | 5.868 | 21.2 | 25 | OK- No Action Required | #DIV/0!
BLW2X465 | 2019-03-19 13:14 | 0.6 | 0.4 | 20.3 | 78.7 | -64.2 | 0.106 | 5.9 | 0 | Shut/Shut | 3.8768
BLW2X464 | 2019-03-19 13:15 | 0.3 | 0.3 | 20.4 | 79 | -65.1 | 0.169 | 3.4 | 0 | Shut/Shut | 3.8725
BGW2X458 | 2019-03-19 13:18 | 55.7 | 37.2 | 0 | 7.1 | -2.9 | 5.358 | 10.2 | 15 | OK- No Action Required | #DIV/0!
BLW2X466 | 2019-03-19 13:19 | 0.2 | 0.1 | 20.3 | 79.4 | -64.1 | 0.024 | 1.3 | 0 | Shut/Shut | 3.9113
BLW2X467 | 2019-03-19 13:21 | 0.1 | 0.1 | 20.5 | 79.3 | -64.4 | 0.01 | 0.8 | 0 | Shut/Shut | 3.8683
BGW2X459 | 2019-03-19 13:23 | 47.1 | 35.1 | 0 | 17.8 | 0 | 1.059 | 4.5 | 15 | OK- No Action Required | #DIV/0!
BGW2T234 | 2019-03-19 13:28 | 54.1 | 40.1 | 0 | 5.8 | -0.7 | 1.389 | 10.3 | 20 | OK- No Action Required | #DIV/0!
BLW2X468 | 2019-03-19 13:30 | 51.4 | 37 | 0.7 | 10.9 | -9.9 | 4.449 | 18.6 | 25 | OK- No Action Required | 15.5714
BGW2T235 | 2019-03-19 13:30 | 0.3 | 0.3 | 20.2 | 79.2 | -0.1 | -0.051 | N/A | 0 | Shut/Shut | 3.9208
BGW2T230 | 2019-03-19 13:32 | 47.1 | 34.4 | 0 | 18.5 | -0.4 | 1.547 | 10.9 | 20 | OK- No Action Required | #DIV/0!
BGW2T229 | 2019-03-19 13:33 | 0.2 | 0.2 | 20 | 79.6 | -0.2 | -0.057 | N/A | 0 | Shut/Shut | 3.98
BGW2T438 | 2019-03-19 13:34 | 53.2 | 38.6 | 0 | 8.2 | -0.6 | 5.257 | 10 | 20 | OK- No Action Required | #DIV/0!
BGW2T339 | 2019-03-19 13:35 | 53.1 | 38.5 | 0 | 8.4 | -4.1 | 2.524 | 13.9 | 25 | OK- No Action Required | #DIV/0!
BGW2T387 | 2019-03-19 13:37 | 59 | 38.2 | 0.2 | 2.6 | 0.2 | 0.738 | 1.9 | 7 | Adjusted Increase | 13
BGW2T228 | 2019-03-19 13:38 | 13.6 | 21.4 | 7.5 | 57.5 | -1.2 | -0.038 | N/A | 0 | Shut/Shut | 7.6667
BGW2T224 | 2019-03-19 13:41 | 58.4 | 40.9 | 0 | 0.7 | 2.4 | 0.069 | 2.3 | 17 | Surge | #DIV/0!
BGW2T220 | 2019-03-19 13:42 | 59.7 | 37.9 | 0 | 2.4 | 0 | 0.017 | 2.6 | 7 | Adjusted Increase | #DIV/0!
BGW2T219 | 2019-03-19 13:43 | 46 | 35.1 | 0 | 18.9 | -2.1 | 4.117 | 8.8 | 15 | OK- No Action Required | #DIV/0!
BGW2Z342 | 2019-03-19 14:29 | 59.8 | 37.8 | 0 | 2.4 | 0.1 | -0.169 | N/A | 15 | Adjusted Increase | #DIV/0!
BGW2Z343 | 2019-03-19 14:31 | 48 | 35.2 | 0.1 | 16.7 | -1.8 | 7.896 | 24.6 | 40 | OK- No Action Required | 167
BGW2Z344 | 2019-03-19 14:34 | 50.9 | 35.7 | 0.2 | 13.2 | -0.4 | 1.597 | 11.1 | 25 | OK- No Action Required | 66
BGW2Z345 | 2019-03-19 14:36 | 46.1 | 34.9 | 0 | 19 | -0.2 | 0.606 | 6.8 | 20 | OK- No Action Required | #DIV/0!
BGW2Z346 | 2019-03-19 14:38 | 51.5 | 36.6 | 0 | 11.9 | -4.6 | 2.621 | 14.2 | 25 | OK- No Action Required | #DIV/0!
BHW2A347 | 2019-03-19 14:40 | 56.3 | 41 | 0 | 2.7 | -22.8 | 22.261 | 143.4 | 99 | OK- No Action Required | #DIV/0!
BHW2A348 | 2019-03-19 14:44 | 54.6 | 39.7 | 0 | 5.7 | -24.8 | 16.858 | 125 | 99 | OK- No Action Required | #DIV/0!
BHW2A349 | 2019-03-19 14:45 | 15.9 | 10.5 | 16.9 | 56.7 | -36 | -0.15 | N/A | 99 | Blocked-Investigation Required | 3.355
BHW2A350 | 2019-03-19 14:46 | 58.4 | 40.6 | 0 | 1 | -28.6 | 11.068 | 100.7 | 99 | OK- No Action Required | #DIV/0!
BGW2L380 | 2019-03-20 11:38 | 24.7 | 25.6 | 5.1 | 44.6 | -0.1 | 13.323 | 1.7 | 5 | OK- No Action Required | 8.7451
BGW2L134 | 2019-03-20 11:39 | 40.1 | 33.7 | 1.2 | 25 | -0.5 | 0.882 | 17.3 | 20 | OK- No Action Required | 20.8333
BGW2L133 | 2019-03-20 11:41 | 46.5 | 37.9 | 0 | 15.6 | -0.9 | 4.955 | 9.4 | 15 | OK- No Action Required | #DIV/0!
BGW2L431 | 2019-03-20 11:42 | 51 | 38.2 | 0 | 10.8 | -38.8 | 24.89 | 146.6 | 90 | OK- No Action Required | #DIV/0!
BGW2L378 | 2019-03-20 11:43 | 43.6 | 37.2 | 0 | 19.2 | -0.8 | 2.723 | 13.8 | 20 | OK- No Action Required | #DIV/0!
BGW2L140 | 2019-03-20 11:45 | 52.8 | 40.9 | 0 | 6.3 | -49 | 11.071 | 7 | 50 | OK- No Action Required | #DIV/0!
BGW2L377 | 2019-03-20 11:46 | 43.8 | 36.5 | 0.2 | 19.5 | -0.1 | 1.203 | 9.3 | 15 | OK- No Action Required | 97.5
BGW2L420 | 2019-03-20 11:47 | 1.2 | 2.6 | 18.5 | 77.7 | -0.4 | 0.962 | 2.1 | 0 | Shut/Shut | 4.2
BGW2L359 | 2019-03-20 11:48 | 5.3 | 16.7 | 6.6 | 71.4 | -0.6 | 1.179 | 2.3 | 5 | OK- No Action Required | 10.8182
BGW2L101 | 2019-03-20 11:49 | 4 | 2 | 18.7 | 75.3 | -0.1 | -0.078 | N/A | 0 | Shut/Shut | 4.0267
BGW2L137 | 2019-03-20 11:51 | 48.1 | 37.5 | 0.2 | 14.2 | -24.8 | 1.55 | 38.3 | 40 | Surge | 71
BGW2L417 | 2019-03-20 11:53 | 38.5 | 29.3 | 5.8 | 26.4 | -1.7 | 0.626 | 14.8 | 20 | Surge | 4.5517
BGW2L056 | 2019-03-20 11:54 | 26 | 30.5 | 0 | 43.5 | -0.1 | 13.281 | 7.8 | 15 | OK- No Action Required | #DIV/0!
BGW2L082 | 2019-03-20 11:55 | 55.6 | 40.3 | 0 | 4.1 | -40.5 | 19.364 | 37.8 | 99 | OK- No Action Required | #DIV/0!
BGW2L448 | 2019-03-20 11:56 | 47.4 | 37 | 0 | 15.6 | -25.1 | 15.649 | 72.6 | 60 | OK- No Action Required | #DIV/0!
BGW2L150 | 2019-03-20 11:57 | 51.5 | 39 | 0 | 9.5 | -61.3 | 5.917 | 71.3 | 99 | OK- No Action Required | #DIV/0!
BGW2L376 | 2019-03-20 11:59 | 43 | 35.6 | 0.5 | 20.9 | -0.4 | 2.303 | 3.3 | 5 | OK- No Action Required | 41.8
BGW2L433 | 2019-03-20 12:00 | 28.3 | 24.5 | 6.4 | 40.8 | -0.2 | 1.42 | 10.3 | 10 | OK- No Action Required | 6.375
BGW2L053 | 2019-03-20 12:01 | 56.4 | 39.5 | 0 | 4.1 | -62.2 | 0.223 | 14.2 | 99 | Blocked-Investigation Required | #DIV/0!
BGW2Q209 | 2019-03-20 12:56 | 42.5 | 28.9 | 2.7 | 25.9 | -50.8 | -0.09 | N/A | 25 | Blocked-Investigation Required | 9.5926
BGW2Q185 | 2019-03-20 12:57 | 52.5 | 33.6 | 0 | 13.9 | -5.5 | 21.03 | 10.2 | 25 | OK- No Action Required | #DIV/0!
BGW2Q180 | 2019-03-20 12:58 | 28.4 | 17.1 | 9.5 | 45 | 0 | 0.058 | 1 | 5 | OK- No Action Required | 4.7368
BGW2Q190 | 2019-03-20 13:00 | 53.7 | 34.9 | 0 | 11.4 | -6.6 | 1.484 | 23.3 | 40 | OK- No Action Required | #DIV/0!
BGW2Q199 | 2019-03-20 13:01 | 49.9 | 34.3 | 0 | 15.8 | -45.7 | -0.063 | N/A | 15 | Blocked-Investigation Required | #DIV/0!
BGW2Q175 | 2019-03-20 13:02 | 23.2 | 25.2 | 0.6 | 51 | -1.6 | 3.102 | 0.8 | 5 | OK- No Action Required | 85
BGW2Q179 | 2019-03-20 13:04 | 43.4 | 30.6 | 1.8 | 24.2 | -6 | 1.291 | 4.9 | 10 | Adjusted Decrease | 13.4444
BGW2Q335 | 2019-03-20 13:05 | 49.7 | 36.6 | 0 | 13.7 | -5.1 | 3.695 | 36.3 | 40 | OK- No Action Required | #DIV/0!
BGW2Q336 | 2019-03-20 13:07 | 50 | 36.2 | 1.1 | 12.7 | 0 | 0.032 | 1.5 | 15 | Damaged | 11.5455
BGW2Q204 | 2019-03-20 13:08 | 14.4 | 10.9 | 15.3 | 59.4 | -4.2 | -0.325 | N/A | 10 | Blocked-Investigation Required | 3.8824
BGW2Q214 | 2019-03-20 13:09 | 52.7 | 35.8 | 0 | 11.5 | -11.5 | 0.201 | 8.5 | 30 | Surge | #DIV/0!
BGW2Q203 | 2019-03-20 13:10 | 58.2 | 40 | 0 | 1.8 | -39.9 | 9.848 | 57.9 | 99 | OK- No Action Required | #DIV/0!
BGW2Q382 | 2019-03-20 13:11 | 51.8 | 37.6 | 0.3 | 10.3 | -1.4 | 9.01 | 26.3 | 30 | OK- No Action Required | 34.3333
BGW2Q184 | 2019-03-20 13:13 | 53.3 | 38.1 | 0.2 | 8.4 | -1 | 0.648 | 25 | 25 | OK- No Action Required | 42
BGW2Q189 | 2019-03-20 13:14 | 0.3 | 1.5 | 19.2 | 79 | 0 | 0.307 | 0.2 | 0 | Shut/Shut | 4.1146
BGW2Q338 | 2019-03-20 13:15 | 13.6 | 18.5 | 3.9 | 64 | -0.5 | -0.102 | N/A | 0 | Shut/Shut | 16.4103
BGW2Q337 | 2019-03-20 13:16 | 42.3 | 33.9 | 0 | 23.8 | -0.5 | 10.64 | 7.1 | 15 | OK- No Action Required | #DIV/0!
BGW2Q444 | 2019-03-20 13:18 | 55.7 | 35.8 | 0.1 | 8.4 | -2 | 0.61 | 6.9 | 15 | OK- No Action Required | 84
BGW2Q168 | 2019-03-20 13:18 | 0.5 | 0.3 | 19.5 | 79.7 | -58.3 | -0.382 | N/A | 99 | Blocked-Investigation Required | 4.0872
BGW2X167 | 2019-03-20 13:24 | 50.7 | 36.3 | 0 | 13 | -2 | 0.802 | 16.8 | 40 | OK- No Action Required | #DIV/0!
BGW2X162 | 2019-03-20 13:26 | 46.7 | 34.8 | 0 | 18.5 | -1.2 | 1.125 | 9.4 | 20 | OK- No Action Required | #DIV/0!
BGW2X161 | 2019-03-20 13:31 | 58.1 | 35.9 | 0.6 | 5.4 | 0 | 0.008 | 0.4 | 5 | Damaged | 9
BGW2X160 | 2019-03-20 13:33 | 56.6 | 38.3 | 0 | 5.1 | -0.6 | 31.429 | 2.7 | 25 | Change Orife Plate Required | #DIV/0!
BGW2X166 | 2019-03-20 13:35 | 48.7 | 37.2 | 0 | 14.1 | -0.2 | 0.206 | 8.6 | 15 | OK- No Action Required | #DIV/0!
BGW2X159 | 2019-03-20 13:36 | 46.8 | 35.8 | 0 | 17.4 | -1.3 | 3.741 | 17 | 25 | OK- No Action Required | #DIV/0!
BGW2X249 | 2019-03-20 13:39 | 39.5 | 31.2 | 0 | 29.3 | -4.6 | 13.108 | 31.7 | 40 | OK- No Action Required | #DIV/0!
BGW2K111 | 2019-03-20 13:41 | 52.4 | 37.3 | 0 | 10.3 | 0 | 5.829 | 10.6 | 15 | OK- No Action Required | #DIV/0!
BGW2L380 | 2019-03-21 09:05 | 23.2 | 25 | 5.4 | 46.4 | -0.2 | 12.972 | 1.7 | 5 | OK- No Action Required | 8.5926
BGW2L134 | 2019-03-21 09:06 | 38.1 | 33 | 1.4 | 27.5 | -0.8 | 0.899 | 17.4 | 25 | OK- No Action Required | 19.6429
BGW2L133 | 2019-03-21 09:07 | 45.1 | 37.5 | 0 | 17.4 | -1.2 | 5.35 | 9.7 | 15 | OK- No Action Required | #DIV/0!
BGW2L431 | 2019-03-21 09:09 | 51.1 | 38.3 | 0 | 10.6 | -56.9 | 14.423 | 110.7 | 90 | OK- No Action Required | #DIV/0!
BGW2L378 | 2019-03-21 09:10 | 43.1 | 36.9 | 0 | 20 | -0.8 | 2.999 | 14.5 | 15 | OK- No Action Required | #DIV/0!
BGW2L140 | 2019-03-21 09:11 | 53.1 | 41.2 | 0 | 5.7 | -68.8 | 0.93 | 2 | 50 | OK- No Action Required | #DIV/0!
BGW2L377 | 2019-03-21 09:13 | 40.1 | 35.3 | 0.4 | 24.2 | -0.2 | 1.158 | 9.1 | 20 | OK- No Action Required | 60.5
BGW2L420 | 2019-03-21 09:14 | 1 | 2.6 | 18.4 | 78 | 0 | 1.113 | 2.2 | 0 | Shut/Shut | 4.2391
BGW2L359 | 2019-03-21 09:15 | 6.6 | 16.5 | 7.5 | 69.4 | -0.2 | 1.038 | 2.1 | 3 | OK- No Action Required | 9.2533
BGW2L101 | 2019-03-21 09:16 | 2.4 | 1.4 | 18.9 | 77.3 | -0.2 | -0.022 | N/A | 0 | Shut/Shut | 4.0899
BGW2L137 | 2019-03-21 09:18 | 47.8 | 37.5 | 0.3 | 14.4 | -31.1 | 1.977 | 43.2 | 40 | Surge | 48
BGW2L417 | 2019-03-21 09:20 | 37.8 | 28.8 | 6.2 | 27.2 | -1.5 | 0.607 | 14.7 | 25 | Surge | 4.3871
BGW2L056 | 2019-03-21 09:21 | 22.4 | 29.4 | 0 | 48.2 | -0.1 | 13.51 | 7.8 | 10 | OK- No Action Required | #DIV/0!
BGW2L082 | 2019-03-21 09:22 | 55.9 | 40.5 | 0 | 3.6 | -41.8 | 18.878 | 37.3 | 99 | OK- No Action Required | #DIV/0!
BGW2L448 | 2019-03-21 09:23 | 47.8 | 37.6 | 0 | 14.6 | -24 | 17.596 | 77 | 60 | OK- No Action Required | #DIV/0!
BGW2L150 | 2019-03-21 09:24 | 52.3 | 39.3 | 0 | 8.4 | -69.7 | 1.524 | 36.2 | 99 | OK- No Action Required | #DIV/0!
BGW2L376 | 2019-03-21 09:26 | 46.3 | 37.3 | 0.2 | 16.2 | 0 | 3.133 | 3.8 | 5 | OK- No Action Required | 81
BGW2L433 | 2019-03-21 09:27 | 29.7 | 25.8 | 5.8 | 38.7 | -0.1 | 1.588 | 10.9 | 10 | OK- No Action Required | 6.6724
BGW2L053 | 2019-03-21 09:28 | 56 | 40 | 0 | 4 | -71.1 | -0.057 | N/A | 99 | Blocked-Investigation Required | #DIV/0!
BGW2X258 | 2019-03-21 10:35 | 55.1 | 38.4 | 0 | 6.5 | -67 | 1.369 | 35 | 99 | OK- No Action Required | #DIV/0!
BGW2X259 | 2019-03-21 10:36 | 60.4 | 38.9 | 0 | 0.7 | -3.2 | 4.554 | 4.8 | 15 | Surge | #DIV/0!
BGW2X393 | 2019-03-21 10:37 | 0.3 | 0.3 | 19.3 | 80.1 | 0 | -0.139 | N/A | 0 | Shut/Shut | 4.1503
BGW2X254 | 2019-03-21 10:39 | 46 | 34.9 | 0 | 19.1 | -66.1 | 2.847 | 30.4 | 99 | Surge | #DIV/0!
BGW2X239 | 2019-03-21 10:40 | 45.8 | 36.4 | 0.1 | 17.7 | -5.2 | 0.462 | 12.7 | 15 | Surge | 177
BGW2X247 | 2019-03-21 10:42 | 39.8 | 35 | 0 | 25.2 | -0.4 | 0.342 | 5 | 15 | OK- No Action Required | #DIV/0!
BGW2X264 | 2019-03-21 10:43 | 57.4 | 39.2 | 0 | 3.4 | -50.9 | 22.84 | 144.6 | 99 | OK- No Action Required | #DIV/0!
BGW2X425 | 2019-03-21 10:44 | 0.2 | 0.3 | 19.9 | 79.6 | -33.9 | 0.457 | 5.7 | 7 | Adjusted Decrease | 4
BGW2X446 | 2019-03-21 10:46 | 59.3 | 40.1 | 0 | 0.6 | -2 | 0.006 | 0.7 | 3 | Adjusted Increase | #DIV/0!
BGW2X443 | 2019-03-21 10:48 | 53.2 | 38.9 | 0.5 | 7.4 | -32.2 | 1.906 | 12 | 20 | OK- No Action Required | 14.8
BGW2X157 | 2019-03-21 10:49 | 0.4 | 0.4 | 19.7 | 79.5 | 0.1 | -0.07 | N/A | 0 | Shut/Shut | 4.0355
BGW2X158 | 2019-03-21 10:50 | 0.5 | 0.3 | 20.3 | 78.9 | -26.9 | 0.039 | 1.7 | 0 | Shut/Shut | 3.8867
BGW2X441 | 2019-03-21 10:51 | 59.6 | 39.6 | 0 | 0.8 | -2.2 | -0.054 | N/A | 20 | Blocked-Investigation Required | #DIV/0!
BGW2X164 | 2019-03-21 10:53 | 52 | 37.2 | 1.1 | 9.7 | -88.5 | -0.062 | N/A | 99 | Blocked-Investigation Required | 8.8182
BGW2U243 | 2019-03-21 11:03 | 43.4 | 35.7 | 0 | 20.9 | -11.5 | 9.273 | 56 | 50 | OK- No Action Required | #DIV/0!
BGW2U398 | 2019-03-21 11:05 | 39.9 | 33 | 1.2 | 25.9 | -21.9 | 5.322 | 42.5 | 40 | Surge | 21.5833
BGW2U238 | 2019-03-21 11:07 | 37.1 | 32.4 | 0.8 | 29.7 | -8.7 | 20.938 | 39.6 | 35 | Adjusted Decrease | 37.125
BGW2U227 | 2019-03-21 11:08 | 44 | 35.9 | 0 | 20.1 | -10.3 | 23.717 | 41.8 | 40 | OK- No Action Required | #DIV/0!
BGW2U232 | 2019-03-21 11:10 | 57.8 | 40.5 | 0.1 | 1.6 | -58.1 | 1.018 | 29.9 | 60 | OK- No Action Required | 16
BGW2U226 | 2019-03-21 11:12 | 58.5 | 42.5 | 0 | 0 | -63.5 | -0.001 | N/A | 40 | Blocked-Investigation Required | #DIV/0!
BGW2U439 | 2019-03-21 11:13 | 12.9 | 8.7 | 16.4 | 62 | -0.2 | 0.089 | 2.6 | 0 | Shut/Shut | 3.7805
BGW2U241 | 2019-03-21 11:14 | 56.9 | 42.6 | 0 | 0.5 | -53.9 | 2.046 | 25.4 | 42 | Surge | #DIV/0!
BGW2U251 | 2019-03-21 11:15 | 54.8 | 41.8 | 0 | 3.4 | -59.5 | 4.707 | 38.8 | 99 | OK- No Action Required | #DIV/0!
BGW2U245 | 2019-03-21 11:17 | 48 | 36.8 | 1.4 | 13.8 | -57.4 | -0.032 | N/A | 40 | Blocked-Investigation Required | 9.8571
BGW2U391 | 2019-03-21 11:19 | 39.5 | 32.9 | 1.8 | 25.8 | -14.4 | 7.392 | 23.1 | 25 | Surge | 14.3333
BGW2U440 | 2019-03-21 11:20 | 0.3 | 0.2 | 20.2 | 79.3 | -59.9 | 0.1 | 2.6 | 0 | Blocked-Investigation Required | 3.9257
BGW2U284 | 2019-03-21 11:21 | 59.1 | 41.4 | 0 | 0 | -62.6 | 0.53 | 13.1 | 99 | Blocked-Investigation Required | #DIV/0!
BGW2U399 | 2019-03-21 11:23 | 47.9 | 38 | 1.3 | 12.8 | -44.7 | 0.688 | 14.7 | 25 | Surge | 9.8462
BGW2U351 | 2019-03-21 11:24 | 1.8 | 1.4 | 17 | 79.8 | -62.1 | -0.028 | N/A | 0 | Blocked-Investigation Required | 4.6941
BHW2U352 | 2019-03-21 11:25 | 54.9 | 40.4 | 0.4 | 4.3 | -59.7 | 3.411 | 53.9 | 99 | OK- No Action Required | 10.75
BHW2U353 | 2019-03-21 11:26 | 57.2 | 41.2 | 0 | 1.6 | -57.7 | 5.817 | 43.2 | 99 | OK- No Action Required | #DIV/0!
BHW2U354 | 2019-03-21 11:28 | 47.5 | 37 | 1.4 | 14.1 | -10.3 | 1.613 | 22.9 | 22 | Adjusted Decrease | 10.0714
BGW1A004 | 2019-03-21 11:53 | 57.6 | 38.5 | 0 | 3.9 | -2.4 | 1.075 | 9.2 | 25 | Surge | #DIV/0!
BGW1A003 | 2019-03-21 11:54 | 60.4 | 37.8 | 0 | 1.8 | -23.3 | -0.036 | N/A | 99 | Blocked-Investigation Required | #DIV/0!
BGW1A005 | 2019-03-21 11:55 | 12.5 | 8.1 | 16.9 | 62.5 | -23.2 | -0.134 | N/A | 99 | Blocked-Investigation Required | 3.6982
BGW1A002 | 2019-03-21 11:56 | 9.1 | 5.7 | 17.9 | 67.3 | -23.3 | -0.145 | N/A | 30 | Blocked-Investigation Required | 3.7598
BGW1A001 | 2019-03-21 11:58 | 13.3 | 8.4 | 16.8 | 61.5 | -23.3 | -0.016 | N/A | 99 | Blocked-Investigation Required | 3.6607
BGW1A268 | 2019-03-21 11:59 | 53.6 | 34.8 | 1.1 | 10.5 | -8.1 | 1.662 | 2.8 | 5 | OK- No Action Required | 9.5455
BGW1A009 | 2019-03-21 12:00 | 60.7 | 37.5 | 0 | 1.8 | -23.4 | -0.017 | N/A | 99 | Blocked-Investigation Required | #DIV/0!
BGW1A269 | 2019-03-21 12:01 | 17.8 | 10.4 | 14.9 | 56.9 | -0.3 | -0.082 | N/A | 0 | Shut/Shut | 3.8188
BGW1AM01 | 2019-03-21 12:02 | 23.8 | 25.6 | 0.2 | 50.4 | -23.3 | 0.077 | 0.5 | 99 | OK- No Action Required | 252
BGW1A008 | 2019-03-21 12:04 | 52.2 | 35.5 | 0 | 12.3 | -12.2 | 2.373 | 13.6 | 25 | OK- No Action Required | #DIV/0!
BGW1A007 | 2019-03-21 12:04 | 1.4 | 1.1 | 16.2 | 81.3 | 0 | -0.116 | N/A | 0 | Shut/Shut | 5.0185
BGW1A006 | 2019-03-21 12:06 | 43.1 | 27.5 | 5.4 | 24 | -19.6 | -0.144 | N/A | 5 | Blocked-Investigation Required | 4.4444
BGW1B018 | 2019-03-21 12:09 | 60.4 | 36.6 | 0 | 3 | -22.5 | -0.158 | N/A | 40 | Blocked-Investigation Required | #DIV/0!
BGW1B017 | 2019-03-21 12:11 | 60.2 | 37.7 | 0 | 2.1 | -18.3 | 1.79 | 3 | 35 | Adjusted Increase | #DIV/0!
BGW1B011 | 2019-03-21 12:12 | 17.6 | 13.9 | 11.5 | 57 | -0.2 | 1.486 | 10.6 | 20 | OK- No Action Required | 4.9565
BGW1B010 | 2019-03-21 12:13 | 2 | 1.5 | 19.2 | 77.3 | -23.1 | 0.047 | 3.8 | 99 | Blocked-Investigation Required | 4.026
BGW1B013 | 2019-03-21 12:14 | 34 | 18.7 | 7.6 | 39.7 | 0 | -0.04 | N/A | 0 | Shut/Shut | 5.2237
BGW1B016 | 2019-03-21 12:16 | 54.1 | 35.7 | 0 | 10.2 | -17.6 | -0.242 | N/A | 20 | Blocked-Investigation Required | #DIV/0!
BGW1B019 | 2019-03-21 12:17 | 61.7 | 36.3 | 0 | 2 | -22.8 | 0.542 | 1.6 | 99 | Blocked-Investigation Required | #DIV/0!
BGW1B015 | 2019-03-21 12:18 | 62.9 | 35.1 | 0 | 2 | -23 | 0.027 | 0.3 | 99 | Blocked-Investigation Required | #DIV/0!
BGW1B020 | 2019-03-21 12:19 | 4.8 | 2.6 | 18.9 | 73.7 | -22.9 | -0.09 | N/A | 40 | Blocked-Investigation Required | 3.8995
BGW1B014 | 2019-03-21 12:20 | 13.9 | 7.7 | 16.2 | 62.2 | -0.1 | -0.02 | N/A | 0 | Shut/Shut | 3.8395
BGW1B012 | 2019-03-21 12:21 | 51.9 | 30.7 | 2.9 | 14.5 | -23 | -0.049 | N/A | 99 | Blocked-Investigation Required | 5
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0

## rungas Export
Asset ID | Monitor ID | Date Taken | Time Taken | Methane % | Carbon Dioxide % | Oxygen % | Balance Gas % | Pressure mbar | Diff Pressure scmh | Energy kW kW | Flow m3/h m3/h | Valve Position % open | Atmos Pressure mbar | Comments | X GPS text | Y GPS text

## rungas Import
Paste readings below - then choose correct heading above to ensure readings line up | [14 empty] | ID
Asset | Date/Time | Methane | Carbon Dioxide | Oxygen | Balance Gas | Pressure | Vacuum | Atmospheric Pressure | Differential Pressure | LFG Flow | Energy | Valve Position | Temperature | Comments | 2 Date/Time
BGW2I442 | 2018-07-31 14:32 | 56.6 | 40.7 | 0 | 2.7 | 0 | 0 | 998 | 22.16 | 2.3 | 13 | 3 | 16.9 | Adjusted Increase | 3 Methane
BGW2I369 | 2018-07-31 14:31 | 53.4 | 39.6 | 0 | 7 | -1.5 | 1.5 | 998 | -0.365 | 0 | 0 | 25 | 29.1 | Blocked-Investigation Required | 4 CO2
BGW2I445 | 2018-07-31 14:29 | 60.3 | 41.1 | 0 | 0 | -0.3 | 0.3 | 999 | 6.164 | 11.2 | 70 | 25 | 14.9 | Adjusted Increase | 5 O2
BGW2I370 | 2018-07-31 14:26 | 57.3 | 40.8 | 0 | 1.9 | -0.3 | 0.3 | 999 | 21.122 | 10.2 | 61 | 20 | 24.3 | Adjusted Increase | 6 Balance
BGW2I368 | 2018-07-31 14:24 | 55.6 | 39.7 | 0 | 4.7 | -0.2 | 0.2 | 998 | 2.188 | 6.5 | 38 | 10 | 19.5 | Adjusted Increase | 7 Pressure
BGW2K426 | 2018-07-31 14:20 | 56.5 | 40 | 0 | 3.5 | -0.2 | 0.2 | 998 | 19.853 | 10 | 59 | 12 | 17.5 | Adjusted Increase | 8 Diff Pressure
BGW2K429 | 2018-07-31 14:18 | 42 | 36 | 0 | 22 | 0 | 0 | 997 | 2.396 | 3.4 | 15 | 5 | 17.8 | OK- No Action Required | 9 Flow
BGW2J400 | 2018-07-31 14:15 | 48.1 | 39.1 | 0.7 | 12.1 | -0.2 | 0.2 | 998 | 2.08 | 12.5 | 63 | 25 | 27.9 | OK- No Action Required | 10 Energy kW
BGW2J408 | 2018-07-31 14:14 | 59.2 | 42.9 | 0 | 0 | -0.1 | 0.1 | 998 | 1.229 | 10 | 62 | 12 | 15.2 | Adjusted Increase | 11 Atm Pressure
BGW2J089 | 2018-07-31 14:12 | 48 | 37.7 | 0.8 | 13.5 | 0 | 0 | 998 | 1.854 | 12 | 60 | 15 | 21.8 | OK- No Action Required | 12 CO
BGW2J401 | 2018-07-31 14:10 | 60.1 | 41.9 | 0 | 0 | -52.1 | 52.1 | 997 | 3.697 | 16.9 | 106 | 45 | 17.3 | Adjusted Increase | 13 Valve Arrive
BGW2M432 | 2018-07-31 14:08 | 50.7 | 39.7 | 1.1 | 8.5 | -2.1 | 2.1 | 996 | 3.359 | 4.1 | 21 | 15 | 17.1 | OK- No Action Required | 14 Valve Depart
BGW2L417 | 2018-07-31 14:05 | 57.9 | 40.7 | 0.6 | 0.8 | -1 | 1 | 996 | 2.299 | 29.3 | 178 | 25 | 20.1 | OK- No Action Required | 15 Comment
BGW2L359 | 2018-07-31 14:03 | 58.1 | 42.7 | 0 | 0 | 0 | 0 | 997 | 19.96 | 10 | 61 | 5 | 16.5 | Adjusted Increase
BGW2L420 | 2018-07-31 14:01 | 52.1 | 38.2 | 0.1 | 9.6 | 0 | 0 | 998 | 20.566 | 10.2 | 56 | 5 | 15.2 | Adjusted Increase
BGW2H360 | 2018-07-31 13:57 | 51.5 | 38.3 | 0 | 10.2 | -0.6 | 0.6 | 998 | 5.418 | 5.2 | 28 | 25 | 17.3 | OK- No Action Required
BGW2F358 | 2018-07-31 13:31 | 49.4 | 39.2 | 0.1 | 11.3 | -0.4 | 0.4 | 999 | 1.048 | 9 | 46 | 15 | 23.8 | OK- No Action Required
BGW2K111 | 2018-07-31 13:27 | 56.2 | 39.1 | 0 | 4.7 | 0 | 0 | 998 | 3.978 | 8.8 | 52 | 20 | 20.5 | Adjusted Increase
BGW2W261 | 2018-07-31 13:23 | 43.3 | 36.7 | 0 | 20 | -2.6 | 2.6 | 998 | 4.181 | 17.7 | 80 | 25 | 28.4 | Adjusted Decrease
BGW2W246 | 2018-07-31 13:21 | 47.6 | 37.6 | 0 | 14.8 | -1.1 | 1.1 | 998 | 1.487 | 10.7 | 53 | 15 | 20.9 | Adjusted Decrease
BGW2U399 | 2018-07-31 13:17 | 58.8 | 43.5 | 1 | 0 | -60.2 | 60.2 | 999 | 0.072 | 5 | 31 | 25 | 17.6 | Blocked-Investigation Required
BHW2R409 | 2018-07-31 13:11 | 7.2 | 5.9 | 17.6 | 69.3 | -0.1 | 0.1 | 999 | 0.012 | 0.9 | 0 | 0 | 15.2 | Shut/Shut
BGW2R277 | 2018-07-31 13:10 | 12.9 | 13.5 | 11 | 62.6 | -4.8 | 4.8 | 999 | 1.19 | 0.5 | 0 | 5 | 15.8 | Adjusted Decrease
BGW2R437 | 2018-07-31 13:07 | 39.9 | 30.7 | 6.2 | 23.2 | -4 | 4 | 999 | 0.952 | 2.1 | 9 | 10 | 18.7 | Adjusted Decrease
BGW2R197 | 2018-07-31 13:05 | 46.7 | 37.4 | 0 | 15.9 | -3.8 | 3.8 | 999 | 3.277 | 33.7 | 164 | 40 | 33.7 | Adjusted Decrease
BGW2R208 | 2018-07-31 13:03 | 61.4 | 42.3 | 0 | 0 | -0.1 | 0.1 | 999 | 3.496 | 4.2 | 27 | 10 | 17 | Adjusted Increase
BGW2X264 | 2018-07-31 12:58 | 57.2 | 40.1 | 0 | 2.7 | -49.7 | 49.7 | 1000 | 23.421 | 146.1 | 875 | 90 | 32.9 | Adjusted Increase
BGW2T224 | 2018-07-31 12:54 | 59.2 | 42.1 | 0 | 0 | -0.5 | 0.5 | 1000 | 0.048 | 1.9 | 12 | 10 | 18.6 | Adjusted Increase
BGW2T387 | 2018-07-31 12:52 | 60.9 | 39.9 | 0 | 0 | -0.2 | 0.2 | 1000 | 0.101 | 2.9 | 18 | 5 | 16.9 | Adjusted Increase
BGW2T339 | 2018-07-31 12:50 | 44.4 | 36.2 | 0.1 | 19.3 | -5.6 | 5.6 | 1000 | 3.307 | 15.9 | 74 | 30 | 22.8 | Adjusted Decrease
BGW2T438 | 2018-07-31 12:48 | 48 | 37 | 0 | 15 | -0.3 | 0.3 | 1000 | 2.399 | 6.8 | 34 | 20 | 19.8 | Adjusted Decrease
BGW2X456 | 2018-07-31 12:41 | 57.2 | 36.1 | 1.4 | 5.3 | -0.2 | 0.2 | 1001 | 2.825 | 15 | 89 | 10 | 30.1 | Adjusted Increase
BGW2E395 | 2018-07-31 11:48 | 47.5 | 36 | 0.3 | 16.2 | -16.2 | 16.2 | 1000 | 10.786 | 28.6 | 142 | 42 | 26.8 | Adjusted Decrease
BGW2E356 | 2018-07-31 11:46 | 45.3 | 32.1 | 3.9 | 18.7 | 0 | 0 | 999 | 0.096 | 2.7 | 13 | 10 | 16.2 | Adjusted Decrease
BGW2Y482 | 2018-07-31 11:40 | 46.9 | 39.2 | 0 | 13.9 | -0.6 | 0.6 | 1000 | 7.774 | 24.2 | 119 | 42 | 26.8 | Adjusted Decrease
BGW2Y481 | 2018-07-31 11:38 | 18 | 29.4 | 0 | 52.6 | 0 | 0 | 999 | 0.08 | 2.4 | 4 | 5 | 15.2 | OK- No Action Required
BGW2Y483 | 2018-07-31 11:36 | 1.5 | 4.9 | 16.6 | 77 | -0.2 | 0.2 | 1000 | 1.893 | 12 | 1 | 10 | 16 | Damaged
BGW2Y311 | 2018-07-31 11:34 | 52.5 | 38.6 | 0.3 | 8.6 | -4.7 | 4.7 | 1001 | 2.94 | 14.6 | 80 | 20 | 43.7 | OK- No Action Required
BGW2P288 | 2018-07-31 11:28 | 50.4 | 37.3 | 1.1 | 11.2 | 0.1 | -0.1 | 1001 | 1.014 | 4.4 | 23 | 10 | 23.8 | OK- No Action Required
BGW2P280 | 2018-07-31 11:26 | 50.8 | 35.1 | 1.9 | 12.2 | -2.5 | 2.5 | 1001 | 4.932 | 42.2 | 224 | 40 | 30.2 | Adjusted Decrease
BGW2P333 | 2018-07-31 11:23 | 59.4 | 40.1 | 0.2 | 0.3 | -0.3 | 0.3 | 1001 | >>>> | 0 | 0 | 10 | 16.9 | Change Orife Plate Required
BGW2P293 | 2018-07-31 11:21 | 52.5 | 38.5 | 0 | 9 | -31.7 | 31.7 | 1002 | 9.795 | 58.4 | 321 | 80 | 28.5 | OK- No Action Required
BGW2Q338 | 2018-07-31 11:10 | 30.1 | 26.9 | 1.6 | 41.4 | -44.1 | 44.1 | 1002 | 0.878 | 17.5 | 55 | 30 | 14.9 | Surge
BGW2Q184 | 2018-07-31 11:08 | 51.5 | 37.8 | 1 | 9.7 | -0.8 | 0.8 | 1002 | 0.128 | 11.3 | 61 | 30 | 17.1 | Adjusted Decrease
BGW2Q204 | 2018-07-31 11:05 | 44.2 | 35.2 | 0.8 | 19.8 | -5.8 | 5.8 | 1002 | -0.025 | 0 | 0 | 10 | 14.6 | Blocked-Investigation Required
BGW2Q336 | 2018-07-31 11:02 | 56.7 | 40 | 0.2 | 3.1 | 0 | 0 | 1002 | 0.078 | 2.5 | 15 | 10 | 14.8 | OK- No Action Required
BGW2Q179 | 2018-07-31 11:00 | 39.9 | 31.3 | 0 | 28.8 | -0.8 | 0.8 | 1002 | 0.03 | 0.7 | 3 | 5 | 14 | OK- No Action Required
BGW2Q175 | 2018-07-31 10:59 | 31.5 | 26.8 | 0.2 | 41.5 | -0.4 | 0.4 | 1002 | 2.876 | 0.8 | 2 | 8 | 14.1 | Adjusted Decrease
BGW2Q199 | 2018-07-31 10:56 | 61.9 | 38.9 | 0 | 0 | -48.8 | 48.8 | 1002 | 0.597 | 6.9 | 44 | 40 | 15.8 | Adjusted Increase
BGW2Q190 | 2018-07-31 10:54 | 41.1 | 30.9 | 0 | 28 | -11.5 | 11.5 | 1002 | 2.026 | 27.2 | 117 | 45 | 18.4 | Adjusted Decrease
BGW2Q180 | 2018-07-31 10:52 | 4.6 | 6.4 | 13.1 | 75.9 | -0.2 | 0.2 | 1003 | 0.066 | 1.1 | 0 | 2 | 15.6 | Adjusted Increase
BGW2X459 | 2018-07-31 10:41 | 42.2 | 34.1 | 0 | 23.7 | -0.6 | 0.6 | 1003 | 5.4 | 10.1 | 44 | 15 | 23.3 | Adjusted Decrease
BHW2A350 | 2018-07-26 13:34 | 61.9 | 42.2 | 0 | 0 | -33.5 | 33.5 | 1008 | 12.4 | 107.4 | 697 | 99 | 34.2 | OK- No Action Required
BHW2A349 | 2018-07-26 13:33 | 61.7 | 42.5 | 0 | 0 | -44.1 | 44.1 | 1008 | -0.14 | 0 | 0 | 99 | 23.6 | Blocked-Investigation Required
BHW2A348 | 2018-07-26 13:32 | 58.7 | 41.4 | 0 | 0 | -30.2 | 30.2 | 1008 | 20.8 | 140 | 860 | 99 | 28.4 | OK- No Action Required
BHW2A347 | 2018-07-26 13:31 | 60.1 | 42.5 | 0 | 0 | -32.7 | 32.7 | 1008 | 17.35 | 126.9 | 799 | 99 | 32.1 | OK- No Action Required
BGW2Z346 | 2018-07-26 13:28 | 57.2 | 38.5 | 0 | 4.3 | -5.8 | 5.8 | 1008 | 3.82 | 17.4 | 104 | 28 | 25.8 | Adjusted Increase
BGW2Z345 | 2018-07-26 13:26 | 50.4 | 36.5 | 0 | 13.1 | -0.2 | 0.2 | 1008 | 2.3 | 13.4 | 70 | 20 | 25.6 | OK- No Action Required
BGW2Z344 | 2018-07-26 13:24 | 55.6 | 37.9 | 0 | 6.5 | -0.2 | 0.2 | 1008 | 2.05 | 12.7 | 74 | 25 | 25.3 | OK- No Action Required
BGW2Z343 | 2018-07-26 13:22 | 51.1 | 36.7 | 0 | 12.2 | -1.7 | 1.7 | 1008 | 8.79 | 26.2 | 140 | 40 | 25 | OK- No Action Required
BGW2Z342 | 2018-07-26 13:20 | 33.8 | 26.9 | 3.9 | 35.4 | 0 | 0 | 1008 | 0.21 | 4 | 14 | 10 | 24.3 | OK- No Action Required
BGW2Z341 | 2018-07-26 13:18 | 47.3 | 34.3 | 0.7 | 17.7 | 0 | 0 | 1009 | 1.38 | 10.4 | 51 | 25 | 23.2 | OK- No Action Required
BGW2E357 | 2018-07-26 13:09 | 45.2 | 35.4 | 0 | 19.4 | -2.1 | 2.1 | 1007 | 4.34 | 18.2 | 86 | 15 | 26.6 | OK- No Action Required
BGW2E395 | 2018-07-26 13:08 | 47.1 | 35.3 | 0.4 | 17.2 | -19.9 | 19.9 | 1007 | 16.21 | 35 | 173 | 30 | 27.9 | Adjusted Decrease
BGW2E356 | 2018-07-26 13:05 | 45.4 | 31.9 | 3.7 | 19 | -0.4 | 0.4 | 1007 | 0.78 | 7.9 | 37 | 5 | 17.8 | Adjusted Decrease
BGW2X458 | 2018-07-26 12:08 | 41.2 | 34.2 | 0 | 24.6 | -4.3 | 4.3 | 1008 | 8.96 | 12.7 | 55 | 10 | 33.5 | OK- No Action Required
BLW2X467 | 2018-07-26 12:06 | 0.2 | 0.1 | 20.4 | 79.3 | -64.7 | 64.7 | 1008 | -0.03 | 0 | 0 | 0 | 25.1 | Shut/Shut
BLW2X466 | 2018-07-26 12:05 | 0.2 | 0.1 | 20.2 | 79.5 | -64.6 | 64.6 | 1009 | -0.14 | 0 | 0 | 0 | 23.7 | Shut/Shut
BLW2X464 | 2018-07-26 12:03 | 0.6 | 0.4 | 20.1 | 78.9 | -65.6 | 65.6 | 1009 | -0.04 | 0 | 0 | 0 | 24.4 | Shut/Shut
BLW2X465 | 2018-07-26 12:02 | 58.8 | 39.8 | 0.1 | 1.3 | -69.2 | 69.2 | 1008 | 26.27 | 44.4 | 273 | 40 | 23 | Change Orife Plate Required
BGW2K117 | 2018-07-26 12:00 | 45.9 | 36 | 0 | 18.1 | -4.5 | 4.5 | 1008 | 6.74 | 23 | 110 | 25 | 18.7 | OK- No Action Required
BGW2K115 | 2018-07-26 11:57 | 50.2 | 37.2 | 0 | 12.6 | -0.1 | 0.1 | 1009 | 0.08 | 2.5 | 13 | 5 | 20.5 | OK- No Action Required
BGW2X457 | 2018-07-26 11:55 | 55.2 | 38.3 | 0 | 6.5 | -8.2 | 8.2 | 1009 | 21.47 | 40.5 | 234 | 50 | 34 | OK- No Action Required
BGW2X456 | 2018-07-26 11:52 | 42.6 | 27.9 | 5.8 | 23.7 | -0.4 | 0.4 | 1009 | 3.3 | 16 | 71 | 12 | 29.7 | Adjusted Decrease
BLW2X463 | 2018-07-26 11:50 | 0.1 | 0.1 | 20.5 | 79.3 | -65.6 | 65.6 | 1009 | -0.09 | 0 | 0 | 0 | 22.8 | Shut/Shut
BLW2X462 | 2018-07-26 11:49 | 0.1 | 0 | 20.5 | 79.4 | -65.2 | 65.2 | 1009 | 0.02 | 3.7 | 0 | 5 | 21.5 | OK- No Action Required
BLW2X461 | 2018-07-26 11:47 | 50.2 | 34.8 | 3.1 | 11.9 | -66.2 | 66.2 | 1010 | 3.17 | 54.3 | 286 | 99 | 19.9 | OK- No Action Required
BLW2X460 | 2018-07-26 11:44 | 0.1 | 0.1 | 20.7 | 79.1 | -66.8 | 66.8 | 1007 | -0.02 | 0 | 0 | 99 | 18.3 | OK- No Action Required
BGW2S216 | 2018-07-26 11:37 | 60 | 43.5 | 0 | 0 | -62.1 | 62.1 | 1007 | 0.61 | 23.4 | 147 | 99 | 29.6 | Blocked-Investigation Required
BGW2S206 | 2018-07-26 11:35 | 57.8 | 41.8 | 0.2 | 0.2 | 0 | 0 | 1007 | -0.03 | 0 | 0 | 0 | 23.5 | Shut/Shut
BHW2S411 | 2018-07-26 11:34 | 60.2 | 43.8 | 0 | 0 | -59.2 | 59.2 | 1007 | 1.87 | 11.6 | 73 | 99 | 30 | OK- No Action Required
BGW2S281 | 2018-07-26 11:33 | 56.8 | 39.9 | 1.3 | 2 | -62.6 | 62.6 | 1007 | 0.15 | 3.3 | 20 | 99 | 16.3 | Blocked-Investigation Required
BGW2S385 | 2018-07-26 11:32 | 51.1 | 37.6 | 0 | 11.3 | -40.4 | 40.4 | 1007 | 8.36 | 54.6 | 292 | 50 | 18.8 | Surge
BGW2S211 | 2018-07-26 11:30 | 61.2 | 43 | 0 | 0 | -61.9 | 61.9 | 1007 | 0.38 | 5.3 | 34 | 99 | 20.5 | Blocked-Investigation Required
BGW2S212 | 2018-07-26 11:29 | 0.2 | 2.8 | 18.7 | 78.3 | -2.6 | 2.6 | 1007 | -0.02 | 0 | 0 | 0 | 29.7 | Shut/Shut
BGW2S217 | 2018-07-26 11:28 | 48.7 | 37.2 | 0.4 | 13.7 | -23.5 | 23.5 | 1007 | 4.71 | 39.6 | 202 | 40 | 41.6 | OK- No Action Required
BGW2S223 | 2018-07-26 11:26 | 48.3 | 37.3 | 0 | 14.4 | -60.7 | 60.7 | 1007 | 3.74 | 56.9 | 288 | 99 | 38.2 | OK- No Action Required
BGW2S222 | 2018-07-26 11:25 | 51.8 | 40 | 0.2 | 8 | -0.6 | 0.6 | 1007 | 1.44 | 10.2 | 55 | 40 | 41.6 | OK- No Action Required
BGW2Y482 | 2018-07-26 10:54 | 44.8 | 38.4 | 0 | 16.8 | -1.6 | 1.6 | 1008 | 8.95 | 26 | 122 | 25 | 26.5 | OK- No Action Required
BGW2Y480 | 2018-07-26 10:53 | 54.8 | 41.3 | 0 | 3.9 | -1.4 | 1.4 | 1008 | 5.33 | 20.4 | 117 | 25 | 22.1 | OK- No Action Required
BGW2Y481 | 2018-07-26 10:52 | 14 | 28.2 | 0 | 57.8 | -0.4 | 0.4 | 1008 | 0.81 | 7.7 | 11 | 5 | 15.2 | Adjusted Decrease
BGW2Y478 | 2018-07-26 10:50 | 51.3 | 40 | 0 | 8.7 | -0.9 | 0.9 | 1008 | 0.63 | 7.1 | 38 | 10 | 15.6 | OK- No Action Required
BGW2Y483 | 2018-07-26 10:49 | 1 | 5 | 16.6 | 77.4 | -0.4 | 0.4 | 1008 | 0.17 | 3.6 | 0 | 2 | 15.2 | Adjusted Decrease
BGW2Y315 | 2018-07-26 10:47 | 57.4 | 41.1 | 0 | 1.5 | -38.4 | 38.4 | 1008 | 29.51 | 167.6 | 1007 | 99 | 21.7 | OK- No Action Required
BGW2Y311 | 2018-07-26 10:46 | 48.8 | 36.9 | 0.6 | 13.7 | -1.8 | 1.8 | 1008 | 2.8 | 14.3 | 73 | 15 | 44 | OK- No Action Required
BGW2Y318 | 2018-07-26 10:41 | 0.7 | 0.7 | 19.8 | 78.8 | -8.3 | 8.3 | 1008 | -0.04 | 0 | 0 | 0 | 16.7 | Shut/Shut
BGW2Y322 | 2018-07-26 10:40 | 0.4 | 0.4 | 19.2 | 80 | -19.4 | 19.4 | 1008 | -1.1 | 0 | 0 | 0 | 24.5 | Shut/Shut
BGW2Y329 | 2018-07-26 10:38 | 57.9 | 42.1 | 0 | 0 | -39.4 | 39.4 | 1008 | 28.09 | 157.2 | 954 | 99 | 44.7 | OK- No Action Required
BGW2Y271 | 2018-07-26 10:37 | 19.9 | 27.6 | 4.5 | 48 | -0.1 | 0.1 | 1009 | 0 | 0 | 0 | 5 | 17.7 | Blocked-Investigation Required
BGW2Z317 | 2018-07-26 10:33 | 60.6 | 39 | 0.4 | 0 | -16.7 | 16.7 | 1009 | 0.1 | 6.1 | 39 | 10 | 19 | OK- No Action Required
BGW2Z306 | 2018-07-26 10:32 | 47.7 | 35.6 | 0 | 16.7 | -12.5 | 12.5 | 1009 | 19.33 | 38.1 | 190 | 50 | 33.3 | OK- No Action Required
BGW2Z310 | 2018-07-26 10:30 | 51.3 | 36.5 | 0 | 12.2 | -10.1 | 10.1 | 1010 | 18.63 | 80.8 | 434 | 60 | 36 | OK- No Action Required
BGW2Z314 | 2018-07-26 10:29 | 47.1 | 36.4 | 0 | 16.5 | -3 | 3 | 1009 | 12.87 | 30.6 | 151 | 40 | 42.3 | OK- No Action Required
BGW2Z321 | 2018-07-26 10:28 | 51.1 | 38.6 | 0 | 10.3 | -41.9 | 41.9 | 1009 | 22.86 | 86.2 | 462 | 99 | 45.2 | OK- No Action Required
BGW2Z327 | 2018-07-26 10:26 | 23.7 | 27.8 | 0 | 48.5 | -58.3 | 58.3 | 1009 | 0.3 | 9.7 | 24 | 99 | 34.9 | Blocked-Investigation Required
BGW2Z324 | 2018-07-26 10:25 | 2.8 | 21 | 0 | 76.2 | -1.5 | 1.5 | 1009 | -0.22 | 0 | 0 | 5 | 28.3 | Blocked-Investigation Required
BGW2Z320 | 2018-07-26 10:24 | 62.9 | 39.8 | 0 | 0 | -44.1 | 44.1 | 1009 | 6.76 | 22.7 | 150 | 99 | 30.5 | OK- No Action Required
BGW2Z313 | 2018-07-26 10:22 | 53.1 | 37 | 0 | 9.9 | -24.6 | 24.6 | 1009 | 7.42 | 50.9 | 283 | 40 | 33.1 | OK- No Action Required
BGW2Z479 | 2018-07-26 10:21 | 50.5 | 37.6 | 0.2 | 11.7 | -3.3 | 3.3 | 1009 | 13.57 | 32.7 | 173 | 40 | 20.9 | OK- No Action Required
BGW2Z328 | 2018-07-26 10:19 | 55.3 | 39.7 | 0.1 | 4.9 | -22 | 22 | 1009 | 15.77 | 33.9 | 196 | 40 | 42.1 | OK- No Action Required
BGW2P288 | 2018-07-26 09:31 | 36 | 29 | 4.4 | 30.6 | -0.5 | 0.5 | 1009 | 4.39 | 9 | 34 | 15 | 26.3 | Adjusted Decrease
BGW2P280 | 2018-07-26 09:29 | 47.3 | 33.3 | 3.1 | 16.3 | -3.5 | 3.5 | 1009 | 6.32 | 47.4 | 235 | 40 | 31.3 | Adjusted Decrease
BGW2P269 | 2018-07-26 09:26 | 25.2 | 18.2 | 13.3 | 43.3 | -60.6 | 60.6 | 1009 | -0.15 | 0 | 0 | 50 | 18.3 | Blocked-Investigation Required
BGW2P477 | 2018-07-26 09:25 | 53.2 | 39.4 | 0 | 7.4 | -4 | 4 | 1009 | 3.69 | 36.3 | 202 | 40 | 28.8 | OK- No Action Required
BGW2P283 | 2018-07-26 09:24 | 48.1 | 37.2 | 0.2 | 14.5 | -32.9 | 32.9 | 1009 | 5.39 | 42.5 | 214 | 50 | 35.9 | OK- No Action Required
BGW2P333 | 2018-07-26 09:22 | 59.1 | 39.8 | 0.2 | 0.9 | -0.3 | 0.3 | 1009 | 22.08 | 2.3 | 14 | 12 | 16 | Adjusted Increase
BGW2P334 | 2018-07-26 09:20 | 44 | 36 | 0 | 20 | -1.9 | 1.9 | 1009 | 1.73 | 5.7 | 26 | 10 | 21.4 | OK- No Action Required
BGW2P286 | 2018-07-26 09:18 | 62 | 40.4 | 0 | 0 | -60.4 | 60.4 | 1009 | 0.77 | 27.4 | 178 | 99 | 16.9 | OK- No Action Required
BGW2P447 | 2018-07-26 09:17 | 0.3 | 0.3 | 20.5 | 78.9 | -41 | 41 | 1009 | 0.95 | 0.4 | 0 | 0 | 15.1 | Open/Shut
BGW2P290 | 2018-07-26 09:15 | 55.6 | 38.4 | 0 | 6 | -4.8 | 4.8 | 1009 | 7.76 | 24.9 | 145 | 25 | 20.3 | Surge
BGW2P293 | 2018-07-26 09:14 | 39.9 | 28.7 | 5.9 | 25.5 | -1 | 1 | 1009 | 1.22 | 21.1 | 88 | 20 | 21.4 | Adjusted Decrease
BGW2P291 | 2018-07-26 09:12 | 54.5 | 40.2 | 0 | 5.3 | -0.7 | 0.7 | 1009 | 1.74 | 11.5 | 66 | 25 | 28.4 | OK- No Action Required
BGW2P295 | 2018-07-26 09:10 | 54 | 38.8 | 0 | 7.2 | -31.2 | 31.2 | 1008 | 9.56 | 94.7 | 536 | 80 | 27.9 | OK- No Action Required
BHW2R409 | 2018-07-26 09:08 | 21 | 19.2 | 10 | 49.8 | -0.9 | 0.9 | 1008 | 0.63 | 6.8 | 15 | 0 | 31.8 | Open/Shut
BHW2R410 | 2018-07-26 09:06 | 48.2 | 39 | 0 | 12.8 | -37.1 | 37.1 | 1008 | 30.54 | 162.2 | 819 | 99 | 44.5 | OK- No Action Required
BGW2R277 | 2018-07-26 09:05 | 11.4 | 13.5 | 11.7 | 63.4 | -8.5 | 8.5 | 1008 | 11.06 | 1.6 | 1 | 5 | 13.6 | Adjusted Decrease
BGW2R437 | 2018-07-26 09:02 | 44.5 | 33.5 | 5.2 | 16.8 | -6.6 | 6.6 | 1009 | 19.32 | 9.8 | 45 | 10 | 18.4 | Adjusted Decrease
BGW2R201 | 2018-07-26 09:00 | 48 | 38.5 | 0 | 13.5 | -3.2 | 3.2 | 1009 | 1.46 | 22.4 | 112 | 20 | 35.7 | OK- No Action Required
BGW2R197 | 2018-07-26 08:59 | 45.6 | 37.4 | 0 | 17 | -4.9 | 4.9 | 1008 | 3.3 | 34.4 | 164 | 25 | 20 | OK- No Action Required
BGW2R192 | 2018-07-26 08:49 | 48 | 36.7 | 2.3 | 13 | -0.2 | 0.2 | 1008 | 3.7 | 8.4 | 42 | 15 | 19.4 | OK- No Action Required
BGW2R436 | 2018-07-26 08:47 | 51.7 | 37.8 | 0 | 10.5 | -7.6 | 7.6 | 1008 | 5.23 | 43.6 | 236 | 40 | 23.5 | OK- No Action Required
BGW2R202 | 2018-07-26 08:46 | 50.2 | 38.4 | 0 | 11.4 | -61.2 | 61.2 | 1008 | 0.45 | 12.3 | 65 | 70 | 26.9 | OK- No Action Required
BGW2R384 | 2018-07-26 08:44 | 51.6 | 37.7 | 0.5 | 10.2 | -3 | 3 | 1008 | 1.03 | 19.8 | 107 | 25 | 10.3 | OK- No Action Required
BGW2R208 | 2018-07-26 08:43 | 39.3 | 29.6 | 5.1 | 26 | -0.2 | 0.2 | 1009 | 4.56 | 4.7 | 19 | 5 | 17.4 | Adjusted Decrease
BGW2R207 | 2018-07-26 08:41 | 37.9 | 34.6 | 0 | 27.5 | -0.6 | 0.6 | 1008 | 7 | 5.7 | 22 | 10 | 26.8 | OK- No Action Required
BGW2J400 | 2018-07-25 15:55 | 38.1 | 34.1 | 1.3 | 26.5 | -1.4 | 1.4 | 1004 | 3.18 | 15.3 | 61 | 22 | 29.8 | Adjusted Decrease
BGW2J430 | 2018-07-25 15:53 | 47.5 | 38 | 0 | 14.5 | -2.6 | 2.6 | 1004 | 1.27 | 10 | 50 | 25 | 14.3 | OK- No Action Required
BGW2J408 | 2018-07-25 15:52 | 47.1 | 36.5 | 2.5 | 13.9 | -0.2 | 0.2 | 1004 | 1.53 | 11 | 54 | 15 | 14.7 | Adjusted Decrease
BGW2J089 | 2018-07-25 15:50 | 28.4 | 27.5 | 3.8 | 40.3 | -0.5 | 0.5 | 1004 | 3.47 | 16.2 | 48 | 15 | 22.7 | Adjusted Decrease
BGW2J401 | 2018-07-25 15:48 | 21.5 | 15.4 | 11.4 | 51.7 | -62.8 | 62.8 | 1004 | 0.13 | 3.1 | 7 | 40 | 17.1 | Blocked-Investigation Required
BGW2J091 | 2018-07-25 15:47 | 46.6 | 36.1 | 0.3 | 17 | -1.3 | 1.3 | 1004 | 0.35 | 18.5 | 90 | 25 | 22.2 | OK- No Action Required
BGW2J087 | 2018-07-25 15:46 | 50.3 | 39 | 0.7 | 10 | -0.8 | 0.8 | 1004 | 3.07 | 7.7 | 40 | 15 | 19.3 | OK- No Action Required
BGW2J090 | 2018-07-25 15:44 | 51.2 | 37.7 | 0.4 | 10.7 | -4.8 | 4.8 | 1004 | 9.64 | 27.1 | 145 | 25 | 30.1 | OK- No Action Required
BGW2M128 | 2018-07-25 15:35 | 51.4 | 36.2 | 2.8 | 9.6 | -12.8 | 12.8 | 1003 | 0.05 | 2 | 11 | 5 | 16.8 | Blocked-Investigation Required
BGW2M083 | 2018-07-25 15:34 | 59.5 | 42.9 | 0 | 0 | -0.4 | 0.4 | 1003 | 0 | 0 | 0 | 5 | 27.7 | Blocked-Investigation Required
BGW2M434 | 2018-07-25 15:33 | 55.3 | 40.1 | 0 | 4.6 | -1.5 | 1.5 | 1003 | 10.42 | 28.3 | 164 | 25 | 31.1 | OK- No Action Required
BGW2M131 | 2018-07-25 15:31 | 41.1 | 35.2 | 0 | 23.7 | -0.1 | 0.1 | 1003 | 6.53 | 11 | 47 | 15 | 24 | OK- No Action Required
BGW2M432 | 2018-07-25 15:30 | 45.4 | 37.4 | 1 | 16.2 | -3.9 | 3.9 | 1003 | 3.69 | 4.2 | 20 | 5 | 17.6 | Adjusted Decrease
BGW2M397 | 2018-07-25 15:27 | 49.3 | 40 | 0 | 10.7 | -46.8 | 46.8 | 1003 | 7.85 | 23 | 118 | 60 | 49.4 | OK- No Action Required
BGW2M124 | 2018-07-25 15:26 | 53 | 39.6 | 1.2 | 6.2 | -2.4 | 2.4 | 1003 | 0.05 | 4.2 | 23 | 20 | 22.8 | OK- No Action Required
BGW2M381 | 2018-07-25 15:25 | 54.1 | 40.9 | 0 | 5 | -19.1 | 19.1 | 1003 | 16.05 | 33.9 | 192 | 40 | 45 | OK- No Action Required
BGW2M450 | 2018-07-25 15:23 | 55.7 | 41.3 | 1.1 | 1.9 | -45.9 | 45.9 | 1004 | 4.13 | 4.4 | 25 | 25 | 22.7 | OK- No Action Required
BGW2M435 | 2018-07-25 15:22 | 0.7 | 0.6 | 20.3 | 78.4 | -1.6 | 1.6 | 1003 | 0 | 0 | 0 | 0 | 15.5 | Shut/Shut
BGW2L053 | 2018-07-25 15:19 | 58.1 | 41.1 | 0 | 0.8 | -66.4 | 66.4 | 1003 | -0.01 | 0 | 0 | 40 | 22.8 | Blocked-Investigation Required
BGW2L433 | 2018-07-25 15:18 | 38.9 | 30.9 | 4.6 | 25.6 | -1.3 | 1.3 | 1003 | 6.5 | 22.3 | 91 | 22 | 24.8 | Adjusted Decrease
BGW2L376 | 2018-07-25 15:16 | 45.2 | 36.8 | 0.6 | 17.4 | -0.6 | 0.6 | 1003 | 15.3 | 8.6 | 41 | 12 | 23 | Adjusted Decrease
BGW2L150 | 2018-07-25 15:14 | 54.2 | 40.5 | 0 | 5.3 | -64.3 | 64.3 | 1003 | 2.49 | 46.4 | 264 | 99 | 39.2 | OK- No Action Required
BGW2L448 | 2018-07-25 15:13 | 53.5 | 39.7 | 0 | 6.8 | -18.9 | 18.9 | 1003 | 9.94 | 58.8 | 330 | 50 | 31.8 | OK- No Action Required
BGW2L082 | 2018-07-25 15:11 | 58.4 | 42 | 0 | 0 | -40.1 | 40.1 | 1003 | 18.45 | 37.5 | 229 | 99 | 22.8 | OK- No Action Required
BGW2L056 | 2018-07-25 15:10 | 29.8 | 31.6 | 0 | 38.6 | -0.1 | 0.1 | 1003 | 22.13 | 10.2 | 32 | 15 | 21.7 | OK- No Action Required
BGW2L417 | 2018-07-25 15:09 | 44.9 | 32.9 | 4.5 | 17.7 | -1.3 | 1.3 | 1003 | 1.8 | 25.7 | 121 | 30 | 18.7 | OK- No Action Required
BGW2L137 | 2018-07-25 15:07 | 51.2 | 38.8 | 0.2 | 9.8 | -32.8 | 32.8 | 1003 | 1.75 | 41.1 | 220 | 50 | 15.9 | OK- No Action Required
BGW2L359 | 2018-07-25 15:06 | 36 | 31.7 | 1.7 | 30.6 | -0.3 | 0.3 | 1003 | 6.71 | 5.7 | 21 | 5 | 15.9 | Adjusted Decrease
BGW2L420 | 2018-07-25 15:04 | 9.8 | 7.2 | 16.8 | 66.2 | -0.2 | 0.2 | 1003 | 15.84 | 8.8 | 9 | 5 | 15.8 | Adjusted Decrease
BGW2L377 | 2018-07-25 15:02 | 50.4 | 39.1 | 0 | 10.5 | -0.2 | 0.2 | 1003 | 1.7 | 11.3 | 60 | 20 | 31.2 | OK- No Action Required
BGW2L101 | 2018-07-25 15:01 | 1.5 | 1.1 | 19.9 | 77.5 | -0.1 | 0.1 | 1003 | 0 | 0 | 0 | 0 | 17.6 | Shut/Shut
BGW2L140 | 2018-07-25 15:00 | 59.5 | 43.7 | 0 | 0 | -38.5 | 38.5 | 1003 | 0.87 | 2 | 12 | 5 | 22.5 | OK- No Action Required
BGW2L378 | 2018-07-25 14:58 | 50.3 | 39.7 | 0 | 10 | -0.8 | 0.8 | 1003 | 2.89 | 14.4 | 76 | 15 | 46.1 | OK- No Action Required
BGW2L431 | 2018-07-25 14:57 | 55.1 | 39.4 | 0 | 5.5 | -46.1 | 46.1 | 1003 | 12.26 | 103.2 | 596 | 80 | 47.7 | OK- No Action Required
BGW2L133 | 2018-07-25 14:55 | 48.8 | 38.3 | 0 | 12.9 | -1 | 1 | 1003 | 7.72 | 11.8 | 60 | 25 | 40.1 | OK- No Action Required
BGW2L134 | 2018-07-25 14:54 | 46.7 | 36.7 | 0.2 | 16.4 | -0.7 | 0.7 | 1004 | 0.61 | 14.6 | 71 | 15 | 33.8 | OK- No Action Required
BGW2L380 | 2018-07-25 14:52 | 38.6 | 34.2 | 2.2 | 25 | 0 | 0 | 1004 | -4.95 | 0 | 0 | 5 | 13.8 | OK- No Action Required
BHW3A455 | 2018-07-25 11:49 | 63.2 | 43.9 | 0 | 0 | -70.2 | 70.2 | 1005 | 3.82 | 36 | 239 | 99 | 27.9 | OK- No Action Required
BHW3A454 | 2018-07-25 11:47 | 62.1 | 45.5 | 0 | 0 | -69 | 69 | 1005 | 6.75 | 47.7 | 310 | 99 | 26.5 | OK- No Action Required
BHW3A453 | 2018-07-25 11:46 | 62.5 | 46.2 | 0 | 0 | -58.1 | 58.1 | 1005 | 22.41 | 88.5 | 580 | 99 | 19 | Change Orife Plate Required
BHW3A452 | 2018-07-25 11:45 | 48.3 | 43.4 | 0 | 8.3 | -7.9 | 7.9 | 1005 | 9 | 56.4 | 285 | 50 | 17.8 | OK- No Action Required
BHW3A451 | 2018-07-25 11:44 | 58.1 | 47 | 0 | 0 | -75.3 | 75.3 | 1005 | -0.07 | 0 | 0 | 99 | 17.9 | Blocked-Investigation Required
BHW2U354 | 2018-07-25 11:40 | 49 | 37.7 | 1.3 | 12 | -45 | 45 | 1005 | 18.48 | 76.2 | 391 | 99 | 53 | OK- No Action Required
BHW2U353 | 2018-07-25 11:38 | 59.8 | 42.3 | 0 | 0 | -51.8 | 51.8 | 1005 | 7.8 | 50.6 | 317 | 99 | 44.3 | OK- No Action Required
BHW2U352 | 2018-07-25 11:37 | 57.9 | 41.7 | 0.2 | 0.2 | -50.9 | 50.9 | 1005 | 8.33 | 85.2 | 517 | 99 | 44.6 | OK- No Action Required
BGW2U351 | 2018-07-25 11:36 | 42 | 33.1 | 2 | 22.9 | -3.4 | 3.4 | 1005 | -3.32 | 0 | 0 | 0 | 32.3 | Shut/Shut
BGW2U399 | 2018-07-25 11:34 | 41.2 | 32.3 | 4.9 | 21.6 | -27.7 | 27.7 | 1005 | -1.21 | 0 | 0 | 15 | 46.8 | Surge
BGW2U284 | 2018-07-25 11:32 | 61.4 | 42.8 | 0 | 0 | -59.9 | 59.9 | 1005 | 0.37 | 11.1 | 71 | 99 | 37.8 | Blocked-Investigation Required
BGW2U440 | 2018-07-25 11:31 | 0.4 | 0.3 | 20.3 | 79 | -52.2 | 52.2 | 1005 | 0.07 | 2.2 | 0 | 0 | 16.4 | Shut/Shut
BGW2U391 | 2018-07-25 11:30 | 47.1 | 38.6 | 0.5 | 13.8 | -1 | 1 | 1005 | 1.02 | 8.9 | 44 | 20 | 17.7 | OK- No Action Required
BGW2U245 | 2018-07-25 11:28 | 46.8 | 36.4 | 2.1 | 14.7 | -26.4 | 26.4 | 1005 | 0.7 | 15.2 | 74 | 50 | 41.9 | Surge
BGW2U251 | 2018-07-25 11:27 | 53.6 | 41.7 | 0 | 4.7 | -58.3 | 58.3 | 1005 | 4.63 | 38.5 | 216 | 99 | 41.2 | OK- No Action Required
BGW2U241 | 2018-07-25 11:26 | 0.2 | 0.1 | 20.9 | 78.8 | -22.1 | 22.1 | 1005 | -0.06 | 0 | 0 | 0 | 17.5 | Shut/Shut
BGW2U439 | 2018-07-25 11:25 | 0.3 | 0.2 | 20.3 | 79.2 | 0 | 0 | 1005 | -0.1 | 0 | 0 | 0 | 17.7 | Shut/Shut
BGW2U226 | 2018-07-25 11:24 | 20.6 | 14.2 | 18.1 | 47.1 | -55.4 | 55.4 | 1005 | -0.07 | 0 | 0 | 0 | 20.4 | Shut/Shut
BGW2U232 | 2018-07-25 11:22 | 60.1 | 41.8 | 0 | 0 | -60.6 | 60.6 | 1005 | 1.87 | 40.8 | 257 | 99 | 37.2 | OK- No Action Required
BGW2U227 | 2018-07-25 11:21 | 49.3 | 37.9 | 0 | 12.8 | -5.5 | 5.5 | 1005 | 8.99 | 26.6 | 137 | 25 | 18.2 | OK- No Action Required
BGW2U238 | 2018-07-25 11:20 | 45.2 | 35.9 | 0.5 | 18.4 | -2.9 | 2.9 | 1005 | 4.22 | 18.1 | 86 | 15 | 20.8 | OK- No Action Required
BGW2U398 | 2018-07-25 11:18 | 47.7 | 37.4 | 0.6 | 14.3 | -6.2 | 6.2 | 1005 | 1.4 | 22.6 | 113 | 25 | 16.1 | OK- No Action Required
BGW2U243 | 2018-07-25 11:17 | 55.4 | 40.6 | 0 | 4 | -2.8 | 2.8 | 1005 | 1.58 | 24.1 | 140 | 25 | 19.6 | OK- No Action Required
BGW2T219 | 2018-07-25 10:33 | 46.4 | 35.8 | 0 | 17.8 | -2.7 | 2.7 | 1006 | 4.2 | 9 | 43 | 10 | 18.1 | OK- No Action Required
BGW2T220 | 2018-07-25 10:32 | 52.3 | 35.5 | 0 | 12.2 | -1 | 1 | 1006 | 0.57 | 14.8 | 81 | 10 | 14.4 | OK- No Action Required
BGW2T224 | 2018-07-25 10:30 | 49.5 | 36.4 | 3.1 | 11 | -0.8 | 0.8 | 1006 | 0.15 | 3.4 | 17 | 12 | 17.9 | Adjusted Decrease
BGW2T228 | 2018-07-25 10:29 | 12.4 | 8.8 | 16.2 | 62.6 | -67.3 | 67.3 | 1006 | -0.07 | 0 | 0 | 99 | 16.1 | Blocked-Investigation Required
BGW2T387 | 2018-07-25 10:27 | 46 | 31.7 | 4.6 | 17.7 | -0.2 | 0.2 | 1006 | 0.06 | 2.2 | 10 | 5 | 16.4 | Adjusted Decrease
BGW2T339 | 2018-07-25 10:26 | 45.6 | 36.3 | 0 | 18.1 | -6.5 | 6.5 | 1006 | 4.09 | 17.8 | 85 | 25 | 21.9 | OK- No Action Required
BGW2T438 | 2018-07-25 10:24 | 43.3 | 35.5 | 2 | 19.2 | -0.7 | 0.7 | 1006 | 3.56 | 8.2 | 37 | 22 | 17.9 | Adjusted Decrease
BGW2T229 | 2018-07-25 10:22 | 0.3 | 0.3 | 20.7 | 78.7 | -0.2 | 0.2 | 1006 | 0.05 | 2 | 0 | 0 | 15.3 | Shut/Shut
BGW2T230 | 2018-07-25 10:21 | 45.9 | 33.1 | 0 | 21 | -0.8 | 0.8 | 1006 | 2.07 | 12.9 | 62 | 15 | 14.7 | OK- No Action Required
BGW2T235 | 2018-07-25 10:20 | 10.8 | 6.6 | 17 | 65.6 | 0 | 0 | 1006 | 0 | 0 | 0 | 0 | 16.5 | Shut/Shut
BLW2X468 | 2018-07-25 10:19 | 53.9 | 38.6 | 0.7 | 6.8 | -11.7 | 11.7 | 1006 | 4.36 | 18.6 | 105 | 25 | 18.8 | OK- No Action Required
BGW2T234 | 2018-07-25 10:17 | 51.3 | 40 | 0.2 | 8.5 | -1 | 1 | 1007 | 1.32 | 10.1 | 54 | 20 | 22 | OK- No Action Required
BGW2X166 | 2018-07-25 10:15 | 44.3 | 36.4 | 0 | 19.3 | -0.5 | 0.5 | 1007 | 0.4 | 11.7 | 54 | 15 | 29.7 | OK- No Action Required
BGW2X159 | 2018-07-25 10:13 | 45.9 | 35.9 | 0 | 18.2 | -1.8 | 1.8 | 1007 | 5.72 | 20.6 | 99 | 20 | 36 | OK- No Action Required
BGW2X160 | 2018-07-25 10:10 | 0.2 | 0.1 | 20.7 | 79 | -0.4 | 0.4 | 1007 | 0.25 | 0.2 | 0 | 0 | 13.1 | Shut/Shut
BGW2X161 | 2018-07-25 10:06 | 48 | 34.8 | 0 | 17.2 | -4 | 4 | 1007 | 2.04 | 6.2 | 31 | 15 | 26.7 | OK- No Action Required
BGW2X162 | 2018-07-25 10:04 | 50.2 | 36.2 | 0 | 13.6 | -1.6 | 1.6 | 1007 | 1.39 | 10.6 | 56 | 20 | 15.6 | OK- No Action Required
BGW2X167 | 2018-07-25 10:02 | 50.8 | 37.7 | 0.1 | 11.4 | -4.8 | 4.8 | 1007 | 1.49 | 22.4 | 119 | 30 | 44.1 | OK- No Action Required
BGW2Q168 | 2018-07-25 09:59 | 60.4 | 41.2 | 0 | 0 | -55.1 | 55.1 | 1007 | 0.29 | 10.2 | 64 | 99 | 14.3 | Blocked-Investigation Required
BGW2Q444 | 2018-07-25 09:57 | 55.2 | 36.7 | 0.1 | 8 | -3.6 | 3.6 | 1007 | 1 | 9.1 | 52 | 15 | 15.5 | OK- No Action Required
BGW2Q337 | 2018-07-25 09:56 | 1.4 | 6.7 | 18.7 | 73.2 | 0 | 0 | 1007 | -0.02 | 0 | 0 | 0 | 13.6 | Shut/Shut
BGW2Q338 | 2018-07-25 09:55 | 31.1 | 28.1 | 1.6 | 39.2 | -49.9 | 49.9 | 1007 | 1.04 | 19 | 62 | 20 | 14.5 | Adjusted Decrease
BGW2Q189 | 2018-07-25 09:53 | 0.2 | 0.2 | 21 | 78.6 | -8.7 | 8.7 | 1007 | 0.14 | 0.1 | 0 | 5 | 15.3 | OK- No Action Required
BGW2Q184 | 2018-07-25 09:52 | 48.5 | 36.3 | 1.8 | 13.4 | -1.8 | 1.8 | 1007 | 0.3 | 17.2 | 87 | 17 | 17.2 | Adjusted Decrease
BGW2Q382 | 2018-07-25 09:50 | 59.6 | 40.3 | 4.9 | 0 | 0 | 0 | 1007 | 0.05 | 2 | 12 | 0 | 25.8 | Shut/Shut
BGW2Q203 | 2018-07-25 09:49 | 60.2 | 41.7 | 0 | 0 | -43.1 | 43.1 | 1007 | 8.94 | 55.3 | 349 | 99 | 34.7 | OK- No Action Required
BGW2Q214 | 2018-07-25 09:47 | 48.8 | 36 | 0 | 15.2 | -15.1 | 15.1 | 1007 | 0.47 | 12.9 | 66 | 20 | 22.7 | OK- No Action Required
BGW2Q204 | 2018-07-25 09:46 | 34.9 | 31 | 2.4 | 31.7 | -5.2 | 5.2 | 1007 | 0.08 | 2.5 | 9 | 7 | 14.9 | Adjusted Decrease
BGW2Q336 | 2018-07-25 09:44 | 58.2 | 40.3 | 0 | 1.5 | 0 | 0 | 1007 | 0.11 | 3 | 18 | 10 | 14.7 | OK- No Action Required
BGW2Q335 | 2018-07-25 09:41 | 51 | 37.5 | 0 | 11.5 | -4.7 | 4.7 | 1007 | 4.07 | 39 | 208 | 40 | 15.1 | OK- No Action Required
BGW2Q179 | 2018-07-25 09:40 | 35.2 | 28.8 | 2.6 | 33.4 | -1.9 | 1.9 | 1007 | 0.1 | 1.3 | 5 | 2 | 14.2 | Adjusted Decrease
BGW2Q175 | 2018-07-25 09:38 | 25 | 24.5 | 0.7 | 49.8 | -1.1 | 1.1 | 1007 | 6.12 | 1.2 | 3 | 5 | 14.3 | Adjusted Decrease
BGW2Q199 | 2018-07-25 09:36 | 59.7 | 38.5 | 0 | 1.8 | -25 | 25 | 1007 | 0.36 | 5.4 | 34 | 30 | 15.7 | Adjusted Increase
BGW2Q190 | 2018-07-25 09:34 | 38.3 | 30.8 | 0 | 30.9 | -16.4 | 16.4 | 1007 | 3.59 | 35.9 | 144 | 40 | 18.7 | Adjusted Decrease
BGW2Q180 | 2018-07-25 09:32 | 16.6 | 12.7 | 10 | 60.7 | -0.3 | 0.3 | 1007 | 0.09 | 1.3 | 2 | 2 | 14.2 | Adjusted Decrease
BGW2Q185 | 2018-07-25 09:31 | 51.1 | 32.5 | 0 | 16.4 | -9.8 | 9.8 | 1007 | >>>> | 0 | 0 | 99 | 14.7 | OK- No Action Required
BGW2Q209 | 2018-07-25 09:29 | 31 | 23.2 | 6.8 | 39 | -49.3 | 49.3 | 1007 | 0.21 | 8.6 | 28 | 2 | 17.2 | Blocked-Investigation Required
BGW2X459 | 2018-07-24 14:15 | 55.8 | 38.9 | 0 | 5.3 | 0.3 | -0.3 | 995 | 3.36 | 8.1 | 47 | 15 | 19.4 | Adjusted Increase
BGW2K111 | 2018-07-24 14:12 | 61.7 | 41 | 0 | 0 | 0 | 0 | 996 | 1.45 | 5.4 | 34 | 15 | 19.1 | Adjusted Increase
BGW2X249 | 2018-07-24 14:08 | 55 | 36.5 | 0 | 8.5 | -3.2 | 3.2 | 994 | 7.15 | 24.2 | 139 | 25 | 17.5 | OK- No Action Required
BGW2X164 | 2018-07-24 14:00 | 57.3 | 40.9 | 0 | 1.8 | -73.6 | 73.6 | 995 | -0.51 | 0 | 0 | 99 | 21.3 | Blocked-Investigation Required
BGW2X441 | 2018-07-24 13:58 | 52 | 38.5 | 0 | 9.5 | -38.3 | 38.3 | 995 | 2.22 | 12.9 | 70 | 50 | 26.7 | OK- No Action Required
BGW2X158 | 2018-07-24 13:57 | 18 | 10.4 | 15.2 | 56.4 | -0.5 | 0.5 | 994 | -0.22 | 0 | 0 | 0 | 16.3 | Shut/Shut
BGW2X157 | 2018-07-24 13:56 | 42.2 | 34.3 | 0 | 23.5 | -13.2 | 13.2 | 994 | 6.85 | 5.7 | 25 | 15 | 18.7 | OK- No Action Required
BGW2X443 | 2018-07-24 13:55 | 53 | 40.2 | 0 | 6.8 | -27.4 | 27.4 | 994 | 5.11 | 19.3 | 107 | 40 | 35.9 | OK- No Action Required
BGW2X446 | 2018-07-24 13:53 | 52.8 | 39.7 | 0 | 7.5 | -22.2 | 22.2 | 994 | 7.55 | 24.1 | 133 | 40 | 22.3 | OK- No Action Required
BGW2X425 | 2018-07-24 13:52 | 59.4 | 42.5 | 0 | 0 | -3.7 | 3.7 | 994 | -0.25 | 0 | 0 | 8 | 21.2 | Blocked-Investigation Required
BGW2X264 | 2018-07-24 13:50 | 59.3 | 41.2 | 0 | 0 | -33.3 | 33.3 | 995 | 17.13 | 126.4 | 786 | 90 | 31.9 | Adjusted Increase
BGW2X247 | 2018-07-24 13:47 | 47.7 | 37.6 | 0 | 14.7 | -0.1 | 0.1 | 995 | 0.82 | 8 | 40 | 10 | 19.6 | OK- No Action Required
BGW2X239 | 2018-07-24 13:46 | 49.4 | 37.9 | 0.1 | 12.6 | -12.5 | 12.5 | 995 | 1.16 | 20.6 | 106 | 15 | 16.5 | OK- No Action Required
BGW2X254 | 2018-07-24 13:44 | 51.3 | 37.7 | 0 | 11 | -20.9 | 20.9 | 995 | 0.04 | 3.7 | 20 | 15 | 33.8 | OK- No Action Required
BGW2X393 | 2018-07-24 13:43 | 49.2 | 36.7 | 0 | 14.1 | -6.2 | 6.2 | 995 | 5.53 | 44.5 | 229 | 40 | 26.8 | OK- No Action Required
BGW2X259 | 2018-07-24 13:42 | 40.3 | 31.5 | 2.7 | 25.5 | 0 | 0 | 995 | 11.28 | 7.4 | 31 | 5 | 19.9 | OK- No Action Required
BGW2X258 | 2018-07-24 13:39 | 45 | 36.1 | 0 | 18.9 | -63.6 | 63.6 | 995 | 0.11 | 10 | 47 | 99 | 30.5 | OK- No Action Required
BHW2C404 | 2018-07-24 11:34 | 54.6 | 38.2 | 0 | 7.2 | -4 | 4 | 996 | 2.33 | 47.5 | 272 | 40 | 27.3 | OK- No Action Required
BHW2C403 | 2018-07-24 11:33 | 63.9 | 38.2 | 0 | 0 | -63.8 | 63.8 | 996 | 5.56 | 20.8 | 139 | 99 | 21.4 | OK- No Action Required
BGW2C394 | 2018-07-24 11:31 | 53.8 | 38 | 0 | 8.2 | -12.4 | 12.4 | 996 | 3.83 | 61 | 344 | 50 | 23.6 | OK- No Action Required
BGW2C355 | 2018-07-24 11:30 | 54.6 | 39.8 | 0 | 5.6 | -27.7 | 27.7 | 996 | 18.45 | 129.8 | 743 | 90 | 35.9 | OK- No Action Required
BGW2F358 | 2018-07-24 11:28 | 58.2 | 42.5 | 0 | 0 | 0 | 0 | 996 | 0.13 | 3.2 | 19 | 8 | 20.8 | Adjusted Increase
BHW2F416 | 2018-07-24 11:26 | 49.5 | 38.1 | 0.2 | 12.2 | -31.2 | 31.2 | 996 | 3.71 | 57.6 | 299 | 50 | 36.6 | OK- No Action Required
BGW2V267 | 2018-07-24 11:22 | 3.8 | 3.3 | 19.3 | 73.6 | -10.9 | 10.9 | 996 | -0.11 | 0 | 0 | 0 | 33.4 | Shut/Shut
BHW2V415 | 2018-07-24 11:21 | 60.9 | 42.6 | 0 | 0 | -63.9 | 63.9 | 996 | 0.92 | 28.3 | 181 | 99 | 42.1 | OK- No Action Required
BGW2V244 | 2018-07-24 11:20 | 0.9 | 0.8 | 19.9 | 78.4 | -65.6 | 65.6 | 996 | -0.07 | 0 | 0 | 99 | 13.7 | Blocked-Investigation Required
BHW2V414 | 2018-07-24 11:19 | 6.8 | 4.5 | 19.2 | 69.5 | -65.3 | 65.3 | 996 | -0.11 | 0 | 0 | 99 | 13.9 | Blocked-Investigation Required
BHW2V413 | 2018-07-24 11:18 | 2.2 | 1.9 | 19.9 | 76 | -0.9 | 0.9 | 996 | -0.11 | 0 | 0 | 0 | 14.6 | Shut/Shut
BGW2V379 | 2018-07-24 11:17 | 50.7 | 38.8 | 0.1 | 10.4 | -0.5 | 0.5 | 995 | 9.23 | 6.7 | 35 | 10 | 22.8 | OK- No Action Required
BGW2V390 | 2018-07-24 11:16 | 54 | 41.1 | 0 | 4.9 | -14.7 | 14.7 | 996 | 4.05 | 37 | 209 | 40 | 40.3 | OK- No Action Required
BGW2V262 | 2018-07-24 11:14 | 56.6 | 42.3 | 0.8 | 0.3 | -65.4 | 65.4 | 995 | 0.16 | 7.1 | 42 | 99 | 39.1 | Blocked-Investigation Required
BGW2V255 | 2018-07-24 11:13 | 59.5 | 42.8 | 0 | 0 | -65.1 | 65.1 | 996 | -0.11 | 0 | 0 | 99 | 14.4 | Blocked-Investigation Required
BHW2V407 | 2018-07-24 11:12 | 42 | 32.2 | 5.4 | 20.4 | -65.4 | 65.4 | 995 | -0.15 | 0 | 0 | 20 | 13.1 | Blocked-Investigation Required

## CV Reads
Paste readings below and ensure that "Security Code" is in Cell A2 | [18 empty] | ID
Security code | [633C567B]
ID | DATE | CH4 | CO2 | O2 | BALANCE | BARO | ADJ-SP | ADJ-DP | ADJ-TEMP | ADJ-FLOW | ADJ-POWER | INI-SP | INI-DP | INI-TEMP | INI-FLOW | INI-POWER | CHOSEN 1 | ANSWER 1 | ANSWER 2 | Res Nitrogen | PEAKCH4 | PEAKCO2 | MIN O2 | CH4 %LEL
|  | % | % | % | % | mb | mb | mb | DegC | m3/h | kW | mb | mb | DegC | m3/h | kW |  |  |  | % | % | % | % | %
BGW2E356 | 2019-03-18 10:01 | 36.4 | 27.1 | 5.5 | 31 | 1009 | -0.4 | 0.129 | 23.8 | 3.1 | 12 | -0.5 | 0.442 | 23.7 | 5.8 | 22 | Adjusted Decrease | 10 | 5 | 10.21 | 36.4 | 27.1 | 5.5 | >>>>
BGW2E357 | 2019-03-18 10:06 | 45.4 | 33.1 | 2.1 | 19.4 | 1010 | -1.1 | 1.531 | 29.4 | 10.8 | 51 | -1.6 | 2.567 | 29.1 | 14 | 66 | Adjusted Decrease | 291 | 5 | 11.46 | 45.4 | 33.1 | 2.1 | >>>>
BHW2F416 | 2019-03-18 10:08 | 47.4 | 36.9 | 0.4 | 15.3 | 1010 | -28.3 | 1.269 | 36.5 | 33.7 | 167 | -26.3 | 1.817 | 36.3 | 40.4 | 201 | Surge | 50 | 50 | 13.79 | 47.4 | 36.9 | 0.4 | >>>>
BGW2F358 | 2019-03-18 10:10 | 36.5 | 32.9 | 1.4 | 29.2 | 1009 | -0.1 | 0.212 | 31.2 | 3.9 | 15 | -0.9 | 0.799 | 31.2 | 7.6 | 29 | Adjusted Decrease | 10 | 5 | 23.91 | 36.5 | 32.9 | 1.4 | >>>>
BGW2C355 | 2019-03-18 10:14 | 48.6 | 36.1 | 1.7 | 13.6 | 1009 | -12.7 | 8.81 | 35.8 | 90.1 | 459 | -17.9 | 12.286 | 35.6 | 106.2 | 541 | Adjusted Decrease | 80 | 70 | 7.17 | 48.6 | 36.1 | 1.7 | >>>>
BGW2C394 | 2019-03-18 10:15 | 47.6 | 35.7 | 0 | 16.7 | 1009 | -14 | 3.617 | 33.1 | 57.9 | 289 | -13.8 | 3.673 | 31.6 | 58.5 | 292 | OK- No Action Required | 50 | 50 | 16.7 | 47.6 | 35.7 | 0 | >>>>
BHW2C403 | 2019-03-18 10:16 | 2.4 | 1.4 | 20 | 76.2 | 1009 | -5.9 | -0.365 | 23.3 | N/A | N/A | -6.1 | -0.42 | 23.6 | N/A | N/A | Shut/Shut | 0 | 0 | 0.6 | 2 | 1.2 | 20 | 48
BHW2C404 | 2019-03-18 10:18 | 49.5 | 36.7 | 0 | 13.8 | 1010 | -5.9 | 2.394 | 31.1 | 47.5 | 246 | -6 | 2.397 | 31 | 47.6 | 247 | OK- No Action Required | 50 | 50 | 13.8 | 49.5 | 36.7 | 0 | >>>>
BHW3A451 | 2019-03-18 10:21 | 51.9 | 32.7 | 4.1 | 11.3 | 1010 | -8.5 | -0.28 | 20.5 | N/A | N/A | -8.7 | -0.289 | 21.1 | N/A | N/A | Shut/Shut | 0 | 0 | 0 | 51.9 | 32.7 | 4.1 | >>>>
BHW3A452 | 2019-03-18 10:24 | 55.3 | 40.8 | 0 | 3.9 | 1009 | -13 | 12.969 | 28 | 67.9 | 393 | -10.8 | 11.423 | 27.4 | 63.8 | 370 | Surge | 50 | 55 | 3.9 | 55.3 | 40.8 | 0 | >>>>
BHW3A453 | 2019-03-18 10:27 | 62.2 | 41.9 | 0 | 0 | 1009 | -60.2 | 7.538 | 28.8 | 83.4 | 544 | -68.3 | 9.184 | 28.2 | 91.8 | 599 | OK- No Action Required | 99 | 99 | 0 | 62.2 | 41.9 | 0 | >>>>
BHW3A454 | 2019-03-18 10:28 | 60.5 | 41.4 | 0 | 0 | 1008 | -68.6 | 4.519 | 32.1 | 39 | 247 | -71.2 | 3.874 | 31.7 | 36.1 | 229 | OK- No Action Required | 99 | 99 | 0 | 60.5 | 41.4 | 0 | >>>>
BHW3A455 | 2019-03-18 10:29 | 61.8 | 41.4 | 0 | 0 | 1009 | -62.3 | 12.316 | 36.2 | 64.4 | 417 | -59.4 | 12.517 | 35.8 | 65.1 | 421 | OK- No Action Required | 99 | 99 | 0 | 61.7 | 41.4 | 0 | >>>>
BGW2V255 | 2019-03-18 10:38 | 17.7 | 12.2 | 14.9 | 55.2 | 1009 | -61.9 | -0.028 | 23.7 | N/A | N/A | -62 | 0.001 | 22.9 | 0.3 | 0 | Blocked-Investigation Required | 99 | 99 | 0 | 17.2 | 12 | 14.9 | >>>>
BGW2V262 | 2019-03-18 10:39 | 56 | 41.9 | 0.4 | 1.7 | 1009 | -62.6 | 0.576 | 23.2 | 14 | 82 | -62.5 | 0.552 | 22.6 | 13.7 | 80 | Blocked-Investigation Required | 99 | 99 | 0.19 | 56 | 41.9 | 0.3 | >>>>
BGW2V390 | 2019-03-18 10:41 | 52.1 | 38.9 | 0.7 | 8.3 | 1009 | -2.4 | 0.638 | 38.8 | 14.8 | 81 | -2.4 | 0.628 | 38.5 | 14.7 | 80 | OK- No Action Required | 15 | 15 | 5.65 | 52.1 | 38.9 | 0.7 | >>>>
BGW2V379 | 2019-03-18 10:42 | 45.4 | 36.1 | 0.7 | 17.8 | 1009 | -0.2 | 4.118 | 32.5 | 4.4 | 21 | -0.6 | 8.952 | 32.2 | 6.5 | 31 | Adjusted Decrease | 15 | 10 | 15.15 | 45.5 | 36.2 | 0.7 | >>>>
BHW2V413 | 2019-03-18 10:44 | 50.5 | 38.6 | 0.2 | 10.7 | 1009 | 0.1 | -0.085 | 23 | N/A | N/A | -0.1 | -0.107 | 22.5 | N/A | N/A | Shut/Shut | 0 | 0 | 9.94 | 50.5 | 38.6 | 0.2 | >>>>
BGW2V244 | 2019-03-18 10:47 | 4.9 | 4.9 | 18.2 | 72 | 1009 | 0 | 0.02 | 22.5 | 1.2 | 0 | 0 | 0.023 | 22.6 | 1.3 | 0 | Shut/Shut | 0 | 0 | 3.2 | 15.1 | 4.9 | 5.4 | 98
BHW2V415 | 2019-03-18 10:48 | 58.4 | 41.4 | 0 | 0.2 | 1009 | -61.8 | 0.533 | 44.7 | 21.4 | 131 | -60.7 | 0.65 | 43.8 | 23.7 | 145 | Blocked-Investigation Required | 60 | 99 | 0.2 | 58.4 | 41.4 | 0 | >>>>
BGW2V267 | 2019-03-18 10:49 | 1.3 | 0.9 | 20.1 | 77.7 | 1009 | -5.9 | 0.011 | 35.4 | 0.9 | 0 | -5.6 | 0.017 | 38.8 | 1.1 | 0 | Shut/Shut | 0 | 0 | 1.72 | 1.6 | 0.8 | 12.5 | 26
BGW2W257 | 2019-03-18 10:52 | 45.5 | 38.6 | 0.1 | 15.8 | 1009 | -0.3 | 0.994 | 38.7 | 8.5 | 40 | -0.2 | 1.101 | 38.1 | 8.9 | 42 | OK- No Action Required | 15 | 15 | 15.42 | 45.5 | 38.6 | 0.1 | >>>>
BGW2W242 | 2019-03-18 10:53 | 49.3 | 37.5 | 0.2 | 13 | 1009 | -32.4 | 0.793 | 31.9 | 26.9 | 139 | -32.3 | 0.695 | 31.7 | 25.2 | 130 | OK- No Action Required | 40 | 40 | 12.24 | 49.3 | 37.5 | 0.2 | >>>>
BGW2W246 | 2019-03-18 10:55 | 42.3 | 35.7 | 0 | 22 | 1009 | -1.2 | 1.184 | 29.7 | 9.4 | 41 | -1.2 | 1.167 | 29 | 9.3 | 41 | OK- No Action Required | 15 | 15 | 22 | 42.3 | 35.6 | 0 | >>>>
BGW2W256 | 2019-03-18 10:56 | 56.6 | 41.4 | 0 | 2 | 1009 | -49.8 | 1.537 | 36.8 | 37 | 219 | -47.4 | 1.412 | 36.4 | 35.5 | 210 | Surge | 40 | 40 | 2 | 56.6 | 41.4 | 0 | >>>>
BGW2W261 | 2019-03-18 10:58 | 54.7 | 39.3 | 0 | 6 | 1008 | -1.3 | 1.611 | 32.4 | 11.1 | 63 | -1.3 | 1.589 | 32.1 | 11 | 63 | OK- No Action Required | 20 | 20 | 6 | 54.7 | 39.3 | 0 | >>>>
BGW2N145 | 2019-03-18 11:03 | 50.5 | 38.5 | 0 | 11 | 1010 | -1.1 | 2.084 | 28.7 | 12.6 | 66 | -1 | 2.071 | 28.5 | 12.6 | 66 | OK- No Action Required | 20 | 20 | 11 | 50.5 | 38.5 | 0 | >>>>
BGW2N146 | 2019-03-18 11:05 | 57 | 41.1 | 0 | 1.9 | 1010 | -7.2 | 0.346 | 28 | 11.1 | 66 | -7.1 | 0.762 | 27 | 16.6 | 99 | Surge | 22 | 25 | 1.9 | 57 | 41.1 | 0 | >>>>
BGW2N143 | 2019-03-18 11:06 | 52.8 | 39.5 | 0 | 7.7 | 1010 | -1.2 | 0.184 | 27.5 | 8.1 | 45 | -1.2 | 0.178 | 26.8 | 8 | 44 | OK- No Action Required | 15 | 15 | 7.7 | 52.8 | 39.5 | 0 | >>>>
BGW2N144 | 2019-03-18 11:08 | 54 | 38.9 | 0.6 | 6.5 | 1010 | -4.3 | 3.801 | 27.5 | 8.5 | 48 | -4.3 | 3.777 | 27.2 | 8.5 | 48 | Damaged | 15 | 15 | 4.23 | 54.1 | 38.9 | 0.5 | >>>>
BGW2X163 | 2019-03-18 11:10 | 47.2 | 36.5 | 1 | 15.3 | 1010 | -1.1 | 1.837 | 27 | 25.6 | 126 | -1.1 | 1.758 | 26.6 | 25 | 124 | OK- No Action Required | 40 | 40 | 11.52 | 47.2 | 36.5 | 1 | >>>>
BGW2H424 | 2019-03-18 13:08 | 55.4 | 39.3 | 0.2 | 5.1 | 1008 | 0 | -0.252 | 26.6 | N/A | N/A | 0 | -0.263 | 26.3 | N/A | N/A | Blocked-Investigation Required | 25 | 25 | 4.34 | 55.4 | 39.3 | 0.2 | >>>>
BGW2H059 | 2019-03-18 13:10 | 52.4 | 39.5 | 0 | 8.1 | 1008 | 0 | 6.524 | 29 | 5.6 | 30 | 0 | 6.555 | 27.2 | 5.6 | 31 | OK- No Action Required | 15 | 15 | 8.1 | 52.4 | 39.5 | 0 | >>>>
BGW2H402 | 2019-03-18 13:11 | 53.1 | 39.3 | 0.2 | 7.4 | 1008 | -0.6 | 6.268 | 33.4 | 10.8 | 60 | -0.7 | 6.243 | 32.3 | 10.8 | 60 | OK- No Action Required | 25 | 25 | 6.64 | 53.1 | 39.3 | 0.2 | >>>>
BGW2H064 | 2019-03-18 13:12 | 45.2 | 35.4 | 0.6 | 18.8 | 1008 | -0.2 | 1.273 | 28.9 | 4.8 | 23 | -0.6 | 6.039 | 28.5 | 10.6 | 50 | Adjusted Decrease | 15 | 12 | 16.53 | 45.2 | 35.4 | 0.6 | >>>>
BGW2H423 | 2019-03-18 13:15 | 46.4 | 35.9 | 0 | 17.7 | 1008 | -4.1 | 16.604 | 31.6 | 35.4 | 172 | -4.1 | 16.897 | 31.3 | 35.7 | 174 | OK- No Action Required | 50 | 50 | 17.7 | 46.4 | 35.9 | 0 | >>>>
BGW2H363 | 2019-03-18 13:17 | 53.3 | 38 | 0.4 | 8.3 | 1008 | -0.5 | 0.79 | 27.5 | 16.9 | 94 | -0.5 | 0.844 | 27.2 | 17.5 | 97 | OK- No Action Required | 25 | 25 | 6.79 | 53.3 | 38 | 0.4 | >>>>
BGW2H365 | 2019-03-18 13:18 | 49.9 | 37 | 0 | 13.1 | 1008 | -3.5 | 0.414 | 28.9 | 12.1 | 63 | -3.5 | 0.424 | 27.4 | 12.3 | 64 | OK- No Action Required | 25 | 25 | 13.1 | 49.8 | 36.9 | 0 | >>>>
BGW2H361 | 2019-03-18 13:19 | 55.9 | 40.4 | 0 | 3.7 | 1008 | -0.2 | 5.808 | 30.5 | 10.5 | 61 | -0.2 | 5.913 | 29.9 | 10.6 | 62 | OK- No Action Required | 25 | 25 | 3.7 | 55.9 | 40.4 | 0 | >>>>
BGW2H360 | 2019-03-18 13:20 | 51.5 | 37.4 | 0 | 11.1 | 1008 | -0.2 | 4.349 | 26.7 | 4.6 | 25 | -0.2 | 4.372 | 26 | 4.6 | 25 | OK- No Action Required | 20 | 20 | 11.1 | 51.5 | 37.3 | 0 | >>>>
BGW2H366 | 2019-03-18 13:22 | 55.2 | 36.1 | 0.6 | 8.1 | 1008 | 0 | 2.692 | 26.8 | 7.2 | 42 | 0 | 2.684 | 25.9 | 7.2 | 42 | Damaged | 20 | 20 | 5.83 | 55.2 | 36.1 | 0.6 | >>>>
BGW2H362 | 2019-03-18 13:23 | 47.5 | 36.3 | 1.2 | 15 | 1008 | 0 | 1.429 | 30.3 | 5.1 | 25 | -0.7 | 4.254 | 28.8 | 8.9 | 44 | Adjusted Decrease | 10 | 7 | 10.46 | 47.5 | 36.3 | 1.2 | >>>>
BGW2H058 | 2019-03-18 13:25 | 49.2 | 36.2 | 2.4 | 12.2 | 1008 | -5.2 | -0.154 | 26 | N/A | N/A | -5.2 | -0.152 | 25.8 | N/A | N/A | Blocked-Investigation Required | 10 | 10 | 3.13 | 49.1 | 36.1 | 2.4 | >>>>
BGW2H412 | 2019-03-18 13:26 | 20.1 | 21.9 | 4.9 | 53.1 | 1008 | 0 | 0.434 | 25.3 | 5.6 | 12 | 0 | 0.439 | 24.7 | 5.7 | 12 | Blocked-Investigation Required | 10 | 10 | 34.58 | 20.1 | 21.9 | 4.9 | >>>>
BGW2H102 | 2019-03-18 13:27 | 50.9 | 36 | 1.4 | 11.7 | 1008 | -29.4 | 0.139 | 26.5 | 1.6 | 8 | -29.4 | 0.129 | 25.9 | 1.5 | 8 | OK- No Action Required | 5 | 5 | 6.41 | 50.9 | 36 | 1.4 | >>>>
BGW2H422 | 2019-03-18 13:28 | 7.9 | 7.3 | 15.1 | 69.7 | 1008 | 0.1 | 6.148 | 27.8 | 1.1 | 0 | 0 | 6.21 | 26.5 | 1.1 | 0 | OK- No Action Required | 10 | 10 | 12.62 | 27.3 | 9.4 | 4.5 | >>>>
BGW2G052 | 2019-03-18 13:38 | 53.8 | 37 | 0.3 | 8.9 | 1009 | 0 | -0.054 | 27.7 | N/A | N/A | 0.1 | -0.054 | 29.9 | N/A | N/A | Blocked-Investigation Required | 15 | 15 | 7.77 | 53.8 | 37 | 0.3 | >>>>
BGW2G054 | 2019-03-18 13:39 | 47.2 | 36.6 | 0.5 | 15.7 | 1009 | -53.3 | 16.138 | 41.5 | 72.2 | 357 | -55.3 | 15.562 | 41 | 70.9 | 351 | OK- No Action Required | 70 | 70 | 13.81 | 47.3 | 36.6 | 0.5 | >>>>
BGW2G418 | 2019-03-18 13:41 | 48.1 | 35.1 | 0 | 16.8 | 1009 | -0.1 | -0.07 | 30.6 | N/A | N/A | 0 | -0.076 | 32.6 | N/A | N/A | Blocked-Investigation Required | 20 | 20 | 16.8 | 48.1 | 35.1 | 0 | >>>>
BGW2G419 | 2019-03-18 13:42 | 52.9 | 37.1 | 0.1 | 9.9 | 1009 | -3.4 | 2.037 | 33.7 | 26.9 | 149 | -3.2 | 1.954 | 33.5 | 26.4 | 146 | OK- No Action Required | 40 | 40 | 9.52 | 52.9 | 37.1 | 0.1 | >>>>
BGW2G421 | 2019-03-18 13:44 | 54.5 | 36.2 | 1 | 8.3 | 1009 | -0.5 | 0.487 | 30.2 | 13.3 | 76 | -0.5 | 0.442 | 30.1 | 12.7 | 72 | OK- No Action Required | 25 | 25 | 4.52 | 54.5 | 36.2 | 1 | >>>>
BGW2M435 | 2019-03-18 14:18 | 0.1 | 0 | 19.8 | 80.1 | 1008 | -0.9 | -0.054 | 30.7 | N/A | N/A | -0.9 | -0.042 | 30.6 | N/A | N/A | Shut/Shut | 0 | 0 | 5.26 | 0.4 | 0.4 | 19.4 | 2
BGW2M450 | 2019-03-18 14:19 | 56.6 | 40.5 | 0.1 | 2.8 | 1008 | -57.2 | 6.899 | 30.9 | 5.6 | 33 | -57.2 | 6.933 | 30.5 | 5.6 | 33 | OK- No Action Required | 99 | 99 | 2.42 | 56.6 | 40.5 | 0.1 | >>>>
BGW2M381 | 2019-03-18 14:21 | 47.8 | 36.8 | 0.2 | 15.2 | 1009 | -16.1 | 19.37 | 46.3 | 37.1 | 186 | -17 | 21.437 | 46.2 | 39.1 | 195 | Adjusted Decrease | 45 | 42 | 14.44 | 47.8 | 36.8 | 0.2 | >>>>
BGW2M124 | 2019-03-18 14:22 | 54.1 | 38.6 | 0.4 | 6.9 | 1008 | -1.5 | -0.073 | 30.6 | N/A | N/A | -1.6 | -0.111 | 32.5 | N/A | N/A | Blocked-Investigation Required | 25 | 25 | 5.39 | 54.1 | 38.6 | 0.4 | >>>>
BGW2M397 | 2019-03-18 14:23 | 50.9 | 39.1 | 0 | 10 | 1008 | -45.4 | 10.076 | 49.8 | 26.2 | 140 | -45.4 | 10.01 | 48.9 | 26.2 | 140 | OK- No Action Required | 50 | 50 | 10 | 50.9 | 39.1 | 0 | >>>>
BGW2M432 | 2019-03-18 14:24 | 50.5 | 38.9 | 0 | 10.6 | 1008 | -2 | 10.325 | 30.4 | 7 | 37 | -1.9 | 10.313 | 30.8 | 7 | 37 | OK- No Action Required | 15 | 15 | 10.6 | 50.5 | 38.9 | 0 | >>>>
BGW2M131 | 2019-03-18 14:25 | 43.5 | 34.8 | 0 | 21.7 | 1008 | -0.1 | 3.609 | 30.5 | 8.2 | 37 | 0 | 3.588 | 29.4 | 8.1 | 37 | OK- No Action Required | 15 | 15 | 21.7 | 43.5 | 34.8 | 0 | >>>>
BGW2M434 | 2019-03-18 14:26 | 43 | 34.7 | 0 | 22.3 | 1008 | -1.8 | 12.897 | 36.6 | 30.9 | 139 | -1.8 | 12.928 | 34.8 | 31 | 139 | OK- No Action Required | 30 | 30 | 22.3 | 43.9 | 35.4 | 0 | >>>>
BGW2M083 | 2019-03-18 14:27 | 56.7 | 39.9 | 0.2 | 3.2 | 1008 | -3 | -0.125 | 34 | N/A | N/A | -3.5 | -0.149 | 33.3 | N/A | N/A | Blocked-Investigation Required | 10 | 10 | 2.44 | 56.6 | 39.9 | 0.2 | >>>>
BGW2M128 | 2019-03-18 14:28 | 51.5 | 35.5 | 1.9 | 11.1 | 1008 | -29.3 | -0.005 | 26.7 | N/A | N/A | -29.5 | 0.075 | 28 | 2.3 | 12 | Blocked-Investigation Required | 10 | 10 | 3.92 | 51.5 | 35.5 | 1.9 | >>>>
BGW2L380 | 2019-03-18 14:37 | 33.2 | 29.6 | 3.3 | 33.9 | 1008 | 0 | 13.009 | 28.4 | 1.7 | 5 | -0.1 | 15.616 | 28.1 | 1.8 | 6 | Adjusted Decrease | 10 | 5 | 21.43 | 33.2 | 29.6 | 3.3 | >>>>
BGW2L134 | 2019-03-18 14:39 | 49 | 36.6 | 0.4 | 14 | 1008 | -0.7 | 0.483 | 38.1 | 12.9 | 66 | -0.3 | 0.407 | 37.5 | 11.9 | 61 | Damaged | 25 | 25 | 12.49 | 49 | 36.6 | 0.4 | >>>>
BGW2L133 | 2019-03-18 14:40 | 49.3 | 37.8 | 0 | 12.9 | 1008 | -0.8 | 5.338 | 39.3 | 9.8 | 51 | -0.8 | 5.31 | 37.2 | 9.8 | 51 | OK- No Action Required | 15 | 15 | 12.9 | 49.3 | 37.7 | 0 | >>>>
BGW2L431 | 2019-03-18 14:41 | 51.1 | 37.2 | 0 | 11.7 | 1008 | -47 | 21.158 | 48.5 | 135 | 722 | -47.3 | 20.575 | 48 | 133.2 | 713 | OK- No Action Required | 90 | 90 | 11.7 | 51 | 37.2 | 0 | >>>>
BGW2L378 | 2019-03-18 14:42 | 47.4 | 37.2 | 0 | 15.4 | 1008 | -0.6 | 3.024 | 48 | 14.7 | 73 | -0.6 | 2.985 | 46.8 | 14.6 | 72 | OK- No Action Required | 20 | 20 | 15.4 | 47.4 | 37.2 | 0 | >>>>
BGW2L140 | 2019-03-18 14:43 | 52.8 | 39.9 | 0 | 7.3 | 1008 | -46.9 | 4.628 | 34.4 | 4.5 | 25 | -47.2 | 4.542 | 34.1 | 4.5 | 25 | OK- No Action Required | 50 | 50 | 7.3 | 52.8 | 39.8 | 0 | >>>>
BGW2L377 | 2019-03-18 14:44 | 50.3 | 38.1 | 0 | 11.6 | 1008 | -0.3 | 1.676 | 39.5 | 11.1 | 58 | -0.1 | 1.655 | 38.2 | 11.1 | 58 | OK- No Action Required | 20 | 20 | 11.6 | 50.3 | 38 | 0 | >>>>
BGW2L420 | 2019-03-18 14:45 | 36.1 | 26.9 | 6.1 | 30.9 | 1008 | 0 | 1.171 | 27.8 | 2.3 | 9 | 0 | 1.224 | 28.1 | 2.4 | 9 | Damaged | 5 | 5 | 7.84 | 36.1 | 26.9 | 6.1 | >>>>
BGW2L359 | 2019-03-18 14:46 | 25.9 | 24.3 | 4.5 | 45.3 | 1007 | -0.2 | 0.819 | 28.5 | 1.9 | 5 | -0.2 | 1.736 | 25.8 | 2.8 | 7 | Adjusted Decrease | 10 | 5 | 28.29 | 25.9 | 24.3 | 4.5 | >>>>
BGW2L101 | 2019-03-18 14:47 | 2.5 | 1.4 | 18.1 | 78 | 1007 | 0 | -0.009 | 27 | N/A | N/A | 0 | -0.013 | 25.2 | N/A | N/A | Shut/Shut | 0 | 0 | 9.58 | 23.8 | 24.6 | 5.1 | 50
BGW2L137 | 2019-03-18 14:49 | 47.3 | 36.7 | 0.3 | 15.7 | 1007 | -24 | 2.069 | 26.9 | 43.9 | 218 | -23.7 | 2.29 | 26.2 | 46.2 | 229 | OK- No Action Required | 40 | 40 | 14.57 | 47.3 | 36.7 | 0.3 | >>>>
BGW2L417 | 2019-03-18 14:51 | 52.3 | 37.4 | 1.4 | 8.9 | 1008 | -0.3 | 0.59 | 30.2 | 14.5 | 79 | 1 | 0.796 | 29.9 | 16.9 | 92 | Surge | 20 | 20 | 3.61 | 52.3 | 37.3 | 1.4 | >>>>
BGW2L056 | 2019-03-18 14:51 | 36.1 | 33.3 | 0 | 30.6 | 1008 | -0.1 | 13.407 | 27.9 | 7.9 | 30 | -0.2 | 13.414 | 27.5 | 7.9 | 30 | OK- No Action Required | 15 | 15 | 30.6 | 44 | 33.3 | 0 | >>>>
BGW2L082 | 2019-03-18 14:52 | 55.1 | 39.3 | 0 | 5.6 | 1007 | -37.5 | 18.16 | 32 | 36.7 | 212 | -38 | 18.575 | 31.5 | 37.1 | 214 | OK- No Action Required | 99 | 99 | 5.6 | 55 | 39.2 | 0 | >>>>
BGW2L448 | 2019-03-18 14:54 | 46.9 | 36.3 | 0 | 16.8 | 1008 | -27.9 | 15.741 | 36.8 | 72.8 | 358 | -24.2 | 15.791 | 36.6 | 73.1 | 359 | OK- No Action Required | 60 | 60 | 16.8 | 46.9 | 36.3 | 0 | >>>>
BGW2L150 | 2019-03-18 14:55 | 50.3 | 37.9 | 0 | 11.8 | 1007 | -60.4 | 8.986 | 39.1 | 88.3 | 466 | -56 | 9.422 | 37.6 | 90.9 | 479 | OK- No Action Required | 99 | 99 | 11.8 | 50.3 | 37.7 | 0 | >>>>
BGW2L376 | 2019-03-18 14:56 | 43.3 | 34.8 | 0.8 | 21.1 | 1007 | -0.5 | 3.511 | 30.1 | 4 | 18 | -0.5 | 5.684 | 30.9 | 5.2 | 23 | Adjusted Decrease | 10 | 5 | 18.08 | 43.3 | 34.8 | 0.8 | >>>>
BGW2L433 | 2019-03-18 14:58 | 36.2 | 28.8 | 4.6 | 30.4 | 1007 | -0.2 | 1.265 | 30 | 9.7 | 37 | -0.4 | 1.97 | 29.1 | 12.2 | 46 | Adjusted Decrease | 15 | 10 | 13.01 | 36.2 | 28.8 | 4.6 | >>>>
BGW2L053 | 2019-03-18 14:59 | 55.8 | 39.2 | 0 | 5 | 1007 | -66.8 | 0.195 | 30.2 | 13.2 | 77 | -65.9 | 0.143 | 29.2 | 11.4 | 66 | Blocked-Investigation Required | 99 | 99 | 5 | 55.8 | 39.1 | 0 | >>>>
BGW2J090 | 2019-03-19 08:30 | 53.4 | 38.4 | 0.6 | 7.6 | 1006 | -3.3 | 8.947 | 31.5 | 26.2 | 146 | -3.3 | 9.066 | 31 | 26.4 | 147 | OK- No Action Required | 30 | 30 | 5.33 | 53.4 | 38.4 | 0.6 | >>>>
BGW2J087 | 2019-03-19 08:31 | 50.8 | 39.5 | 0.2 | 9.5 | 1006 | -3.1 | 3.884 | 27.6 | 8.5 | 45 | -3.2 | 3.762 | 27.4 | 8.4 | 44 | OK- No Action Required | 20 | 20 | 8.74 | 50.8 | 39.5 | 0.2 | >>>>
BGW2J091 | 2019-03-19 08:33 | 46.3 | 36 | 1.4 | 16.3 | 1006 | -0.8 | 14.72 | 30.1 | 16.5 | 80 | -1.1 | 25.056 | 29.7 | 21.6 | 105 | Adjusted Decrease | 25 | 22 | 11.01 | 46.4 | 36 | 1.4 | >>>>
BGW2J401 | 2019-03-19 08:34 | 51.3 | 37.9 | 0.7 | 10.1 | 1006 | -43.7 | 3.415 | 26.5 | 15.9 | 85 | -44.3 | 3.125 | 26.4 | 15.2 | 82 | OK- No Action Required | 40 | 40 | 7.45 | 51.4 | 38 | 0.6 | >>>>
BGW2J089 | 2019-03-19 08:36 | 31.5 | 30.8 | 1.8 | 35.9 | 1006 | 0 | 1.637 | 29.2 | 10.9 | 36 | 0 | 1.693 | 28.5 | 11.1 | 36 | Damaged | 15 | 15 | 29.1 | 31.5 | 30.8 | 1.8 | >>>>
BGW2J430 | 2019-03-19 08:37 | 44.7 | 36.5 | 0 | 18.8 | 1006 | -2.7 | 1.315 | 25.4 | 10 | 47 | -2.7 | 1.226 | 25 | 9.6 | 45 | OK- No Action Required | 20 | 20 | 18.8 | 44.7 | 36.5 | 0 | >>>>
BGW2J408 | 2019-03-19 08:39 | 43.5 | 34.9 | 2.2 | 19.4 | 1006 | 0 | 6.029 | 26.2 | 5.4 | 24 | -0.1 | 5.89 | 25.8 | 5.3 | 24 | Damaged | 20 | 20 | 11.08 | 43.5 | 34.9 | 2.2 | >>>>
BGW2J400 | 2019-03-19 08:40 | 38.2 | 35.5 | 0.4 | 25.9 | 1006 | -0.1 | 1.604 | 34.1 | 10.8 | 43 | -0.1 | 2.107 | 33.7 | 12.4 | 49 | Adjusted Decrease | 25 | 22 | 24.39 | 38.2 | 35.5 | 0.4 | >>>>
BGW2K429 | 2019-03-19 08:50 | 30 | 31.5 | 0.6 | 37.9 | 1007 | -0.5 | 5.437 | 25.9 | 5 | 15 | -0.6 | 9.305 | 25.7 | 6.5 | 20 | Adjusted Decrease | 10 | 7 | 35.63 | 36 | 31.5 | 0.6 | >>>>
BGW2K372 | 2019-03-19 08:52 | 39 | 33.8 | 1.5 | 25.7 | 1007 | -0.5 | 3.726 | 30.4 | 4.1 | 17 | -0.8 | 5.833 | 28.9 | 5.2 | 21 | Adjusted Decrease | 10 | 7 | 20.03 | 39 | 33.8 | 1.5 | >>>>
BGW2K375 | 2019-03-19 08:55 | 47.9 | 37.7 | 0.2 | 14.2 | 1007 | -25.5 | 14.453 | 39.3 | 69.4 | 348 | -27 | 16.266 | 39 | 73.6 | 369 | Adjusted Decrease | 75 | 72 | 13.44 | 47.9 | 37.7 | 0.2 | >>>>
BGW2K428 | 2019-03-19 08:56 | 45.2 | 35.2 | 0.9 | 18.7 | 1007 | -0.6 | 2.437 | 33.7 | 13.5 | 64 | -0.9 | 3.648 | 33.6 | 16.5 | 78 | Adjusted Decrease | 30 | 25 | 15.3 | 45.2 | 35.2 | 0.9 | >>>>
BGW2K427 | 2019-03-19 08:57 | 45.3 | 35.6 | 0 | 19.1 | 1007 | -1.6 | 11.643 | 26.2 | 7.5 | 35 | -1.6 | 11.691 | 26.2 | 7.5 | 35 | OK- No Action Required | 10 | 10 | 19.1 | 45.3 | 35.6 | 0 | >>>>
BGW2K426 | 2019-03-19 09:00 | 47.6 | 37 | 0.1 | 15.3 | 1007 | -0.3 | 20.924 | 21.1 | 10.1 | 50 | -0.4 | 27.113 | 20.7 | 11.6 | 57 | Adjusted Decrease | 25 | 22 | 14.92 | 47.6 | 37 | 0.1 | >>>>
BGW2K373 | 2019-03-19 09:01 | 44.7 | 36.3 | 0 | 19 | 1007 | -5.2 | 1.465 | 29.2 | 22.6 | 106 | -5.1 | 1.46 | 27.9 | 22.6 | 106 | OK- No Action Required | 25 | 25 | 19 | 44.7 | 36.3 | 0 | >>>>
BGW2K374 | 2019-03-19 09:02 | 47.8 | 37.2 | 0.1 | 14.9 | 1007 | -1.5 | 0.555 | 29.7 | 14 | 70 | -1.2 | 0.523 | 29.6 | 13.6 | 68 | OK- No Action Required | 25 | 25 | 14.52 | 47.8 | 37.2 | 0.1 | >>>>
BGW2K093 | 2019-03-19 09:04 | 39.3 | 35.1 | 0 | 25.6 | 1007 | -1.9 | 3.411 | 37.2 | 3.9 | 16 | -1.9 | 3.836 | 36.9 | 4.1 | 17 | OK- No Action Required | 25 | 25 | 25.6 | 39.2 | 35.1 | 0 | >>>>
BGW2K095 | 2019-03-19 09:05 | 16.8 | 12.7 | 14.1 | 56.4 | 1007 | -59.8 | -0.194 | 24.7 | N/A | N/A | -60 | -0.236 | 25.9 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 3.1 | 23.8 | 22.2 | 1 | >>>>
BGW2K094 | 2019-03-19 09:07 | 45.9 | 35.9 | 0.9 | 17.3 | 1007 | -2.7 | 2.23 | 40.1 | 27.5 | 132 | -2.7 | 2.181 | 39.3 | 27.3 | 131 | Damaged | 40 | 40 | 13.9 | 45.9 | 35.9 | 0.9 | >>>>
BGW2I367 | 2019-03-19 09:12 | 33.3 | 31.2 | 0.8 | 34.7 | 1007 | -0.1 | 4.856 | 31.3 | 4.7 | 16 | -0.4 | 9.803 | 30.9 | 6.7 | 23 | Adjusted Decrease | 25 | 22 | 31.68 | 33.3 | 31.2 | 0.8 | >>>>
BGW2I368 | 2019-03-19 09:13 | 12.5 | 10.3 | 14.4 | 62.8 | 1008 | 0 | 0.618 | 24.5 | 3.4 | 4 | 0 | 1.719 | 25.1 | 5.6 | 7 | Adjusted Decrease | 5 | 3 | 8.37 | 26.2 | 16.5 | 1.8 | >>>>
BGW2I370 | 2019-03-19 09:14 | 53.7 | 38.7 | 0.1 | 7.5 | 1008 | -0.2 | >>>> | 26.4 | N/A | N/A | -0.2 | >>>> | 26 | N/A | N/A | Change Orife Plate Required | 40 | 40 | 7.12 | 53.7 | 38.7 | 0.1 | >>>>
BGW2I445 | 2019-03-19 09:16 | 24.2 | 18.2 | 10.7 | 46.9 | 1008 | -0.3 | 4.352 | 25.2 | 9 | 22 | -0.6 | 11.58 | 24.9 | 14.8 | 37 | Adjusted Decrease | 25 | 20 | 6.45 | 24.2 | 18.2 | 4.1 | >>>>
BGW2I081 | 2019-03-19 09:18 | 59.7 | 39.2 | 0 | 1.1 | 1008 | -30.5 | 1.159 | 27.8 | 20.4 | 127 | -20.7 | 0.739 | 26.6 | 16.4 | 102 | Adjusted Increase | 25 | 27 | 1.1 | 59.7 | 39.2 | 0 | >>>>
BGW2I371 | 2019-03-19 09:19 | 49 | 36.6 | 0 | 14.4 | 1008 | -3 | 1.097 | 34.6 | 19.6 | 100 | -2.9 | 1.103 | 34 | 19.6 | 101 | OK- No Action Required | 25 | 25 | 14.4 | 49 | 36.6 | 0 | >>>>
BGW2I369 | 2019-03-19 09:20 | 48.1 | 37.1 | 0.2 | 14.6 | 1008 | -0.5 | 15.21 | 33.3 | 8.5 | 42 | -0.5 | 15.208 | 32.9 | 8.5 | 42 | OK- No Action Required | 25 | 25 | 13.84 | 48.1 | 37.1 | 0.2 | >>>>
BGW2I396 | 2019-03-19 09:21 | 55.8 | 38.8 | 0 | 5.4 | 1008 | -9.2 | 3.444 | 32.5 | 35 | 204 | -9.3 | 3.48 | 32.3 | 35.2 | 206 | OK- No Action Required | 40 | 40 | 5.4 | 55.8 | 38.8 | 0 | >>>>
BGW2I442 | 2019-03-19 09:23 | 15.5 | 23.6 | 1.4 | 59.5 | 1008 | -0.1 | 4.122 | 26.5 | 0.9 | 1 | -0.3 | 28.387 | 25.4 | 2.5 | 4 | Adjusted Decrease | 10 | 5 | 54.21 | 15.5 | 23.6 | 1.4 | >>>>
BLW2X460 | 2019-03-19 12:55 | 0.2 | 0.4 | 20.6 | 78.8 | 1009 | -65.8 | -0.044 | 23.4 | N/A | N/A | -65.4 | -0.053 | 22.2 | N/A | N/A | Shut/Shut | 0 | 0 | 0.93 | 0.2 | 0.4 | 20.6 | 4
BLW2X461 | 2019-03-19 12:58 | 59.3 | 39.8 | 0 | 0.9 | 1009 | -65.9 | 1.436 | 21 | 36.7 | 228 | -65.9 | 0.793 | 21.3 | 27.3 | 169 | OK- No Action Required | 30 | 30 | 0.9 | 59.3 | 39.8 | 0 | >>>>
BLW2X462 | 2019-03-19 13:00 | 0.3 | 0.2 | 20.6 | 78.9 | 1009 | -65.1 | -0.039 | 21.4 | N/A | N/A | -65.1 | -0.024 | 21.4 | N/A | N/A | Shut/Shut | 0 | 0 | 1.03 | 2.2 | 1.8 | 19.5 | 6
BLW2X463 | 2019-03-19 13:02 | 0.7 | 0.5 | 20.5 | 78.3 | 1009 | -64.9 | 0.169 | 23.4 | 12.2 | 1 | -65.9 | 0.133 | 22.7 | 10.8 | 0 | Shut/Shut | 0 | 0 | 0.81 | 0.7 | 0.6 | 20.5 | 14
BGW2X456 | 2019-03-19 13:05 | 62.1 | 38.3 | 0 | 0 | 1009 | 0 | 1.019 | 29.2 | 9 | 59 | 0 | 0.453 | 28.5 | 6 | 39 | Adjusted Increase | 5 | 7 | 0 | 62.1 | 38.3 | 0 | >>>>
BGW2X457 | 2019-03-19 13:08 | 56.6 | 38.4 | 0 | 5 | 1009 | -8.5 | 22.546 | 33.2 | 41.7 | 247 | -8.6 | 22.745 | 33.1 | 41.9 | 248 | OK- No Action Required | 40 | 40 | 5 | 56.6 | 38.4 | 0 | >>>>
BGW2K115 | 2019-03-19 13:10 | 56.5 | 38.9 | 0 | 4.6 | 1009 | -0.1 | 0.173 | 25.2 | 3.7 | 21 | 0.1 | -0.085 | 24.7 | N/A | N/A | Adjusted Increase | 5 | 7 | 4.6 | 56.4 | 38.8 | 0 | >>>>
BGW2K117 | 2019-03-19 13:12 | 44.8 | 35.1 | 0 | 20.1 | 1008 | -4.2 | 5.871 | 26.6 | 21.2 | 99 | -4.1 | 5.868 | 26.4 | 21.2 | 99 | OK- No Action Required | 25 | 25 | 20.1 | 44.8 | 35.1 | 0 | >>>>
BLW2X465 | 2019-03-19 13:14 | 0.6 | 0.4 | 20.3 | 78.7 | 1009 | -64.5 | 0.121 | 27 | 6.3 | 0 | -64.2 | 0.106 | 26.9 | 5.9 | 0 | Shut/Shut | 0 | 0 | 1.97 | 0.9 | 0.8 | 19.9 | 12
BLW2X464 | 2019-03-19 13:15 | 0.3 | 0.3 | 20.4 | 79 | 1009 | -65.1 | 0.136 | 27 | 3.1 | 0 | -65.1 | 0.169 | 27 | 3.4 | 0 | Shut/Shut | 0 | 0 | 1.89 | 0.3 | 0.3 | 20.4 | 6
BGW2X458 | 2019-03-19 13:18 | 55.7 | 37.2 | 0 | 7.1 | 1009 | -2.9 | 5.367 | 25.3 | 10.2 | 59 | -2.9 | 5.358 | 24.9 | 10.2 | 59 | OK- No Action Required | 15 | 15 | 7.1 | 55.7 | 37.2 | 0 | >>>>
BLW2X466 | 2019-03-19 13:19 | 0.2 | 0.1 | 20.3 | 79.4 | 1009 | -65 | 0.025 | 26.2 | 1.3 | 0 | -64.1 | 0.024 | 25.9 | 1.3 | 0 | Shut/Shut | 0 | 0 | 2.67 | 0.7 | 0.6 | 19.6 | 4
BLW2X467 | 2019-03-19 13:21 | 0.1 | 0.1 | 20.5 | 79.3 | 1009 | -64.6 | 0.008 | 26.6 | 0.7 | 0 | -64.4 | 0.01 | 26.5 | 0.8 | 0 | Shut/Shut | 0 | 0 | 1.81 | 0.2 | 0.1 | 20.5 | 2
BGW2X459 | 2019-03-19 13:23 | 47.1 | 35.1 | 0 | 17.8 | 1009 | 0 | 0.625 | 26.4 | 3.4 | 17 | 0 | 1.059 | 26.3 | 4.5 | 22 | OK- No Action Required | 15 | 15 | 17.8 | 47.1 | 35.1 | 0 | >>>>
BGW2T234 | 2019-03-19 13:28 | 54.1 | 40.1 | 0 | 5.8 | 1009 | -0.6 | 1.13 | 32.3 | 9.2 | 52 | -0.7 | 1.389 | 32 | 10.3 | 58 | OK- No Action Required | 20 | 20 | 5.8 | 54.1 | 40.1 | 0 | >>>>
BLW2X468 | 2019-03-19 13:30 | 51.4 | 37 | 0.7 | 10.9 | 1009 | -9.9 | 4.466 | 24.5 | 18.6 | 100 | -9.9 | 4.449 | 24.4 | 18.6 | 100 | OK- No Action Required | 25 | 25 | 8.25 | 51.4 | 37 | 0.7 | >>>>
BGW2T235 | 2019-03-19 13:30 | 0.3 | 0.3 | 20.2 | 79.2 | 1009 | -0.1 | -0.049 | 23.1 | N/A | N/A | -0.1 | -0.051 | 22.8 | N/A | N/A | Shut/Shut | 0 | 0 | 2.84 | 30.9 | 28.1 | 2.1 | 6
BGW2T230 | 2019-03-19 13:32 | 47.1 | 34.4 | 0 | 18.5 | 1009 | -0.4 | 1.557 | 28.1 | 10.9 | 54 | -0.4 | 1.547 | 27.6 | 10.9 | 54 | OK- No Action Required | 20 | 20 | 18.5 | 47.1 | 34.4 | 0 | >>>>
BGW2T229 | 2019-03-19 13:33 | 0.2 | 0.2 | 20 | 79.6 | 1009 | -0.2 | -0.055 | 22 | N/A | N/A | -0.2 | -0.057 | 23.8 | N/A | N/A | Shut/Shut | 0 | 0 | 4 | 40.1 | 26.3 | 1.1 | 4
BGW2T438 | 2019-03-19 13:34 | 53.2 | 38.6 | 0 | 8.2 | 1009 | -0.6 | 5.245 | 28.6 | 10 | 55 | -0.6 | 5.257 | 28.2 | 10 | 55 | OK- No Action Required | 20 | 20 | 8.2 | 53.2 | 38.5 | 0 | >>>>
BGW2T339 | 2019-03-19 13:35 | 53.1 | 38.5 | 0 | 8.4 | 1009 | -4.1 | 2.54 | 31.2 | 13.9 | 77 | -4.1 | 2.524 | 30.5 | 13.9 | 77 | OK- No Action Required | 25 | 25 | 8.4 | 53.1 | 38.5 | 0 | >>>>
BGW2T387 | 2019-03-19 13:37 | 59 | 38.2 | 0.2 | 2.6 | 1009 | 0 | 1.668 | 25.3 | 2.9 | 18 | 0.2 | 0.738 | 25.4 | 1.9 | 12 | Adjusted Increase | 5 | 7 | 1.84 | 59 | 38.1 | 0.2 | >>>>
BGW2T228 | 2019-03-19 13:38 | 13.6 | 21.4 | 7.5 | 57.5 | 1009 | -1.5 | -0.036 | 22 | N/A | N/A | -1.2 | -0.038 | 21.3 | N/A | N/A | Shut/Shut | 0 | 0 | 29.15 | 13.6 | 21.4 | 7.5 | >>>>
BGW2T224 | 2019-03-19 13:41 | 58.4 | 40.9 | 0 | 0.7 | 1009 | -1.9 | 0.016 | 28.2 | 1.1 | 6 | 2.4 | 0.069 | 25.1 | 2.3 | 14 | Surge | 15 | 17 | 0.7 | 58.4 | 40.9 | 0 | >>>>
BGW2T220 | 2019-03-19 13:42 | 59.7 | 37.9 | 0 | 2.4 | 1008 | 0 | 0.087 | 23.8 | 5.7 | 36 | 0 | 0.017 | 24 | 2.6 | 16 | Adjusted Increase | 5 | 7 | 2.4 | 59.7 | 37.8 | 0 | >>>>
BGW2T219 | 2019-03-19 13:43 | 46 | 35.1 | 0 | 18.9 | 1008 | -2.1 | 4.188 | 29.6 | 8.8 | 42 | -2.1 | 4.117 | 28 | 8.8 | 42 | OK- No Action Required | 15 | 15 | 18.9 | 46 | 35 | 0 | >>>>
BGW2Z342 | 2019-03-19 14:29 | 59.8 | 37.8 | 0 | 2.4 | 1008 | 0 | 0.05 | 29.9 | 2 | 12 | 0.1 | -0.169 | 28.4 | N/A | N/A | Adjusted Increase | 12 | 15 | 2.4 | 59.8 | 37.8 | 0 | >>>>
BGW2Z343 | 2019-03-19 14:31 | 48 | 35.2 | 0.1 | 16.7 | 1009 | -1.7 | 7.823 | 30.5 | 24.5 | 123 | -1.8 | 7.896 | 30.6 | 24.6 | 123 | OK- No Action Required | 40 | 40 | 16.32 | 48 | 35.2 | 0.1 | >>>>
BGW2Z344 | 2019-03-19 14:34 | 50.9 | 35.7 | 0.2 | 13.2 | 1009 | -0.5 | 1.59 | 29.8 | 11.1 | 59 | -0.4 | 1.597 | 30.2 | 11.1 | 59 | OK- No Action Required | 25 | 25 | 12.44 | 50.9 | 35.7 | 0.2 | >>>>
BGW2Z345 | 2019-03-19 14:36 | 46.1 | 34.9 | 0 | 19 | 1009 | -0.1 | 0.608 | 28.9 | 6.8 | 33 | -0.2 | 0.606 | 28.8 | 6.8 | 32 | OK- No Action Required | 20 | 20 | 19 | 46.1 | 34.9 | 0 | >>>>
BGW2Z346 | 2019-03-19 14:38 | 51.5 | 36.6 | 0 | 11.9 | 1009 | -4.6 | 2.55 | 29.2 | 14 | 75 | -4.6 | 2.621 | 29 | 14.2 | 76 | OK- No Action Required | 25 | 25 | 11.9 | 51.5 | 36.6 | 0 | >>>>
BHW2A347 | 2019-03-19 14:40 | 56.3 | 41 | 0 | 2.7 | 1009 | -22.8 | 22.049 | 34.7 | 142.6 | 841 | -22.8 | 22.261 | 34.5 | 143.4 | 846 | OK- No Action Required | 99 | 99 | 2.7 | 56.3 | 41 | 0 | >>>>
BHW2A348 | 2019-03-19 14:44 | 54.6 | 39.7 | 0 | 5.7 | 1009 | -27.3 | 17.09 | 32.7 | 125.7 | 719 | -24.8 | 16.858 | 32.6 | 125 | 715 | OK- No Action Required | 99 | 99 | 5.7 | 54.6 | 39.7 | 0 | >>>>
BHW2A349 | 2019-03-19 14:45 | 15.9 | 10.5 | 16.9 | 56.7 | 1009 | -36.7 | -0.158 | 27.6 | N/A | N/A | -36 | -0.15 | 28.4 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 0 | 26.5 | 10.5 | 2.9 | >>>>
BHW2A350 | 2019-03-19 14:46 | 58.4 | 40.6 | 0 | 1 | 1009 | -27.1 | 11.905 | 38.9 | 104.4 | 639 | -28.6 | 11.068 | 38.3 | 100.7 | 616 | OK- No Action Required | 99 | 99 | 1 | 58.3 | 40.6 | 0 | >>>>
BGW2L380 | 2019-03-20 11:38 | 24.7 | 25.6 | 5.1 | 44.6 | 1006 | -0.2 | 13.32 | 25 | 1.7 | 4 | -0.1 | 13.323 | 24.6 | 1.7 | 4 | OK- No Action Required | 5 | 5 | 25.32 | 25 | 25.6 | 5.1 | >>>>
BGW2L134 | 2019-03-20 11:39 | 40.1 | 33.7 | 1.2 | 25 | 1006 | -0.6 | 0.923 | 37.2 | 17.7 | 74 | -0.5 | 0.882 | 36.4 | 17.3 | 72 | OK- No Action Required | 20 | 20 | 20.46 | 40.1 | 33.7 | 1.2 | >>>>
BGW2L133 | 2019-03-20 11:41 | 46.5 | 37.9 | 0 | 15.6 | 1006 | -1 | 4.953 | 42 | 9.4 | 45 | -0.9 | 4.955 | 41.8 | 9.4 | 45 | OK- No Action Required | 15 | 15 | 15.6 | 46.5 | 37.9 | 0 | >>>>
BGW2L431 | 2019-03-20 11:42 | 51 | 38.2 | 0 | 10.8 | 1006 | -39.2 | 25.168 | 48.5 | 147.3 | 787 | -38.8 | 24.89 | 48.1 | 146.6 | 783 | OK- No Action Required | 90 | 90 | 10.8 | 51 | 38.3 | 0 | >>>>
BGW2L378 | 2019-03-20 11:43 | 43.6 | 37.2 | 0 | 19.2 | 1006 | -0.8 | 2.702 | 47.6 | 13.8 | 63 | -0.8 | 2.723 | 47.3 | 13.8 | 63 | OK- No Action Required | 20 | 20 | 19.2 | 43.6 | 37.2 | 0 | >>>>
BGW2L140 | 2019-03-20 11:45 | 52.8 | 40.9 | 0 | 6.3 | 1006 | -48.7 | 10.856 | 34.2 | 7 | 38 | -49 | 11.071 | 33.4 | 7 | 39 | OK- No Action Required | 50 | 50 | 6.3 | 52.8 | 40.9 | 0 | >>>>
BGW2L377 | 2019-03-20 11:46 | 43.8 | 36.5 | 0.2 | 19.5 | 1006 | -0.1 | 1.186 | 38.3 | 9.3 | 42 | -0.1 | 1.203 | 37.8 | 9.3 | 43 | OK- No Action Required | 15 | 15 | 18.74 | 43.8 | 36.5 | 0.2 | >>>>
BGW2L420 | 2019-03-20 11:47 | 1.2 | 2.6 | 18.5 | 77.7 | 1006 | -0.2 | 0.797 | 25.2 | 1.9 | 0 | -0.4 | 0.962 | 26.9 | 2.1 | 0 | Shut/Shut | 0 | 0 | 7.77 | 22.3 | 7.4 | 4.3 | 24
BGW2L359 | 2019-03-20 11:48 | 5.3 | 16.7 | 6.6 | 71.4 | 1006 | -0.5 | 1.134 | 24.6 | 2.2 | 1 | -0.6 | 1.179 | 24.4 | 2.3 | 1 | OK- No Action Required | 5 | 5 | 46.45 | 5.4 | 16.7 | 6.6 | >>>>
BGW2L101 | 2019-03-20 11:49 | 4 | 2 | 18.7 | 75.3 | 1007 | -0.1 | -0.084 | 21.5 | N/A | N/A | -0.1 | -0.078 | 21.1 | N/A | N/A | Shut/Shut | 0 | 0 | 4.61 | 4 | 5.3 | 14.5 | 80
BGW2L137 | 2019-03-20 11:51 | 48.1 | 37.5 | 0.2 | 14.2 | 1007 | -23.2 | 1.065 | 21.5 | 31.7 | 160 | -24.8 | 1.55 | 20.9 | 38.3 | 193 | Surge | 40 | 40 | 13.44 | 48.1 | 37.5 | 0.2 | >>>>
BGW2L417 | 2019-03-20 11:53 | 38.5 | 29.3 | 5.8 | 26.4 | 1007 | -1 | 1.364 | 29.3 | 21.9 | 88 | -1.7 | 0.626 | 29.1 | 14.8 | 60 | Surge | 20 | 20 | 4.48 | 38.5 | 29.3 | 5.8 | >>>>
BGW2L056 | 2019-03-20 11:54 | 26 | 30.5 | 0 | 43.5 | 1007 | -0.1 | 13.359 | 26.8 | 7.8 | 21 | -0.1 | 13.281 | 26.6 | 7.8 | 21 | OK- No Action Required | 15 | 15 | 43.5 | 30.6 | 30.5 | 0 | >>>>
BGW2L082 | 2019-03-20 11:55 | 55.6 | 40.3 | 0 | 4.1 | 1007 | -40.3 | 19.246 | 31.8 | 37.7 | 219 | -40.5 | 19.364 | 31.5 | 37.8 | 220 | OK- No Action Required | 99 | 99 | 4.1 | 55.6 | 40.3 | 0 | >>>>
BGW2L448 | 2019-03-20 11:56 | 47.4 | 37 | 0 | 15.6 | 1007 | -27 | 14.913 | 37.4 | 70.8 | 351 | -25.1 | 15.649 | 37.1 | 72.6 | 361 | OK- No Action Required | 60 | 60 | 15.6 | 47.4 | 37 | 0 | >>>>
BGW2L150 | 2019-03-20 11:57 | 51.5 | 39 | 0 | 9.5 | 1007 | -58 | 5.862 | 41.5 | 71.1 | 384 | -61.3 | 5.917 | 41.2 | 71.3 | 385 | OK- No Action Required | 99 | 99 | 9.5 | 51.5 | 39 | 0 | >>>>
BGW2L376 | 2019-03-20 11:59 | 43 | 35.6 | 0.5 | 20.9 | 1007 | -0.4 | 2.406 | 27.1 | 3.4 | 15 | -0.4 | 2.303 | 27 | 3.3 | 15 | OK- No Action Required | 5 | 5 | 19.01 | 43 | 35.6 | 0.5 | >>>>
BGW2L433 | 2019-03-20 12:00 | 28.3 | 24.5 | 6.4 | 40.8 | 1007 | -0.3 | 1.414 | 27.9 | 10.3 | 30 | -0.2 | 1.42 | 27.2 | 10.3 | 30 | OK- No Action Required | 10 | 10 | 16.61 | 35.7 | 25.1 | 1.5 | >>>>
BGW2L053 | 2019-03-20 12:01 | 56.4 | 39.5 | 0 | 4.1 | 1007 | -62.4 | 0.384 | 29.5 | 18.6 | 110 | -62.2 | 0.223 | 29 | 14.2 | 84 | Blocked-Investigation Required | 99 | 99 | 4.1 | 56.3 | 39.5 | 0 | >>>>
BGW2Q209 | 2019-03-20 12:56 | 42.5 | 28.9 | 2.7 | 25.9 | 1009 | -51.6 | -0.052 | 26.1 | N/A | N/A | -50.8 | -0.09 | 25.7 | N/A | N/A | Blocked-Investigation Required | 25 | 25 | 15.69 | 46.7 | 30.9 | 2.3 | >>>>
BGW2Q185 | 2019-03-20 12:57 | 52.5 | 33.6 | 0 | 13.9 | 1009 | -2.2 | 20.731 | 27.4 | 10.2 | 56 | -5.5 | 21.03 | 26.9 | 10.2 | 56 | OK- No Action Required | 25 | 25 | 13.9 | 52.5 | 33.6 | 0 | >>>>
BGW2Q180 | 2019-03-20 12:58 | 28.4 | 17.1 | 9.5 | 45 | 1009 | 0 | 0.05 | 26.5 | 0.9 | 2 | 0 | 0.058 | 25.8 | 1 | 3 | OK- No Action Required | 5 | 5 | 9.09 | 28.4 | 17.1 | 5 | >>>>
BGW2Q190 | 2019-03-20 13:00 | 53.7 | 34.9 | 0 | 11.4 | 1009 | -6.7 | 1.475 | 28.7 | 23.2 | 130 | -6.6 | 1.484 | 28.4 | 23.3 | 131 | OK- No Action Required | 40 | 40 | 11.4 | 53.7 | 34.9 | 0 | >>>>
BGW2Q199 | 2019-03-20 13:01 | 49.9 | 34.3 | 0 | 15.8 | 1009 | -47.2 | -0.08 | 26.6 | N/A | N/A | -45.7 | -0.063 | 26.2 | N/A | N/A | Blocked-Investigation Required | 15 | 15 | 15.8 | 50 | 34.3 | 0 | >>>>
BGW2Q175 | 2019-03-20 13:02 | 23.2 | 25.2 | 0.6 | 51 | 1009 | -1.6 | 3.148 | 24.8 | 0.8 | 2 | -1.6 | 3.102 | 24.5 | 0.8 | 2 | OK- No Action Required | 5 | 5 | 48.73 | 23.2 | 25.2 | 0.6 | >>>>
BGW2Q179 | 2019-03-20 13:04 | 43.4 | 30.6 | 1.8 | 24.2 | 1009 | -2.9 | 0.549 | 26.3 | 3.2 | 14 | -6 | 1.291 | 25.5 | 4.9 | 22 | Adjusted Decrease | 15 | 10 | 17.4 | 43.4 | 30.6 | 1.8 | >>>>
BGW2Q335 | 2019-03-20 13:05 | 49.7 | 36.6 | 0 | 13.7 | 1009 | -5 | 3.799 | 29.7 | 36.8 | 191 | -5.1 | 3.695 | 29.3 | 36.3 | 189 | OK- No Action Required | 40 | 40 | 13.7 | 49.7 | 36.6 | 0 | >>>>
BGW2Q336 | 2019-03-20 13:07 | 50 | 36.2 | 1.1 | 12.7 | 1009 | 0 | 0.026 | 27.2 | 1.4 | 7 | 0 | 0.032 | 27 | 1.5 | 8 | Damaged | 15 | 15 | 8.54 | 50 | 36.2 | 1.1 | >>>>
BGW2Q204 | 2019-03-20 13:08 | 14.4 | 10.9 | 15.3 | 59.4 | 1009 | -4.1 | -0.333 | 25.3 | N/A | N/A | -4.2 | -0.325 | 25 | N/A | N/A | Blocked-Investigation Required | 10 | 10 | 1.57 | 25.8 | 17.1 | 2.9 | >>>>
BGW2Q214 | 2019-03-20 13:09 | 52.7 | 35.8 | 0 | 11.5 | 1009 | -12.4 | 0.778 | 30.7 | 16.7 | 92 | -11.5 | 0.201 | 30.3 | 8.5 | 47 | Surge | 30 | 30 | 11.5 | 52.7 | 35.8 | 0 | >>>>
BGW2Q203 | 2019-03-20 13:10 | 58.2 | 40 | 0 | 1.8 | 1009 | -46.5 | 10.455 | 38.9 | 59.4 | 362 | -39.9 | 9.848 | 38.1 | 57.9 | 353 | OK- No Action Required | 99 | 99 | 1.8 | 58.2 | 40 | 0 | >>>>
BGW2Q382 | 2019-03-20 13:11 | 51.8 | 37.6 | 0.3 | 10.3 | 1009 | -2.4 | 8.737 | 31.5 | 25.9 | 140 | -1.4 | 9.01 | 31.6 | 26.3 | 143 | OK- No Action Required | 30 | 30 | 9.17 | 51.8 | 37.6 | 0.3 | >>>>
BGW2Q184 | 2019-03-20 13:13 | 53.3 | 38.1 | 0.2 | 8.4 | 1009 | -0.8 | 0.711 | 28.5 | 26.2 | 146 | -1 | 0.648 | 28.1 | 25 | 139 | OK- No Action Required | 25 | 25 | 7.64 | 53.3 | 38.1 | 0.2 | >>>>
BGW2Q189 | 2019-03-20 13:14 | 0.3 | 1.5 | 19.2 | 79 | 1009 | 0 | 0.314 | 25.2 | 0.2 | 0 | 0 | 0.307 | 25.4 | 0.2 | 0 | Shut/Shut | 3 | 0 | 6.42 | 44.2 | 38.1 | 2 | 6
BGW2Q338 | 2019-03-20 13:15 | 13.6 | 18.5 | 3.9 | 64 | 1009 | -0.5 | -0.086 | 23.7 | N/A | N/A | -0.5 | -0.102 | 23.6 | N/A | N/A | Shut/Shut | 0 | 0 | 49.26 | 13.6 | 18.5 | 3.9 | >>>>
BGW2Q337 | 2019-03-20 13:16 | 42.3 | 33.9 | 0 | 23.8 | 1010 | -0.5 | 10.43 | 25.8 | 7.1 | 31 | -0.5 | 10.64 | 25.4 | 7.1 | 31 | OK- No Action Required | 15 | 15 | 23.8 | 42.3 | 33.9 | 0 | >>>>
BGW2Q444 | 2019-03-20 13:18 | 55.7 | 35.8 | 0.1 | 8.4 | 1010 | -2.2 | 0.641 | 27.9 | 7.1 | 41 | -2 | 0.61 | 27.4 | 6.9 | 40 | OK- No Action Required | 15 | 15 | 8.02 | 55.7 | 35.8 | 0.1 | >>>>
BGW2Q168 | 2019-03-20 13:18 | 0.5 | 0.3 | 19.5 | 79.7 | 1010 | -49.2 | -0.007 | 24.2 | N/A | N/A | -58.3 | -0.382 | 25.2 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 5.99 | 45.1 | 24.2 | 1.3 | 10
BGW2X167 | 2019-03-20 13:24 | 50.7 | 36.3 | 0 | 13 | 1010 | -1.9 | 0.82 | 38.4 | 16.9 | 89 | -2 | 0.802 | 35.8 | 16.8 | 89 | OK- No Action Required | 40 | 40 | 13 | 50.7 | 36.3 | 0 | >>>>
BGW2X162 | 2019-03-20 13:26 | 46.7 | 34.8 | 0 | 18.5 | 1010 | -1.2 | 1.129 | 22.9 | 9.4 | 46 | -1.2 | 1.125 | 22.6 | 9.4 | 46 | OK- No Action Required | 20 | 20 | 18.5 | 46.6 | 34.8 | 0 | >>>>
BGW2X161 | 2019-03-20 13:31 | 58.1 | 35.9 | 0.6 | 5.4 | 1010 | 0 | 0.005 | 27.9 | 0.3 | 1 | 0 | 0.008 | 27.6 | 0.4 | 2 | Damaged | 5 | 5 | 3.13 | 58.4 | 35.9 | 0.4 | >>>>
BGW2X160 | 2019-03-20 13:33 | 56.6 | 38.3 | 0 | 5.1 | 1010 | -0.6 | 31.432 | 25.5 | 2.7 | 16 | -0.6 | 31.429 | 25.1 | 2.7 | 16 | Change Orife Plate Required | 25 | 25 | 5.1 | 56.6 | 38.3 | 0 | >>>>
BGW2X166 | 2019-03-20 13:35 | 48.7 | 37.2 | 0 | 14.1 | 1010 | -0.2 | 0.211 | 26.5 | 8.7 | 44 | -0.2 | 0.206 | 26.5 | 8.6 | 44 | OK- No Action Required | 15 | 15 | 14.1 | 48.7 | 37.2 | 0 | >>>>
BGW2X159 | 2019-03-20 13:36 | 46.8 | 35.8 | 0 | 17.4 | 1009 | -1.3 | 3.752 | 26.4 | 17 | 83 | -1.3 | 3.741 | 26.5 | 17 | 83 | OK- No Action Required | 25 | 25 | 17.4 | 46.8 | 35.8 | 0 | >>>>
BGW2X249 | 2019-03-20 13:39 | 39.5 | 31.2 | 0 | 29.3 | 1009 | -4.6 | 13.128 | 25.4 | 31.7 | 131 | -4.6 | 13.108 | 25 | 31.7 | 131 | OK- No Action Required | 40 | 40 | 29.3 | 39.6 | 31.2 | 0 | >>>>
BGW2K111 | 2019-03-20 13:41 | 52.4 | 37.3 | 0 | 10.3 | 1010 | 0 | 5.819 | 26 | 10.6 | 58 | 0 | 5.829 | 25.7 | 10.6 | 58 | OK- No Action Required | 15 | 15 | 10.3 | 52.4 | 37.3 | 0 | >>>>
BGW2L380 | 2019-03-21 09:05 | 23.2 | 25 | 5.4 | 46.4 | 1005 | -0.2 | 12.939 | 23.6 | 1.7 | 4 | -0.2 | 12.972 | 23.1 | 1.7 | 4 | OK- No Action Required | 5 | 5 | 25.99 | 23.2 | 25 | 5.4 | >>>>
BGW2L134 | 2019-03-21 09:06 | 38.1 | 33 | 1.4 | 27.5 | 1006 | -0.8 | 0.843 | 37.2 | 16.9 | 67 | -0.8 | 0.899 | 36.8 | 17.4 | 69 | OK- No Action Required | 25 | 25 | 22.21 | 38.1 | 33.1 | 1.4 | >>>>
BGW2L133 | 2019-03-21 09:07 | 45.1 | 37.5 | 0 | 17.4 | 1006 | -1.3 | 5.324 | 42.2 | 9.7 | 46 | -1.2 | 5.35 | 41.8 | 9.7 | 46 | OK- No Action Required | 15 | 15 | 17.4 | 45.1 | 37.5 | 0 | >>>>
BGW2L431 | 2019-03-21 09:09 | 51.1 | 38.3 | 0 | 10.6 | 1006 | -59.8 | 14.431 | 48 | 110.5 | 592 | -56.9 | 14.423 | 47.7 | 110.7 | 593 | OK- No Action Required | 90 | 90 | 10.6 | 51.1 | 38.3 | 0 | >>>>
BGW2L378 | 2019-03-21 09:10 | 43.1 | 36.9 | 0 | 20 | 1006 | -0.9 | 3.016 | 47.6 | 14.6 | 66 | -0.8 | 2.999 | 47.3 | 14.5 | 65 | OK- No Action Required | 15 | 15 | 20 | 43.1 | 36.9 | 0 | >>>>
BGW2L140 | 2019-03-21 09:11 | 53.1 | 41.2 | 0 | 5.7 | 1006 | -68.9 | 0.839 | 29.3 | 1.9 | 10 | -68.8 | 0.93 | 28.6 | 2 | 11 | OK- No Action Required | 50 | 50 | 5.7 | 53.1 | 41.2 | 0 | >>>>
BGW2L377 | 2019-03-21 09:13 | 40.1 | 35.3 | 0.4 | 24.2 | 1006 | -0.2 | 1.158 | 38.5 | 9.1 | 38 | -0.2 | 1.158 | 38.1 | 9.1 | 38 | OK- No Action Required | 20 | 20 | 22.69 | 40.1 | 35.3 | 0.4 | >>>>
BGW2L420 | 2019-03-21 09:14 | 1 | 2.6 | 18.4 | 78 | 1006 | 0 | 1.19 | 24.6 | 2.3 | 0 | 0 | 1.113 | 29.1 | 2.2 | 0 | Shut/Shut | 0 | 0 | 8.45 | 31.5 | 17.8 | 2.5 | 20
BGW2L359 | 2019-03-21 09:15 | 6.6 | 16.5 | 7.5 | 69.4 | 1006 | -0.2 | 1.132 | 23.3 | 2.2 | 1 | -0.2 | 1.038 | 22.6 | 2.1 | 1 | OK- No Action Required | 3 | 3 | 41.05 | 6.7 | 16.5 | 7.5 | >>>>
BGW2L101 | 2019-03-21 09:16 | 2.4 | 1.4 | 18.9 | 77.3 | 1006 | -0.1 | -0.024 | 19.9 | N/A | N/A | -0.2 | -0.022 | 19.9 | N/A | N/A | Shut/Shut | 0 | 0 | 5.86 | 6.6 | 16 | 7.6 | 48
BGW2L137 | 2019-03-21 09:18 | 47.8 | 37.5 | 0.3 | 14.4 | 1006 | -35.2 | 2.352 | 20.7 | 47 | 235 | -31.1 | 1.977 | 20.2 | 43.2 | 216 | Surge | 40 | 40 | 13.27 | 47.8 | 37.5 | 0.3 | >>>>
BGW2L417 | 2019-03-21 09:20 | 37.8 | 28.8 | 6.2 | 27.2 | 1006 | -1.4 | 0.949 | 27.6 | 18.3 | 72 | -1.5 | 0.607 | 27.2 | 14.7 | 58 | Surge | 25 | 25 | 3.76 | 37.8 | 28.8 | 6.2 | >>>>
BGW2L056 | 2019-03-21 09:21 | 22.4 | 29.4 | 0 | 48.2 | 1006 | -0.2 | 13.393 | 26.4 | 7.8 | 18 | -0.1 | 13.51 | 25.8 | 7.8 | 18 | OK- No Action Required | 10 | 10 | 48.2 | 30.8 | 29.4 | 0 | >>>>
BGW2L082 | 2019-03-21 09:22 | 55.9 | 40.5 | 0 | 3.6 | 1006 | -42 | 18.717 | 31.4 | 37.1 | 217 | -41.8 | 18.878 | 31.1 | 37.3 | 218 | OK- No Action Required | 99 | 99 | 3.6 | 55.9 | 40.5 | 0 | >>>>
BGW2L448 | 2019-03-21 09:23 | 47.8 | 37.6 | 0 | 14.6 | 1006 | -32.3 | 17.095 | 37.3 | 75.5 | 378 | -24 | 17.596 | 37.2 | 77 | 385 | OK- No Action Required | 60 | 60 | 14.6 | 47.8 | 37.6 | 0 | >>>>
BGW2L150 | 2019-03-21 09:24 | 52.3 | 39.3 | 0 | 8.4 | 1006 | -70.3 | 1.263 | 39.6 | 32.9 | 180 | -69.7 | 1.524 | 39.1 | 36.2 | 198 | OK- No Action Required | 99 | 99 | 8.4 | 52.3 | 39.3 | 0 | >>>>
BGW2L376 | 2019-03-21 09:26 | 46.3 | 37.3 | 0.2 | 16.2 | 1006 | 0 | 3.153 | 25.8 | 3.9 | 18 | 0 | 3.133 | 25.7 | 3.8 | 18 | OK- No Action Required | 5 | 5 | 15.44 | 46.3 | 37.3 | 0.2 | >>>>
BGW2L433 | 2019-03-21 09:27 | 29.7 | 25.8 | 5.8 | 38.7 | 1006 | -0.2 | 1.541 | 27.2 | 10.7 | 33 | -0.1 | 1.588 | 26.6 | 10.9 | 34 | OK- No Action Required | 10 | 10 | 16.78 | 29.7 | 25.8 | 1.6 | >>>>
BGW2L053 | 2019-03-21 09:28 | 56 | 40 | 0 | 4 | 1006 | -70.8 | 0.063 | 28.6 | 7.5 | 44 | -71.1 | -0.057 | 27.9 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 4 | 56 | 40 | 0 | >>>>
BGW2X258 | 2019-03-21 10:35 | 55.1 | 38.4 | 0 | 6.5 | 1008 | -67.5 | 1.421 | 32.5 | 35.7 | 206 | -67 | 1.369 | 32.3 | 35 | 202 | OK- No Action Required | 99 | 99 | 6.5 | 55.6 | 38.5 | 0 | >>>>
BGW2X259 | 2019-03-21 10:36 | 60.4 | 38.9 | 0 | 0.7 | 1008 | -2.7 | 6.252 | 25.7 | 5.6 | 35 | -3.2 | 4.554 | 25.5 | 4.8 | 30 | Surge | 12 | 15 | 0.7 | 60.5 | 38.9 | 0 | >>>>
BGW2X393 | 2019-03-21 10:37 | 0.3 | 0.3 | 19.3 | 80.1 | 1008 | 0 | -0.138 | 23.5 | N/A | N/A | 0 | -0.139 | 24.3 | N/A | N/A | Shut/Shut | 0 | 0 | 7.15 | 12.5 | 3.7 | 3.5 | 6
BGW2X254 | 2019-03-21 10:39 | 46 | 34.9 | 0 | 19.1 | 1008 | -65.9 | 2.993 | 37.8 | 31.1 | 150 | -66.1 | 2.847 | 37.5 | 30.4 | 146 | Surge | 99 | 99 | 19.1 | 46 | 34.9 | 0 | >>>>
BGW2X239 | 2019-03-21 10:40 | 45.8 | 36.4 | 0.1 | 17.7 | 1008 | -5.7 | 0.582 | 27.6 | 14.3 | 68 | -5.2 | 0.462 | 27.8 | 12.7 | 61 | Surge | 15 | 15 | 17.32 | 45.8 | 36.4 | 0.1 | >>>>
BGW2X247 | 2019-03-21 10:42 | 39.8 | 35 | 0 | 25.2 | 1008 | -0.4 | 0.38 | 27 | 5.3 | 22 | -0.4 | 0.342 | 26.9 | 5 | 21 | OK- No Action Required | 15 | 15 | 25.2 | 39.8 | 35 | 0 | >>>>
BGW2X264 | 2019-03-21 10:43 | 57.4 | 39.2 | 0 | 3.4 | 1008 | -52.4 | 22.574 | 33 | 143.6 | 863 | -50.9 | 22.84 | 32.7 | 144.6 | 869 | OK- No Action Required | 99 | 99 | 3.4 | 57.5 | 39.2 | 0 | >>>>
BGW2X425 | 2019-03-21 10:44 | 0.2 | 0.3 | 19.9 | 79.6 | 1008 | -32.8 | 0.092 | 25.2 | 2.6 | 0 | -33.9 | 0.457 | 26.7 | 5.7 | 0 | Adjusted Decrease | 10 | 7 | 4.38 | 12.4 | 8.8 | 14.1 | 4
BGW2X446 | 2019-03-21 10:46 | 59.3 | 40.1 | 0 | 0.6 | 1008 | -2.5 | 0.071 | 24.3 | 2.3 | 14 | -2 | 0.006 | 24 | 0.7 | 4 | Adjusted Increase | 2 | 3 | 0.6 | 59.3 | 40.1 | 0 | >>>>
BGW2X443 | 2019-03-21 10:48 | 53.2 | 38.9 | 0.5 | 7.4 | 1008 | -33.1 | 2.2 | 23.5 | 12.9 | 72 | -32.2 | 1.906 | 22.9 | 12 | 67 | OK- No Action Required | 20 | 20 | 5.51 | 53.2 | 38.9 | 0.5 | >>>>
BGW2X157 | 2019-03-21 10:49 | 0.4 | 0.4 | 19.7 | 79.5 | 1008 | 0 | -0.083 | 22.3 | N/A | N/A | 0.1 | -0.07 | 24 | N/A | N/A | Shut/Shut | 0 | 0 | 5.03 | 0.7 | 0.6 | 15.6 | 8
BGW2X158 | 2019-03-21 10:50 | 0.5 | 0.3 | 20.3 | 78.9 | 1008 | -28.6 | 0.075 | 23 | 2.3 | 0 | -26.9 | 0.039 | 21.8 | 1.7 | 0 | Shut/Shut | 0 | 0 | 2.17 | 0.5 | 0.3 | 20.3 | 10
BGW2X441 | 2019-03-21 10:51 | 59.6 | 39.6 | 0 | 0.8 | 1008 | -2.2 | -0.06 | 26.1 | N/A | N/A | -2.2 | -0.054 | 25.4 | N/A | N/A | Blocked-Investigation Required | 20 | 20 | 0.8 | 59.6 | 39.6 | 0 | >>>>
BGW2X164 | 2019-03-21 10:53 | 52 | 37.2 | 1.1 | 9.7 | 1009 | -86.9 | -0.22 | 26.6 | N/A | N/A | -88.5 | -0.062 | 26.2 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 5.54 | 52 | 37.3 | 1.1 | >>>>
BGW2U243 | 2019-03-21 11:03 | 43.4 | 35.7 | 0 | 20.9 | 1008 | -11.5 | 9.311 | 37.6 | 56.1 | 255 | -11.5 | 9.273 | 37.3 | 56 | 255 | OK- No Action Required | 50 | 50 | 20.9 | 52.4 | 39.3 | 0 | >>>>
BGW2U398 | 2019-03-21 11:05 | 39.9 | 33 | 1.2 | 25.9 | 1008 | -26.3 | 5.868 | 32.4 | 44.5 | 186 | -21.9 | 5.322 | 31.8 | 42.5 | 178 | Surge | 45 | 40 | 21.36 | 39.9 | 33 | 1.2 | >>>>
BGW2U238 | 2019-03-21 11:07 | 37.1 | 32.4 | 0.8 | 29.7 | 1008 | -7.3 | 14.658 | 24.5 | 33.3 | 129 | -8.7 | 20.938 | 25.8 | 39.6 | 154 | Adjusted Decrease | 40 | 35 | 26.68 | 37.1 | 32.4 | 0.8 | >>>>
BGW2U227 | 2019-03-21 11:08 | 44 | 35.9 | 0 | 20.1 | 1008 | -11.2 | 23.651 | 33.7 | 41.7 | 192 | -10.3 | 23.717 | 33.5 | 41.8 | 193 | OK- No Action Required | 40 | 40 | 20.1 | 44 | 35.9 | 0 | >>>>
BGW2U232 | 2019-03-21 11:10 | 57.8 | 40.5 | 0.1 | 1.6 | 1008 | -57.1 | 0.925 | 40.3 | 28.5 | 173 | -58.1 | 1.018 | 40.1 | 29.9 | 181 | OK- No Action Required | 60 | 60 | 1.22 | 57.9 | 40.5 | 0.1 | >>>>
BGW2U226 | 2019-03-21 11:12 | 58.5 | 42.5 | 0 | 0 | 1008 | -63.9 | -0.003 | 24.2 | N/A | N/A | -63.5 | -0.001 | 24.8 | N/A | N/A | Blocked-Investigation Required | 40 | 40 | 0 | 58.5 | 42.5 | 0 | >>>>
BGW2U439 | 2019-03-21 11:13 | 12.9 | 8.7 | 16.4 | 62 | 1008 | 0 | 0.068 | 21.8 | 2.3 | 3 | -0.2 | 0.089 | 22.6 | 2.6 | 3 | Shut/Shut | 0 | 0 | 0.01 | 27.7 | 8.7 | 5.4 | >>>>
BGW2U241 | 2019-03-21 11:14 | 56.9 | 42.6 | 0 | 0.5 | 1008 | -54.7 | 2.324 | 51.6 | 27 | 161 | -53.9 | 2.046 | 50.5 | 25.4 | 151 | Surge | 40 | 42 | 0.5 | 56.9 | 42.6 | 0 | >>>>
BGW2U251 | 2019-03-21 11:15 | 54.8 | 41.8 | 0 | 3.4 | 1008 | -59.7 | 4.969 | 43.6 | 39.8 | 229 | -59.5 | 4.707 | 43.5 | 38.8 | 222 | OK- No Action Required | 99 | 99 | 3.4 | 54.8 | 41.8 | 0 | >>>>
BGW2U245 | 2019-03-21 11:17 | 48 | 36.8 | 1.4 | 13.8 | 1008 | -60.2 | -0.164 | 38.3 | N/A | N/A | -57.4 | -0.032 | 38.4 | N/A | N/A | Blocked-Investigation Required | 40 | 40 | 8.51 | 48 | 36.9 | 1.3 | >>>>
BGW2U391 | 2019-03-21 11:19 | 39.5 | 32.9 | 1.8 | 25.8 | 1008 | -12.4 | 5.972 | 38.2 | 20.7 | 86 | -14.4 | 7.392 | 37.8 | 23.1 | 95 | Surge | 30 | 25 | 19 | 39.5 | 32.9 | 1.8 | >>>>
BGW2U440 | 2019-03-21 11:20 | 0.3 | 0.2 | 20.2 | 79.3 | 1008 | -61.1 | 0.073 | 25.3 | 2.2 | 0 | -59.9 | 0.1 | 31.2 | 2.6 | 0 | Blocked-Investigation Required | 0 | 0 | 2.94 | 0.9 | 0.7 | 12.6 | 6
BGW2U284 | 2019-03-21 11:21 | 59.1 | 41.4 | 0 | 0 | 1008 | -62.9 | 0.521 | 42.3 | 13 | 80 | -62.6 | 0.53 | 41.7 | 13.1 | 81 | Blocked-Investigation Required | 99 | 99 | 0 | 59 | 41.4 | 0 | >>>>
BGW2U399 | 2019-03-21 11:23 | 47.9 | 38 | 1.3 | 12.8 | 1008 | -46.1 | -0.114 | 50.3 | N/A | N/A | -44.7 | 0.688 | 49.7 | 14.7 | 74 | Surge | 25 | 25 | 7.89 | 47.9 | 38 | 1.3 | >>>>
BGW2U351 | 2019-03-21 11:24 | 1.8 | 1.4 | 17 | 79.8 | 1008 | -62.2 | -0.066 | 40 | N/A | N/A | -62.1 | -0.028 | 47.4 | N/A | N/A | Blocked-Investigation Required |  | 0 | 15.54 | 30.7 | 18.5 | 4.5 | 36
BHW2U352 | 2019-03-21 11:25 | 54.9 | 40.4 | 0.4 | 4.3 | 1008 | -59.8 | 3.328 | 46.7 | 53.2 | 306 | -59.7 | 3.411 | 46.4 | 53.9 | 310 | OK- No Action Required | 99 | 99 | 2.79 | 54.9 | 40.4 | 0.4 | >>>>
BHW2U353 | 2019-03-21 11:26 | 57.2 | 41.2 | 0 | 1.6 | 1008 | -57.5 | 5.801 | 47 | 43.2 | 259 | -57.7 | 5.817 | 46.6 | 43.2 | 259 | OK- No Action Required | 99 | 99 | 1.6 | 57.2 | 41.2 | 0 | >>>>
BHW2U354 | 2019-03-21 11:28 | 47.5 | 37 | 1.4 | 14.1 | 1008 | -9.1 | 2.026 | 53.1 | 25.6 | 127 | -10.3 | 1.613 | 52.8 | 22.9 | 114 | Adjusted Decrease | 25 | 22 | 8.81 | 47.4 | 37 | 1.4 | >>>>
BGW1A004 | 2019-03-21 11:53 | 57.6 | 38.5 | 0 | 3.9 | 1009 | -3.5 | 2.427 | 28.4 | 13.8 | 83 | -2.4 | 1.075 | 28.1 | 9.2 | 55 | Surge | 20 | 25 | 3.9 | 57.6 | 38.4 | 0 | >>>>
BGW1A003 | 2019-03-21 11:54 | 60.4 | 37.8 | 0 | 1.8 | 1009 | -23.3 | 0.062 | 26.3 | 2 | 12 | -23.3 | -0.036 | 26.2 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 1.8 | 60.4 | 37.8 | 0 | >>>>
BGW1A005 | 2019-03-21 11:55 | 12.5 | 8.1 | 16.9 | 62.5 | 1009 | -23.3 | -0.145 | 24.7 | N/A | N/A | -23.2 | -0.134 | 24.6 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 0 | 13.4 | 7.6 | 4.2 | >>>>
BGW1A002 | 2019-03-21 11:56 | 9.1 | 5.7 | 17.9 | 67.3 | 1009 | -23.3 | -0.153 | 24.7 | N/A | N/A | -23.3 | -0.145 | 24.5 | N/A | N/A | Blocked-Investigation Required | 30 | 30 | 0 | 9.1 | 5.7 | 16.1 | >>>>
BGW1A001 | 2019-03-21 11:58 | 13.3 | 8.4 | 16.8 | 61.5 | 1009 | -23.3 | -0.018 | 24.1 | N/A | N/A | -23.3 | -0.016 | 23.5 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 0 | 12.8 | 7.9 | 16.8 | >>>>
BGW1A268 | 2019-03-21 11:59 | 53.6 | 34.8 | 1.1 | 10.5 | 1009 | -7.9 | 1.63 | 24.9 | 2.8 | 16 | -8.1 | 1.662 | 24.7 | 2.8 | 16 | OK- No Action Required | 5 | 5 | 6.34 | 53.6 | 34.8 | 1.1 | >>>>
BGW1A009 | 2019-03-21 12:00 | 60.7 | 37.5 | 0 | 1.8 | 1009 | -23.4 | 0.001 | 24.1 | 0.3 | 2 | -23.4 | -0.017 | 23.8 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 1.8 | 60.7 | 37.5 | 0 | >>>>
BGW1A269 | 2019-03-21 12:01 | 17.8 | 10.4 | 14.9 | 56.9 | 1009 | -0.3 | -0.085 | 24.1 | N/A | N/A | -0.3 | -0.082 | 23.8 | N/A | N/A | Shut/Shut | 0 | 0 | 0.58 | 17.8 | 10.4 | 12.4 | >>>>
BGW1AM01 | 2019-03-21 12:02 | 23.8 | 25.6 | 0.2 | 50.4 | 1009 | -23.3 | 0.06 | 24.2 | 0.5 | 1 | -23.3 | 0.077 | 23.9 | 0.5 | 1 | OK- No Action Required | 99 | 99 | 49.64 | 23.8 | 25.6 | 0.2 | >>>>
BGW1A008 | 2019-03-21 12:04 | 52.2 | 35.5 | 0 | 12.3 | 1009 | -12.2 | 2.383 | 27.8 | 13.6 | 74 | -12.2 | 2.373 | 27.2 | 13.6 | 74 | OK- No Action Required | 25 | 25 | 12.3 | 52.2 | 35.5 | 0 | >>>>
BGW1A007 | 2019-03-21 12:04 | 1.4 | 1.1 | 16.2 | 81.3 | 1009 | 0 | -0.116 | 22.5 | N/A | N/A | 0 | -0.116 | 27.8 | N/A | N/A | Shut/Shut | 0 | 0 | 20.06 | 2.2 | 1.3 | 10.8 | 28
BGW1A006 | 2019-03-21 12:06 | 43.1 | 27.5 | 5.4 | 24 | 1009 | -19.6 | -0.15 | 22.6 | N/A | N/A | -19.6 | -0.144 | 22.2 | N/A | N/A | Blocked-Investigation Required | 5 | 5 | 3.59 | 43.2 | 27.5 | 5.4 | >>>>
BGW1B018 | 2019-03-21 12:09 | 60.4 | 36.6 | 0 | 3 | 1009 | -23.1 | -0.233 | 25.4 | N/A | N/A | -22.5 | -0.158 | 25 | N/A | N/A | Blocked-Investigation Required | 40 | 40 | 3 | 60.4 | 36.6 | 0 | >>>>
BGW1B017 | 2019-03-21 12:11 | 60.2 | 37.7 | 0 | 2.1 | 1009 | -19 | 3.392 | 26.2 | 4.1 | 26 | -18.3 | 1.79 | 25.6 | 3 | 18 | Adjusted Increase | 20 | 35 | 2.1 | 60.2 | 37.7 | 0 | >>>>
BGW1B011 | 2019-03-21 12:12 | 17.6 | 13.9 | 11.5 | 57 | 1009 | -0.2 | 1.469 | 28.7 | 10.5 | 19 | -0.2 | 1.486 | 27.1 | 10.6 | 19 | OK- No Action Required | 20 | 20 | 13.53 | 28.3 | 13.9 | 6.4 | >>>>
BGW1B010 | 2019-03-21 12:13 | 2 | 1.5 | 19.2 | 77.3 | 1009 | -23.1 | 0.005 | 23.7 | 1.3 | 0 | -23.1 | 0.047 | 24.4 | 3.8 | 0 | Blocked-Investigation Required | 99 | 99 | 4.72 | 11.4 | 8.8 | 11.9 | 40
BGW1B013 | 2019-03-21 12:14 | 34 | 18.7 | 7.6 | 39.7 | 1009 | -0.1 | -0.039 | 23.7 | N/A | N/A | 0 | -0.04 | 22.9 | N/A | N/A | Shut/Shut | 0 | 0 | 10.97 | 34 | 18.7 | 7.7 | >>>>
BGW1B016 | 2019-03-21 12:16 | 54.1 | 35.7 | 0 | 10.2 | 1009 | -17.5 | -0.145 | 24.5 | N/A | N/A | -17.6 | -0.242 | 24 | N/A | N/A | Blocked-Investigation Required | 20 | 20 | 10.2 | 54.1 | 35.7 | 0 | >>>>
BGW1B019 | 2019-03-21 12:17 | 61.7 | 36.3 | 0 | 2 | 1009 | -22.8 | 0.447 | 24.5 | 1.5 | 9 | -22.8 | 0.542 | 24.1 | 1.6 | 10 | Blocked-Investigation Required | 99 | 99 | 2 | 61.7 | 36.3 | 0 | >>>>
BGW1B015 | 2019-03-21 12:18 | 62.9 | 35.1 | 0 | 2 | 1009 | -23.1 | -0.001 | 24.2 | N/A | N/A | -23 | 0.027 | 23.6 | 0.3 | 2 | Blocked-Investigation Required | 99 | 99 | 2 | 62.9 | 35.1 | 0 | >>>>
BGW1B020 | 2019-03-21 12:19 | 4.8 | 2.6 | 18.9 | 73.7 | 1009 | -22.9 | -0.061 | 23.7 | N/A | N/A | -22.9 | -0.09 | 23.5 | N/A | N/A | Blocked-Investigation Required | 40 | 40 | 2.26 | 5.2 | 2.4 | 7.7 | 96
BGW1B014 | 2019-03-21 12:20 | 13.9 | 7.7 | 16.2 | 62.2 | 1009 | -0.1 | -0.023 | 24.6 | N/A | N/A | -0.1 | -0.02 | 24.1 | N/A | N/A | Shut/Shut | 0 | 0 | 0.96 | 20.5 | 11.6 | 13.6 | >>>>
BGW1B012 | 2019-03-21 12:21 | 51.9 | 30.7 | 2.9 | 14.5 | 1009 | -23 | -0.071 | 24.8 | N/A | N/A | -23 | -0.049 | 24.7 | N/A | N/A | Blocked-Investigation Required | 99 | 99 | 3.54 | 51.9 | 30.7 | 2.9 | >>>>
BGW2S222 | 2019-03-21 13:13 | 53.1 | 40.6 | 0 | 6.3 | 1008 | -0.4 | 0.478 | 45.5 | 5.8 | 32 | -0.4 | 0.479 | 45.3 | 5.9 | 32 | OK- No Action Required | 40 | 40 | 6.3 | 53.1 | 40.6 | 0 | >>>>
BGW2S223 | 2019-03-21 13:14 | 52.1 | 38 | 0.1 | 9.8 | 1008 | -61.2 | 2.366 | 41.5 | 45.2 | 247 | -61.6 | 2.524 | 41.3 | 46.7 | 255 | OK- No Action Required | 99 | 99 | 9.42 | 52.1 | 38.1 | 0.1 | >>>>
BGW2S217 | 2019-03-21 13:16 | 47.3 | 36.5 | 0.3 | 15.9 | 1008 | -16.7 | 2.725 | 38.2 | 30.4 | 151 | -18 | 2.974 | 38.2 | 31.7 | 157 | Adjusted Decrease | 45 | 42 | 14.77 | 47.3 | 36.5 | 0.3 | >>>>
BGW2S212 | 2019-03-21 13:17 | 4.1 | 17.5 | 7.1 | 71.3 | 1008 | -0.7 | -0.202 | 30.2 | N/A | N/A | -0.8 | -0.203 | 31.8 | N/A | N/A | Blocked-Investigation Required | 5 | 5 | 44.46 | 23.8 | 17.1 | 3.6 | 82
BGW2S211 | 2019-03-21 13:18 | 51.4 | 39.1 | 0 | 9.5 | 1008 | -60.8 | 1.587 | 39.2 | 10.5 | 56 | -61.3 | 1.679 | 37.2 | 10.8 | 58 | OK- No Action Required | 99 | 99 | 9.5 | 51.4 | 39.1 | 0 | >>>>
BGW2S385 | 2019-03-21 13:21 | 49.7 | 35.8 | 2.6 | 11.9 | 1008 | -63.7 | 0.033 | 26.4 | 3.3 | 17 | -63.5 | 0.083 | 26.4 | 5.3 | 27 | Blocked-Investigation Required | 50 | 50 | 2.07 | 51.8 | 36.3 | 2.3 | >>>>
BGW2S281 | 2019-03-21 13:22 | 12.9 | 8.9 | 16.1 | 62.1 | 1008 | -62.9 | 0.418 | 25.9 | 5.4 | 7 | -62.8 | 0.297 | 25.2 | 4.6 | 6 | Blocked-Investigation Required | 99 | 99 | 1.24 | 12.9 | 8.9 | 9.4 | >>>>
BHW2S411 | 2019-03-21 13:24 | 57.4 | 41.9 | 0 | 0.7 | 1008 | -61 | 1.767 | 40.7 | 11.1 | 67 | -62.9 | 1.668 | 40.1 | 10.8 | 65 | Blocked-Investigation Required | 99 | 99 | 0.7 | 57.5 | 41.9 | 0 | >>>>
BGW2S206 | 2019-03-21 13:25 | 52.7 | 36.7 | 1.3 | 9.3 | 1008 | 0.1 | -0.132 | 32.4 | N/A | N/A | 0.1 | -0.131 | 35.4 | N/A | N/A | Shut/Shut | 0 | 0 | 4.39 | 52.7 | 36.7 | 1.3 | >>>>
BGW2S216 | 2019-03-21 13:26 | 57.5 | 41.7 | 0 | 0.8 | 1008 | -63.4 | 0.759 | 36.9 | 25.8 | 155 | -63.7 | 0.742 | 34.4 | 25.6 | 154 | OK- No Action Required | 99 | 99 | 0.8 | 57.5 | 41.7 | 0 | >>>>
BGW2R207 | 2019-03-21 13:34 | 39.2 | 34 | 0.1 | 26.7 | 1009 | -0.1 | 7.424 | 39.6 | 5.8 | 23 | -0.2 | 10.251 | 39.2 | 6.8 | 28 | Adjusted Decrease | 15 | 12 | 26.32 | 39.2 | 34 | 0.2 | >>>>
BGW2R208 | 2019-03-21 13:35 | 50.1 | 36.3 | 0.7 | 12.9 | 1009 | -0.2 | 16.225 | 27.2 | 8.9 | 46 | -0.2 | 20.16 | 28.5 | 9.9 | 52 | Adjusted Decrease | 12 | 10 | 10.25 | 50.1 | 36.3 | 0.7 | >>>>
BGW2R384 | 2019-03-21 13:37 | 50.5 | 36.6 | 0.3 | 12.6 | 1009 | -4.8 | 1.816 | 29.7 | 25.4 | 134 | -4.1 | 1.629 | 29.4 | 24.1 | 127 | OK- No Action Required | 20 | 20 | 11.47 | 50.5 | 36.6 | 0.3 | >>>>
BGW2R202 | 2019-03-21 13:38 | 43.4 | 34.9 | 0 | 21.7 | 1009 | -57.3 | 7.886 | 39.7 | 50.3 | 229 | -58.1 | 7.881 | 39.2 | 50.3 | 229 | OK- No Action Required | 99 | 99 | 21.7 | 43.4 | 34.9 | 0 | >>>>
BGW2R436 | 2019-03-21 13:40 | 49.5 | 36.1 | 0.4 | 14 | 1009 | -3.5 | 3.186 | 32.5 | 33.6 | 174 | -4 | 3.73 | 32.4 | 36.3 | 188 | Adjusted Decrease | 10 | 38 | 12.49 | 49.5 | 36.1 | 0.4 | >>>>
BGW2R192 | 2019-03-21 13:42 | 45.9 | 34.2 | 1.9 | 18 | 1009 | -0.2 | 6.831 | 34 | 11.2 | 54 | -0.3 | 11.081 | 33.7 | 14.3 | 69 | Adjusted Decrease | 20 | 17 | 10.82 | 45.9 | 34.2 | 2 | >>>>
BGW2R197 | 2019-03-21 13:43 | 44.4 | 35.5 | 0 | 20.1 | 1009 | -3.7 | 3.389 | 38.3 | 34 | 158 | -3.8 | 3.363 | 37.5 | 33.9 | 158 | OK- No Action Required | 30 | 30 | 20.1 | 44.4 | 35.4 | 0 | >>>>
BGW2R201 | 2019-03-21 13:44 | 49 | 37.8 | 0.1 | 13.1 | 1009 | -1.9 | 1.597 | 24.5 | 24 | 123 | -1.8 | 1.581 | 25 | 23.8 | 122 | OK- No Action Required | 25 | 25 | 12.72 | 49.1 | 37.8 | 0 | >>>>
BGW2R437 | 2019-03-21 13:45 | 51.7 | 37.1 | 1.9 | 9.3 | 1009 | -7.9 | 9.397 | 24.6 | 6.8 | 36 | -8 | 9.546 | 24.3 | 6.8 | 37 | Damaged | 10 | 10 | 2.12 | 51.7 | 37.1 | 1.9 | >>>>
BGW2R277 | 2019-03-21 13:47 | 0.4 | 0.5 | 20 | 79.1 | 1009 | -3.3 | -0.053 | 25 | N/A | N/A | -3.3 | -0.048 | 24.6 | N/A | N/A | Shut/Shut | 0 | 0 | 3.5 | 1.4 | 1.5 | 19.4 | 8
BHW2R410 | 2019-03-21 13:48 | 42.3 | 34.7 | 1.2 | 21.8 | 1009 | -17.4 | 13.974 | 45.3 | 110.5 | 490 | -23.9 | 19.659 | 44.9 | 130.8 | 580 | Adjusted Decrease | 60 | 70 | 17.26 | 42.3 | 34.7 | 1.2 | >>>>
BHW2R409 | 2019-03-21 13:49 | 9.5 | 8.1 | 15.1 | 67.3 | 1009 | 0 | -0.067 | 37.3 | N/A | N/A | 0 | -0.077 | 38.8 | N/A | N/A | Shut/Shut | 0 | 0 | 10.22 | 31.6 | 24.6 | 2.4 | >>>>
BGW2P295 | 2019-03-21 13:52 | 51 | 36.4 | 0 | 12.6 | 1009 | -29.8 | 10.381 | 33.9 | 97.8 | 523 | -29.5 | 10.36 | 33.7 | 97.7 | 523 | OK- No Action Required | 70 | 70 | 12.6 | 51 | 36.4 | 0 | >>>>
BGW2P291 | 2019-03-21 13:54 | 55.6 | 38.8 | 0 | 5.6 | 1010 | -0.4 | 2.709 | 38 | 14.3 | 83 | -0.2 | 1.997 | 36.6 | 12.3 | 72 | Surge | 30 | 33 | 5.6 | 55.6 | 38.8 | 0 | >>>>
BGW2P293 | 2019-03-21 13:55 | 50.6 | 33.7 | 2 | 13.7 | 1010 | -0.1 | 0.42 | 32.4 | 12.3 | 65 | -0.1 | 0.373 | 32.2 | 11.6 | 61 | Damaged | 15 | 15 | 6.14 | 55.1 | 38.7 | 1.3 | >>>>
BGW2P290 | 2019-03-21 13:56 | 47.7 | 35.6 | 0 | 16.7 | 1010 | -4.2 | 7.956 | 31.1 | 24.6 | 123 | -4.3 | 8.098 | 30.9 | 24.8 | 124 | OK- No Action Required | 40 | 40 | 16.7 | 47.7 | 35.6 | 0 | >>>>
BGW2P447 | 2019-03-21 13:58 | 9.8 | 5.7 | 16.5 | 68 | 1010 | 0 | 0 | 25.2 | N/A | N/A | 0 | 0 | 26.1 | 0 | 0 | Shut/Shut | 0 | 0 | 5.63 | 28.2 | 21 | 5.6 | >>>>
BGW2P286 | 2019-03-21 13:59 | 54.5 | 36.8 | 0 | 8.7 | 1010 | -60 | 2.767 | 29.2 | 50.4 | 288 | -60.1 | 2.821 | 28.7 | 50.9 | 291 | OK- No Action Required | 99 | 99 | 8.7 | 54.5 | 36.8 | 0 | >>>>
BGW2P334 | 2019-03-21 14:00 | 42.9 | 34.7 | 0 | 22.4 | 1010 | -1.8 | 1.826 | 34.5 | 5.7 | 26 | -1.9 | 1.854 | 33.1 | 5.8 | 26 | OK- No Action Required | 10 | 10 | 22.4 | 42.9 | 34.8 | 0 | >>>>
BGW2P333 | 2019-03-21 14:01 | 48 | 31.9 | 3.1 | 17 | 1010 | -0.1 | 0.011 | 27.8 | 0.2 | 1 | -0.1 | 0.008 | 27.3 | 0.2 | 1 | OK- No Action Required | 5 | 5 | 5.28 | 48 | 31.8 | 3.1 | >>>>
BGW2P283 | 2019-03-21 14:03 | 44.8 | 35.2 | 0.7 | 19.3 | 1010 | -24.7 | 4.823 | 25.3 | 41 | 192 | -34.4 | 5.136 | 23.7 | 42.3 | 198 | Surge | 45 | 40 | 16.65 | 44.8 | 35.2 | 0.7 | >>>>
BGW2P477 | 2019-03-21 14:04 | 48.9 | 37.3 | 0 | 13.8 | 1010 | -3.9 | 3.491 | 37.3 | 34.7 | 178 | -3.8 | 3.363 | 35.9 | 34.1 | 175 | OK- No Action Required | 40 | 40 | 13.8 | 48.9 | 37.2 | 0 | >>>>
BGW2P269 | 2019-03-21 14:06 | 43.7 | 33.8 | 0.2 | 22.3 | 1010 | -28.4 | 16.38 | 35.1 | 34.5 | 158 | -24.2 | 18.998 | 34.9 | 37.3 | 170 | Surge | 42 | 40 | 21.54 | 43.7 | 33.7 | 0.2 | >>>>
BGW2P280 | 2019-03-21 14:07 | 49.1 | 34.7 | 1.4 | 14.8 | 1010 | -0.4 | 0.714 | 35.7 | 15.8 | 81 | -0.5 | 0.874 | 35.2 | 17.6 | 90 | Adjusted Decrease |  | 37 | 9.51 | 49.1 | 34.7 | 1.4 | >>>>
BGW2P288 | 2019-03-21 14:09 | 35.1 | 27.8 | 3.7 | 33.4 | 1010 | -1.1 | 5.293 | 37.2 | 9.8 | 36 | -4.9 | 6.231 | 36.1 | 10.6 | 39 | Surge | 40 | 37 | 19.41 | 45.3 | 34.9 | 1.7 | >>>>
BGW2Z328 | 2019-03-21 14:36 | 49.6 | 37.4 | 0 | 13 | 1009 | -18.6 | 17.933 | 40.9 | 36.1 | 187 | -18.5 | 18.252 | 40.8 | 36.4 | 189 | OK- No Action Required | 40 | 40 | 13 | 49.6 | 37.4 | 0 | >>>>
BGW2Z479 | 2019-03-21 14:37 | 47.5 | 35.4 | 0 | 17.1 | 1009 | -1.9 | 7.009 | 32 | 23.1 | 115 | -2.2 | 6.897 | 32 | 22.9 | 114 | OK- No Action Required | 25 | 25 | 17.1 | 47.5 | 35.4 | 0 | >>>>
BGW2Z313 | 2019-03-21 14:38 | 50.1 | 34.7 | 0 | 15.2 | 1009 | -23.1 | 6.866 | 32.9 | 49.1 | 257 | -23.6 | 6.991 | 31.7 | 49.6 | 260 | OK- No Action Required | 40 | 40 | 15.2 | 50.1 | 34.7 | 0 | >>>>
BGW2Z320 | 2019-03-21 14:39 | 60.5 | 37.4 | 0 | 2.1 | 1009 | -52.5 | 0.369 | 34.1 | 5.2 | 33 | -51.6 | 0.452 | 33 | 5.8 | 37 | Blocked-Investigation Required | 99 | 99 | 2.1 | 60.5 | 37.4 | 0 | >>>>
BGW2Z324 | 2019-03-21 14:40 | 4.5 | 14.6 | 7.7 | 73.2 | 1009 | 0.1 | -0.055 | 30.2 | N/A | N/A | 0.1 | -0.059 | 31.2 | N/A | N/A | Shut/Shut | 0 | 0 | 44.09 | 30.8 | 14.6 | 5.4 | 90
BGW2Z327 | 2019-03-21 14:41 | 0.5 | 1.6 | 19.2 | 78.7 | 1009 | -10.9 | -0.072 | 30.7 | N/A | N/A | -10.9 | -0.089 | 27.8 | N/A | N/A | Shut/Shut | 0 | 0 | 6.12 | 4.3 | 15.7 | 7.2 | 10
BGW2Z321 | 2019-03-21 14:42 | 49 | 37.1 | 0 | 13.9 | 1009 | -31.3 | 12.911 | 46.2 | 65 | 334 | -30.8 | 12.993 | 45.3 | 65.3 | 335 | OK- No Action Required | 60 | 60 | 13.9 | 49 | 37.1 | 0 | >>>>
BGW2Z314 | 2019-03-21 14:43 | 46 | 35.5 | 0 | 18.5 | 1009 | -1.9 | 9.556 | 43.1 | 26.4 | 127 | -1.7 | 9.491 | 42.9 | 26.3 | 127 | OK- No Action Required | 30 | 30 | 18.5 | 46 | 35.5 | 0 | >>>>
BGW2Z310 | 2019-03-21 14:44 | 50.1 | 34.8 | 0 | 15.1 | 1009 | -10.3 | 16.474 | 40 | 75.6 | 397 | -11.4 | 16.401 | 39.6 | 75.5 | 396 | OK- No Action Required | 50 | 50 | 15.1 | 50.1 | 34.8 | 0 | >>>>
BGW2Z306 | 2019-03-21 14:46 | 44.7 | 33.8 | 0.1 | 21.4 | 1009 | -5.2 | 5.125 | 38.7 | 19.4 | 91 | -6.2 | 6.831 | 38.5 | 22.5 | 105 | Adjusted Decrease | 35 | 32 | 21.02 | 47.3 | 34.9 | 0.1 | >>>>
BGW2Z317 | 2019-03-21 14:47 | 45.7 | 29.8 | 4.3 | 20.2 | 1009 | -44.4 | -0.098 | 31.5 | N/A | N/A | -44.2 | -0.133 | 31.6 | N/A | N/A | Blocked-Investigation Required | 40 | 40 | 3.95 | 45.7 | 29.8 | 1.1 | >>>>
BGW2Y271 | 2019-03-21 14:51 | 13.4 | 20.1 | 5.4 | 61.1 | 1009 | -2.8 | 0.03 | 26.5 | 1.4 | 2 | -2.7 | 0.038 | 25.2 | 1.6 | 2 | Shut/Shut | 0 | 0 | 40.69 | 13.4 | 20.1 | 5.4 | >>>>
BGW2Y329 | 2019-03-21 14:53 | 54.8 | 39.9 | 0 | 5.3 | 1008 | -31.1 | 23.764 | 37.9 | 146.7 | 842 | -34.4 | 26.461 | 30 | 156.5 | 898 | OK- No Action Required | 99 | 99 | 5.3 | 54.8 | 39.9 | 0 | >>>>
BGW2Y322 | 2019-03-21 14:57 | 2.1 | 4.1 | 18 | 75.8 | 1008 | 0 | -0.013 | 30.8 | N/A | N/A | 0 | -0.011 | 30.4 | N/A | N/A | Shut/Shut | 0 | 0 | 7.76 | 1.6 | 2.8 | 18.8 | 42
BGW2Y318 | 2019-03-21 14:59 | 0.4 | 0.6 | 20.4 | 78.6 | 1008 | -0.4 | -0.058 | 26.8 | N/A | N/A | -0.4 | -0.048 | 30.5 | N/A | N/A | Shut/Shut | 0 | 0 | 1.49 | 0.4 | 0.6 | 20.4 | 8
BGW2Y311 | 2019-03-21 15:00 | 58.1 | 38.8 | 0 | 3.1 | 1008 | -10 | 3.77 | 45.3 | 16.7 | 102 | -6.2 | 2.366 | 44.6 | 13.3 | 81 | Adjusted Increase | 25 | 27 | 3.1 | 58.1 | 38.7 | 0 | >>>>
BGW2Y315 | 2019-03-21 15:01 | 57.8 | 40.2 | 0 | 2 | 1008 | -48.6 | 10.896 | 45.3 | 97.8 | 592 | -46.8 | 11.976 | 45 | 102.7 | 622 | OK- No Action Required | 99 | 99 | 2 | 57.8 | 40.2 | 0 | >>>>
BGW2Y483 | 2019-03-21 15:03 | 16.3 | 16.5 | 9.4 | 57.8 | 1008 | 0 | -0.032 | 31.7 | N/A | N/A | 0 | -0.033 | 32.8 | N/A | N/A | Shut/Shut | 0 | 0 | 22.27 | 23 | 16.5 | 9.4 | >>>>
BGW2Y478 | 2019-03-21 15:04 | 48.4 | 37.5 | 0 | 14.1 | 1008 | -1.2 | 0.615 | 30.4 | 6.8 | 34 | -0.7 | 0.544 | 30.1 | 6.4 | 32 | OK- No Action Required | 10 | 10 | 14.1 | 48.4 | 37.5 | 0 | >>>>
BGW2Y481 | 2019-03-21 15:05 | 23.4 | 24 | 4.1 | 48.5 | 1008 | -103.2 | -0.024 | 26.4 | N/A | N/A | 0 | -0.022 | 26.9 | N/A | N/A | Shut/Shut | 0 | 0 | 33 | 23.4 | 24 | 4.2 | >>>>
BGW2Y480 | 2019-03-21 15:06 | 50.8 | 38.9 | 0 | 10.3 | 1008 | -0.7 | 4.257 | 35 | 17.8 | 95 | -0.8 | 4.283 | 31 | 18 | 96 | OK- No Action Required | 25 | 25 | 10.3 | 50.8 | 38.9 | 0 | >>>>
BGW2Y482 | 2019-03-21 15:07 | 54.4 | 38.4 | 0 | 7.2 | 1008 | -0.5 | 3.657 | 33.3 | 16.7 | 95 | -0.3 | 3.545 | 32.7 | 16.5 | 94 | OK- No Action Required | 20 | 20 | 7.2 | 54.4 | 38.4 | 0 | >>>>

## Header Reads
Paste readings below and ensure that "Security Code" is in Cell A2 | [18 empty] | ID
Security code | [6B8338B3]
ID | DATE | CH4 | CO2 | O2 | BALANCE | BARO | CO | H2S | H2 | ADJ-SP | ADJ-DP | ADJ-TEMP | ADJ-FLOW | ADJ-POWER | INI-SP | INI-DP | INI-TEMP | INI-FLOW | INI-POWER | CHOSEN 1 | ANSWER 1 | ANSWER 2 | CH4/CO2 | Res Nitrogen
|  | % | % | % | % | mb | ppm | ppm | ppm | mb | mb | DegC | m3/h | kW | mb | mb | DegC | m3/h | kW |  |  |  | % | %
BGW2Z340 | 2018-10-25 10:46 | 44.8 | 33.9 | 0.7 | 20.6 | 1011 | 22 | 53 | LOW | [5 empty] | -0.6 | 4.557 | 34.3 | 18.5 | 87 | OK- No Action Required | 20 | 20 | 1.32 | 17.95
BGW2Z341 | 2018-10-25 10:52 | 44.9 | 32.6 | 1.4 | 21.1 | 1011 | 19 | 50 | LOW | [5 empty] | 0.1 | 0.882 | 34 | 8.1 | 38 | OK- No Action Required | 20 | 20 | 1.38 | 15.81
BGW2Z342 | 2018-10-25 10:57 | 30.9 | 24.4 | 5.2 | 39.5 | 1011 | 27 | 9 | LOW | [5 empty] | 0 | 0.419 | 29.1 | 5.6 | 18 | OK- No Action Required | 10 | 10 | 1.27 | 19.84
BGW2Z343 | 2018-10-25 11:02 | 49.9 | 35.7 | 0 | 14.4 | 1011 | 66 | 46 | LOW | [5 empty] | -1.6 | 8.657 | 33.2 | 25.7 | 134 | OK- No Action Required | 30 | 30 | 1.4 | 14.4
BGW2Z344 | 2018-10-25 11:06 | 55.5 | 37.2 | 0.1 | 7.2 | 1011 | 77 | 10 | LOW | [5 empty] | -0.3 | 1.334 | 29.5 | 10.2 | 59 | OK- No Action Required | 10 | 10 | 1.49 | 6.82
BGW2Z345 | 2018-10-25 11:10 | 49 | 35.8 | 0 | 15.2 | 1011 | 70 | 36 | LOW | [5 empty] | -0.3 | 1.526 | 33.1 | 10.8 | 55 | OK- No Action Required | 15 | 15 | 1.37 | 15.2
BGW2Z346 | 2018-10-25 11:15 | 52.6 | 37.1 | 0 | 10.3 | 1011 | 66 | 144 | LOW | [5 empty] | -5.9 | 5.074 | 32.9 | 19.7 | 108 | OK- No Action Required | 20 | 20 | 1.42 | 10.3
BGW2Z346 | 2018-10-25 11:18 | 52.4 | 36.8 | 0 | 10.8 | 1011 | 63 | 121 | LOW | [5 empty] | -6.6 | 4.797 | 33.3 | 19.1 | 105 | OK- No Action Required | 20 | 20 | 1.42 | 10.8
BGW2Z328 | 2018-10-25 11:38 | 50.9 | 37.8 | 0.1 | 11.2 | 1009 | 100 | 70 | LOW | [5 empty] | -21.3 | 17.419 | 42.3 | 35.5 | 189 | OK- No Action Required | 40 | 40 | 1.35 | 10.82
BGW2Z479 | 2018-10-25 11:40 | 50.2 | 36.3 | 0.2 | 13.3 | 1009 | 95 | 45 | LOW | [5 empty] | -3 | 14.177 | 28.5 | 33.1 | 174 | OK- No Action Required | 30 | 30 | 1.38 | 12.54
BGW2Z313 | 2018-10-25 11:43 | 50.9 | 35.4 | 0 | 13.7 | 1009 | 107 | 133 | LOW | [5 empty] | -24.8 | 7.375 | 34.2 | 50.7 | 270 | OK- No Action Required | 40 | 40 | 1.44 | 13.7
BGW2Z320 | 2018-10-25 11:46 | 61.6 | 38.6 | 0 | 0 | 1009 | 88 | 173 | LOW | [5 empty] | -57.2 | 3.353 | 31.8 | 15.8 | 102 | OK- No Action Required | 99 | 99 | 1.6 | 0
BGW2Z324 | 2018-10-25 11:49 | 4 | 20.8 | 0 | 75.2 | 1009 | 87 | 32 | LOW | [5 empty] | -0.1 | 0.058 | 36.6 | 1.9 | 0 | Shut/Shut | 0 | 0 | 0.19 | 75.2
BGW2Z327 | 2018-10-25 11:52 | 14.7 | 24.3 | 0 | 61 | 1009 | 81 | 47 | LOW | [5 empty] | -30.5 | 0.013 | 36.7 | 2 | 3 | OK- No Action Required | 99 | 5 | 0.6 | 61
BGW2Z321 | 2018-10-25 11:57 | 47.7 | 36.9 | 0 | 15.4 | 1009 | 87 | 53 | LOW | [5 empty] | -39.9 | 27.663 | 45.3 | 94.7 | 473 | OK- No Action Required | 99 | 50 | 1.29 | 15.4
BGW2Z314 | 2018-10-25 12:01 | 44.5 | 35 | 0 | 20.5 | 1009 | 103 | 38 | LOW | [5 empty] | -1.9 | 10.974 | 41.4 | 28.3 | 132 | OK- No Action Required | 30 | 30 | 1.27 | 20.5
BGW2Z310 | 2018-10-25 12:04 | 50.4 | 35.4 | 0 | 14.2 | 1009 | 111 | 30 | LOW | [5 empty] | -10.8 | 19.607 | 37.2 | 82.7 | 437 | OK- No Action Required | 50 | 50 | 1.42 | 14.2
BGW2Z306 | 2018-10-25 12:07 | 43.6 | 33.5 | 0 | 22.9 | 1009 | 127 | 39 | LOW | [5 empty] | -11.3 | 17.168 | 35.4 | 35.7 | 163 | OK- No Action Required | 3 | 20 | 1.3 | 22.9
BGW2Z306 | 2018-10-25 12:08 | 43.6 | 33.5 | 0 | 22.9 | 1009 | 127 | 39 | LOW | [5 empty] | -11.3 | 17.168 | 35.4 | 35.7 | 163 | OK- No Action Required | 30 | 20 | 1.3 | 22.9
BGW2Z317 | 2018-10-25 12:12 | 57.8 | 37.3 | 0.8 | 4.1 | 1009 | 115 | 74 | LOW | [5 empty] | -10.1 | 0.365 | 27 | 11.6 | 70 | OK- No Action Required | 20 | 25 | 1.55 | 1.08
BGW2Y271 | 2018-10-25 13:10 | 36.7 | 33.8 | 1 | 28.5 | 1007 | 81 | 7 | LOW | [5 empty] | -0.2 | 0.033 | 23.8 | 1.5 | 6 | OK- No Action Required | 5 | 5 | 1.09 | 24.72
BGW2Y329 | 2018-10-25 13:13 | 55.5 | 40.9 | 0 | 3.6 | 1007 | 78 | 29 | LOW | [5 empty] | -39.9 | 29.111 | 44 | 159.9 | 930 | OK- No Action Required | 99 | 99 | 1.36 | 3.6
BGW2Y322 | 2018-10-25 13:19 | 53.5 | 39.6 | 0.4 | 6.5 | 1007 | 119 | 28 | LOW | [5 empty] | -12.6 | 0.99 | 37.8 | 18.4 | 103 | OK- No Action Required | 20 | 20 | 1.35 | 4.99
BGW2Y322 | 2018-10-25 13:23 | 60.5 | 40.8 | 0 | 0 | 1007 | 86 | 82 | LOW | [5 empty] | -38.1 | 0.041 | 26.4 | 3.8 | 24 | OK- No Action Required | 5 | 15 | 1.48 | 0
BGW2Y318 | 2018-10-25 13:27 | 38.4 | 26.4 | 7.1 | 28.1 | 1007 | 82 | 16 | LOW | [5 empty] | -2.2 | 0.003 | 24 | 1.8 | 7 | OK- No Action Required | 5 | 5 | 1.45 | 1.26
BGW2Y311 | 2018-10-25 13:31 | 56 | 38.4 | 0 | 5.6 | 1007 | 93 | 41 | LOW | [5 empty] | -7.5 | 1.991 | 43.3 | 12.1 | 71 | OK- No Action Required | 10 | 20 | 1.46 | 5.6
BGW2Y315 | 2018-10-25 13:34 | 56.5 | 40.6 | 0 | 2.9 | 1007 | 92 | 29 | LOW | [5 empty] | -41.1 | 25.186 | 46.1 | 148.5 | 880 | OK- No Action Required | 99 | 99 | 1.39 | 2.9
BGW2Y483 | 2018-10-25 13:38 | 7 | 6.9 | 16 | 70.1 | 1007 | 65 | 2 | LOW | [5 empty] | -0.1 | 0.038 | 23.3 | 0 | 0 | Shut/Shut | 0 | 0 | 1.01 | 9.62
BGW2Y478 | 2018-10-25 13:41 | 50.4 | 38.7 | 0 | 10.9 | 1007 | 90 | 36 | LOW | [5 empty] | -0.8 | 0.243 | 22.6 | 4.3 | 23 | OK- No Action Required | 10 | 10 | 1.3 | 10.9
BGW2Y481 | 2018-10-25 13:44 | 20.2 | 29.6 | 0.1 | 50.1 | 1007 | 89 | 4 | LOW | [5 empty] | -0.3 | 0.018 | 24.9 | 1.1 | 2 | Shut/Shut | 0 | 0 | 0.68 | 49.72
BGW2Y480 | 2018-10-25 13:47 | 51.7 | 39.9 | 0 | 8.4 | 1007 | 93 | 92 | LOW | [5 empty] | -1.4 | 5.262 | 29.6 | 20 | 108 | OK- No Action Required | 15 | 15 | 1.3 | 8.4
BGW2Y482 | 2018-10-25 13:49 | 47.6 | 37.7 | 0 | 14.7 | 1007 | 91 | 39 | LOW | [5 empty] | -0.4 | 3.84 | 28.2 | 17.1 | 85 | OK- No Action Required | 15 | 15 | 1.26 | 14.7
BGW2P295 | 2018-10-25 14:02 | 50.6 | 36.9 | 0 | 12.5 | 1008 | 77 | 27 | LOW | [5 empty] | -29.9 | 9.853 | 31.7 | 95.4 | 506 | OK- No Action Required | 60 | 60 | 1.37 | 12.5
BGW2P291 | 2018-10-25 14:03 | 54.6 | 39.1 | 0 | 6.3 | 1008 | 76 | 158 | LOW | [5 empty] | -0.2 | 2.573 | 35.1 | 14 | 80 | OK- No Action Required | 25 | 25 | 1.4 | 6.3
BGW2P293 | 2018-10-25 14:06 | 57.3 | 38 | 0.8 | 3.9 | 1008 | 76 | 63 | LOW | [5 empty] | 0 | 0.495 | 25.7 | 13.5 | 81 | OK- No Action Required | 25 | 25 | 1.51 | 0.88
BGW2P290 | 2018-10-25 14:08 | 52.1 | 36.7 | 0.1 | 11.1 | 1007 | 71 | 53 | LOW | [5 empty] | -4.1 | 7.594 | 27.4 | 24.3 | 133 | OK- No Action Required | 25 | 25 | 1.42 | 10.72
BGW2P447 | 2018-10-25 14:15 | 59.1 | 36.7 | 0.1 | 4.1 | 1008 | 65 | 57 | LOW | [5 empty] | -2.1 | 11.848 | 23.2 | 1.7 | 10 | OK- No Action Required | 10 | 10 | 1.61 | 3.72
BGW2P286 | 2018-10-25 14:17 | 61 | 39.2 | 0 | 0 | 1007 | 59 | 48 | LOW | [5 empty] | -61 | 1.604 | 24 | 39 | 249 | OK- No Action Required | 99 | 99 | 1.56 | 0
BGW2P334 | 2018-10-25 14:20 | 46.5 | 36.2 | 0 | 17.3 | 1007 | 71 | 64 | LOW | [5 empty] | -1.3 | 1.595 | 28.7 | 5.4 | 26 | OK- No Action Required | 10 | 10 | 1.28 | 17.3
BGW2P333 | 2018-10-25 14:23 | 60.2 | 39.2 | 0 | 0.6 | 1007 | 68 | 19 | LOW | [5 empty] | 0.2 | 2.976 | 23.8 | 3.9 | 24 | OK- No Action Required | 5 | 10 | 1.54 | 0.6
BGW2P283 | 2018-10-25 14:26 | 45.5 | 35.8 | 0.5 | 18.2 | 1007 | 66 | 14 | LOW | [5 empty] | -36.9 | 6.561 | 36.6 | 46.7 | 222 | OK- No Action Required | 50 | 50 | 1.27 | 16.31
BGW2P477 | 2018-10-25 14:28 | 49.7 | 37.8 | 0 | 12.5 | 1007 | 69 | 18 | LOW | [5 empty] | -3.6 | 2.968 | 32.9 | 32.2 | 168 | OK- No Action Required | 30 | 30 | 1.31 | 12.5
BGW2P269 | 2018-10-25 14:30 | 53.9 | 36.8 | 0.1 | 9.2 | 1007 | 68 | 20 | LOW | [5 empty] | -51 | 4.654 | 31.1 | 18.5 | 105 | OK- No Action Required | 40 | 40 | 1.46 | 8.82
BGW2P280 | 2018-10-25 14:33 | 47.7 | 33.5 | 2.2 | 16.6 | 1007 | 70 | 11 | LOW | [5 empty] | -2.3 | 5.371 | 33.7 | 43.6 | 218 | OK- No Action Required | 30 | 30 | 1.42 | 8.28
BGW2P288 | 2018-10-25 14:35 | 53.5 | 37.7 | 0.9 | 7.9 | 1007 | 80 | 17 | LOW | [5 empty] | 0 | 2.048 | 29.7 | 6.2 | 35 | OK- No Action Required | 15 | 15 | 1.42 | 4.5
BGW2R207 | 2018-10-25 14:47 | 58.8 | 42.3 | 0 | 0 | 1007 | 109 | 37 | LOW | [5 empty] | -0.1 | 4.161 | 30.3 | 4.5 | 27 | OK- No Action Required | 200 | 20 | 1.39 | 0
BGW2R207 | 2018-10-25 14:47 | 58.8 | 42.3 | 0 | 0 | 1007 | 109 | 37 | LOW | [5 empty] | -0.1 | 4.161 | 30.3 | 4.5 | 27 | OK- No Action Required | 20 | 20 | 1.39 | 0
BGW2R208 | 2018-10-25 14:51 | 47.6 | 34.5 | 2 | 15.9 | 1007 | 130 | 18 | LOW | [5 empty] | -0.1 | 7.575 | 22.4 | 6.1 | 30 | OK- No Action Required | 5 | 5 | 1.38 | 8.34
BGW2R384 | 2018-10-25 14:54 | 50.7 | 36.7 | 0.6 | 12 | 1007 | 96 | 36 | LOW | [5 empty] | -2.1 | 1.304 | 26.7 | 21.7 | 115 | OK- No Action Required | 15 | 15 | 1.38 | 9.73
BGW2R202 | 2018-10-25 14:56 | 47.7 | 36.6 | 0 | 15.7 | 1007 | 102 | 19 | LOW | [5 empty] | -59.7 | 0.763 | 32.2 | 15.9 | 79 | OK- No Action Required | 40 | 40 | 1.3 | 15.7
BGW2R436 | 2018-10-25 14:58 | 48.1 | 35.6 | 0.3 | 16 | 1007 | 97 | 13 | LOW | [5 empty] | -6.6 | 5.726 | 28.7 | 45.2 | 227 | OK- No Action Required | 20 | 20 | 1.35 | 14.87
BGW2R192 | 2018-10-25 15:00 | 53.1 | 38.7 | 0.6 | 7.6 | 1007 | 109 | 38 | LOW | [5 empty] | -0.2 | 8.139 | 27.3 | 12.4 | 69 | OK- No Action Required | 15 | 15 | 1.37 | 5.33
BGW2R197 | 2018-10-25 15:03 | 45.6 | 36.3 | 0 | 18.1 | 1007 | 100 | 21 | LOW | [5 empty] | -4.1 | 3.276 | 35.3 | 33.6 | 160 | OK- No Action Required | 20 | 20 | 1.26 | 18.1
BGW2R201 | 2018-10-25 15:05 | 49.1 | 38.2 | 0.1 | 12.6 | 1006 | 99 | 36 | LOW | [5 empty] | -2.2 | 1.702 | 38.4 | 24.1 | 124 | OK- No Action Required | 10 | 10 | 1.29 | 12.22
BGW2R437 | 2018-10-25 15:09 | 32.2 | 23.4 | 9.4 | 35 | 1006 | 91 | 50 | LOW | [5 empty] | -2.1 | 1.006 | 23.1 | 2.2 | 7 | OK- No Action Required | 5 | 2 | 1.38 | 0
BGW2R277 | 2018-10-25 15:12 | 5.2 | 6.1 | 16.3 | 72.4 | 1007 | 70 | 6 | LOW | [5 empty] | -5 | 0.017 | 22.4 | 0 | 0 | Shut/Shut | 0 | 0 | 0.85 | 10.79
BHW2R410 | 2018-10-25 15:15 | 45.9 | 37.2 | 0.1 | 16.8 | 1007 | 103 | 9 | LOW | [5 empty] | -40.5 | 31.206 | 44.6 | 163.6 | 787 | OK- No Action Required | 99 | 99 | 1.23 | 16.42
BHW2R410 | 2018-10-25 15:16 | 45.9 | 37.2 | 0.1 | 16.8 | 1007 | 103 | 9 | LOW | [5 empty] | -40.5 | 31.206 | 44.6 | 163.6 | 787 | OK- No Action Required | 99 | 70 | 1.23 | 16.42
BHW2R409 | 2018-10-25 15:20 | 25.6 | 20.9 | 8.2 | 45.3 | 1007 | 90 | 2 | LOW | [5 empty] | -0.5 | -0.016 | 33.6 | N/A | N/A | Shut/Shut | 0 | 0 | 1.22 | 14.3
BGW2S222 | 2018-10-25 15:27 | 57.6 | 42.4 | 0 | 0 | 1006 | 112 | 78 | LOW | [5 empty] | -0.2 | 0.464 | 42.8 | 5.8 | 35 | OK- No Action Required | 30 | 30 | 1.36 | 0
BGW2S223 | 2018-10-25 15:31 | 45.6 | 36.1 | 0 | 18.3 | 1006 | 119 | 21 | LOW | [5 empty] | -60.1 | 3.31 | 39.9 | 53.3 | 254 | OK- No Action Required | 99 | 99 | 1.26 | 18.3
BGW2S217 | 2018-10-25 15:34 | 47.8 | 36.4 | 0.5 | 15.3 | 1006 | 116 | 17 | LOW | [5 empty] | -23 | 4.727 | 43 | 39.6 | 198 | OK- No Action Required | 25 | 25 | 1.31 | 13.41
BGW2S212 | 2018-10-25 15:36 | 0.3 | 3.5 | 16.6 | 79.6 | 1006 | 93 | 5 | LOW | [5 empty] | -2.6 | -0.006 | 25.8 | N/A | N/A | Shut/Shut | 0 | 0 | 0.09 | 16.85
BGW2S211 | 2018-10-25 15:37 | 60.3 | 42.5 | 0 | 0 | 1006 | 104 | 38 | LOW | [5 empty] | -62.6 | 0.928 | 26.5 | 8.2 | 52 | OK- No Action Required | 99 | 99 | 1.42 | 0
BGW2S385 | 2018-10-25 15:40 | 50.4 | 37.8 | 0 | 11.8 | 1006 | 100 | 19 | LOW | [5 empty] | -23 | 10.408 | 31 | 60.1 | 317 | OK- No Action Required | 50 | 50 | 1.33 | 11.8
BGW2S281 | 2018-10-25 15:42 | 51.5 | 37 | 2.5 | 9 | 1006 | 98 | 9 | LOW | [5 empty] | -64 | 0.013 | 21.5 | 0.9 | 5 | OK- No Action Required | 99 | 99 | 1.39 | 0
BHW2S411 | 2018-10-25 15:44 | 59.3 | 43.1 | 0 | 0 | 1006 | 101 | 10 | LOW | [5 empty] | -60.1 | 2.231 | 35.1 | 12.6 | 78 | OK- No Action Required | 99 | 99 | 1.38 | 0
BGW2S206 | 2018-10-25 15:47 | 38.8 | 33.7 | 2.2 | 25.3 | 1006 | 106 | 3 | LOW | [5 empty] | -0.3 | 0.032 | 22.6 | 0.3 | 1 | OK- No Action Required | 5 | 5 | 1.15 | 16.98
BGW2S216 | 2018-10-25 15:49 | 59.4 | 42.9 | 0 | 0 | 1006 | 101 | 11 | LOW | [5 empty] | -63.6 | 0.219 | 35 | 13.9 | 86 | OK- No Action Required | 99 | 99 | 1.38 | 0
BGW2Q209 | 2018-10-26 08:38 | 27.2 | 19.7 | 9.2 | 43.9 | 1012 | 16 | 17 | LOW | [5 empty] | -52.8 | 0.068 | 18.2 | 4.8 | 13 | Surge | 10 | 10 | 1.38 | 9.12
BGW2Q185 | 2018-10-26 08:41 | 56.3 | 33.7 | 0 | 10 | 1012 | 20 | 14 | LOW | [5 empty] | -18.8 | 2.739 | 16.6 | 3.7 | 22 | OK- No Action Required | 5 | 5 | 1.67 | 10
BGW2Q180 | 2018-10-26 08:44 | 19.4 | 11.3 | 12.6 | 56.7 | 1012 | 17 | 2 | LOW | [5 empty] | 0 | 0.028 | 14.9 | 0.7 | 1 | Shut/Shut | 2 | 2 | 1.72 | 9.07
BGW2Q190 | 2018-10-26 08:46 | 50 | 33.4 | 0.1 | 16.5 | 1012 | 18 | 9 | LOW | [5 empty] | -6.7 | 1.199 | 21 | 21.1 | 110 | OK- No Action Required | 20 | 20 | 1.5 | 16.12
BGW2Q199 | 2018-10-26 08:49 | 45.6 | 34.5 | 0.1 | 19.8 | 1012 | 19 | 6 | LOW | [5 empty] | -35.7 | 1.009 | 20.6 | 8.7 | 41 | OK- No Action Required | 25 | 25 | 1.32 | 19.42
BGW2Q175 | 2018-10-26 08:51 | 20.7 | 24.4 | 0.8 | 54.1 | 1012 | 14 | 1 | LOW | [5 empty] | -0.2 | 0.156 | 15.4 | 0.1 | 0 | OK- No Action Required | 2 | 2 | 0.85 | 51.08
BGW2Q179 | 2018-10-26 08:54 | 41.2 | 29.5 | 0 | 29.3 | 1012 | 16 | 1 | LOW | [5 empty] | -0.5 | 0.015 | 14.5 | 0.5 | 2 | OK- No Action Required | 5 | 5 | 1.4 | 29.3
BGW2Q335 | 2018-10-26 08:56 | 50.3 | 37.5 | 0 | 12.2 | 1012 | 18 | 12 | LOW | [5 empty] | -4.6 | 4.242 | 20.9 | 39.4 | 208 | OK- No Action Required | 30 | 30 | 1.34 | 12.2
BGW2Q336 | 2018-10-26 08:59 | 51.2 | 36.4 | 1.6 | 10.8 | 1012 | 23 | 42 | LOW | [5 empty] | -0.1 | 0.065 | 16.9 | 2.3 | 12 | OK- No Action Required | 5 | 5 | 1.41 | 4.75
BGW2Q204 | 2018-10-26 09:01 | 32.5 | 30 | 2.3 | 35.2 | 1012 | 33 | 4 | LOW | [5 empty] | -5.3 | 0.037 | 15.1 | 1.7 | 5 | OK- No Action Required | 5 | 5 | 1.08 | 26.51
BGW2Q214 | 2018-10-26 09:03 | 46 | 34.3 | 0 | 19.7 | 1012 | 23 | 16 | LOW | [5 empty] | -9.2 | 0.907 | 24.9 | 18 | 87 | OK- No Action Required | 25 | 25 | 1.34 | 19.7
BGW2Q203 | 2018-10-26 09:05 | 60.6 | 41.6 | 0 | 0 | 1012 | 28 | 15 | LOW | [5 empty] | -50.4 | 8.239 | 37.2 | 52.8 | 335 | OK- No Action Required | 99 | 99 | 1.46 | 0
BGW2Q382 | 2018-10-26 09:08 | 54.6 | 38.9 | 0.3 | 6.2 | 1012 | 31 | 27 | LOW | [5 empty] | -2.6 | 6.091 | 23.3 | 21.9 | 125 | OK- No Action Required | 35 | 35 | 1.4 | 5.07
BGW2Q184 | 2018-10-26 09:11 | 50.3 | 36.9 | 1.2 | 11.6 | 1012 | 65 | 15 | LOW | [5 empty] | -1.3 | 0.551 | 21.5 | 23.2 | 122 | OK- No Action Required | 25 | 25 | 1.36 | 7.06
BGW2Q189 | 2018-10-26 09:13 | 0.1 | 0.8 | 20.5 | 78.6 | 1012 | 19 | 2 | LOW | [5 empty] | 0 | 0.022 | 16 | 0 | 0 | Shut/Shut | 0 | 0 | 0.13 | 1.11
BGW2Q338 | 2018-10-26 09:17 | 18.5 | 18.9 | 6.7 | 55.9 | 1012 | 20 | 1 | LOW | [5 empty] | -19.8 | -0.38 | 18.3 | N/A | N/A | OK- No Action Required | 10 | 2 | 0.98 | 30.57
BGW2Q337 | 2018-10-26 09:20 | 46.7 | 36.2 | 1.5 | 15.6 | 1012 | 33 | 16 | LOW | [5 empty] | -0.1 | 2.843 | 18.5 | 3.7 | 18 | OK- No Action Required | 5 | 5 | 1.29 | 9.93
BGW2Q444 | 2018-10-26 09:26 | 48.7 | 34.7 | 0.5 | 16.1 | 1012 | 32 | 33 | LOW | [5 empty] | -3.1 | 0.809 | 20.3 | 8 | 41 | OK- No Action Required | 5 | 5 | 1.4 | 14.21
BGW2Q444 | 2018-10-26 09:27 | 48.7 | 34.7 | 0.5 | 16.1 | 1012 | 32 | 33 | LOW | [5 empty] | -3.1 | 0.809 | 20.3 | 8 | 41 | OK- No Action Required | 5 | 5 | 1.4 | 14.21
BGW2Q168 | 2018-10-26 09:30 | 54.8 | 37.4 | 0 | 7.8 | 1011 | 33 | 26 | LOW | [5 empty] | -67.4 | 1.247 | 18.9 | 20.9 | 120 | OK- No Action Required | 99 | 99 | 1.47 | 7.8
BGW2T234 | 2018-10-26 09:41 | 55 | 40.6 | 0 | 4.4 | 1011 | 47 | 18 | LOW | [5 empty] | -1.8 | 0.647 | 26.6 | 7 | 40 | OK- No Action Required | 25 | 25 | 1.35 | 4.4
BLW2X468 | 2018-10-26 09:44 | 54.7 | 38.3 | 0.5 | 6.5 | 1011 | 42 | 33 | LOW | [5 empty] | -10.8 | 4.889 | 25.3 | 19.5 | 112 | OK- No Action Required | 25 | 25 | 1.43 | 4.61
BGW2T235 | 2018-10-26 09:46 | 23.3 | 14.8 | 11.4 | 50.5 | 1011 | 43 | 2 | LOW | [5 empty] | 0.6 | 0.261 | 21.6 | 2.2 | 5 | OK- No Action Required | 2 | 2 | 1.57 | 7.41
BGW2T230 | 2018-10-26 09:49 | 48.4 | 33.9 | 0 | 17.7 | 1011 | 37 | 8 | LOW | [5 empty] | -0.3 | 1.525 | 21.3 | 11 | 56 | OK- No Action Required | 10 | 10 | 1.43 | 17.7
BGW2T229 | 2018-10-26 09:54 | 0.1 | 0.1 | 20.3 | 79.5 | 1011 | 30 | 1 | LOW | [5 empty] | -0.2 | 0.039 | 22 | 1.7 | 0 | Shut/Shut | 0 | 0 | 1 | 2.77
BGW2T438 | 2018-10-26 09:56 | 47.4 | 36.5 | 0 | 16.1 | 1011 | 52 | 6 | LOW | [5 empty] | -1.5 | 1.335 | 22.9 | 5 | 25 | OK- No Action Required | 10 | 10 | 1.3 | 16.1
BGW2T339 | 2018-10-26 09:58 | 45.9 | 35.9 | 0 | 18.2 | 1011 | 47 | 13 | LOW | [5 empty] | -4.5 | 2.795 | 26.4 | 14.6 | 70 | OK- No Action Required | 25 | 25 | 1.28 | 18.2
BGW2T387 | 2018-10-26 10:01 | 50.7 | 33.5 | 3 | 12.8 | 1011 | 48 | 11 | LOW | [5 empty] | 0 | 3.609 | 22.8 | 4.2 | 22 | OK- No Action Required | 20 | 20 | 1.51 | 1.46
BGW2T228 | 2018-10-26 10:04 | 25.1 | 18.5 | 10.3 | 46.1 | 1011 | 44 | 8 | LOW | [5 empty] | -69.2 | 0.023 | 21.9 | 4.5 | 12 | OK- No Action Required | 99 | 2 | 1.36 | 7.17
BGW2T224 | 2018-10-26 10:08 | 59.7 | 41.1 | 0.1 | 0 | 1011 | 49 | 16 | LOW | [5 empty] | -5.9 | 0.336 | 24 | 5.1 | 32 | OK- No Action Required | 2 | 10 | 1.45 | 0
BGW2T220 | 2018-10-26 10:11 | 50.5 | 35.6 | 0 | 13.9 | 1011 | 52 | 10 | LOW | [5 empty] | -0.4 | 0.775 | 22 | 16.9 | 89 | OK- No Action Required | 20 | 20 | 1.42 | 13.9
BGW2T219 | 2018-10-26 10:13 | 43.5 | 34.1 | 0 | 22.4 | 1011 | 50 | 27 | LOW | [5 empty] | -2.2 | 3.955 | 24.2 | 8.6 | 39 | OK- No Action Required | 20 | 20 | 1.28 | 22.4
BGW2X258 | 2018-10-26 10:22 | 52.7 | 37.3 | 0 | 10 | 1010 | 49 | 12 | LOW | [5 empty] | -67.5 | 0.962 | 32.4 | 29.3 | 161 | OK- No Action Required | 99 | 99 | 1.41 | 10
BGW2X259 | 2018-10-26 10:25 | 55.9 | 38 | 0 | 6.1 | 1010 | 51 | 10 | LOW | [5 empty] | -2.3 | 3.852 | 24.3 | 4.4 | 25 | OK- No Action Required | 5 | 10 | 1.47 | 6.1
BGW2X393 | 2018-10-26 10:29 | 61.8 | 39.3 | 0 | 0 | 1010 | 48 | 11 | LOW | [5 empty] | 0 | 1.607 | 21.5 | 24.7 | 160 | OK- No Action Required | 5 | 10 | 1.57 | 0
BGW2X254 | 2018-10-26 10:31 | 56.5 | 37.9 | 0 | 5.6 | 1010 | 49 | 25 | LOW | [5 empty] | -24.1 | 0.526 | 34.3 | 13.6 | 80 | OK- No Action Required | 5 | 10 | 1.49 | 5.6
BGW2X254 | 2018-10-26 10:32 | 56.5 | 37.9 | 0 | 5.6 | 1010 | 49 | 25 | LOW | [5 empty] | -24.1 | 0.526 | 34.3 | 13.6 | 80 | OK- No Action Required | 5 | 10 | 1.49 | 5.6
BGW2X239 | 2018-10-26 10:34 | 52.8 | 38.3 | 0 | 8.9 | 1010 | 55 | 11 | LOW | [5 empty] | -4.3 | 0.462 | 23.6 | 13 | 71 | OK- No Action Required | 10 | 10 | 1.38 | 8.9
BGW2X247 | 2018-10-26 10:36 | 49.9 | 37.9 | 0 | 12.2 | 1010 | 56 | 17 | LOW | [5 empty] | 0.1 | 0.457 | 21.6 | 6 | 31 | OK- No Action Required | 5 | 5 | 1.32 | 12.2
BGW2X264 | 2018-10-26 10:38 | 55.4 | 38.7 | 0.3 | 5.6 | 1010 | 57 | 5 | LOW | [5 empty] | -53.4 | 18.719 | 34.1 | 130 | 754 | OK- No Action Required | 99 | 99 | 1.43 | 4.47
BGW2X425 | 2018-10-26 10:40 | 47.7 | 37.4 | 0 | 14.9 | 1010 | 58 | 16 | LOW | [5 empty] | -4.5 | 0.436 | 23 | 5.8 | 29 | OK- No Action Required | 10 | 10 | 1.28 | 14.9
BGW2X446 | 2018-10-26 10:42 | 50.9 | 37.9 | 0 | 11.2 | 1010 | 56 | 9 | LOW | [5 empty] | -22.9 | 8.395 | 25.3 | 25.3 | 135 | OK- No Action Required | 30 | 30 | 1.34 | 11.2
BGW2X443 | 2018-10-26 10:45 | 53.8 | 39.7 | 0 | 6.5 | 1010 | 55 | 16 | LOW | [5 empty] | -28.1 | 4.46 | 35.1 | 18.1 | 102 | OK- No Action Required | 10 | 10 | 1.36 | 6.5
BGW2X157 | 2018-10-26 10:47 | 0.3 | 0.2 | 21 | 78.5 | 1009 | 52 | 3 | LOW | [5 empty] | -3.3 | 0.156 | 24.3 | 0.8 | 0 | Shut/Shut | 0 | 0 | 1.5 | 0
BGW2X158 | 2018-10-26 10:49 | 11 | 5.5 | 17.4 | 66.1 | 1009 | 42 | 2 | LOW | [5 empty] | -0.3 | 0.091 | 20.4 | 2.6 | 3 | OK- No Action Required | 2 | 2 | 2 | 0.33
BGW2X441 | 2018-10-26 10:52 | 60.7 | 40.2 | 0.1 | 0 | 1010 | 44 | 6 | LOW | [5 empty] | -71.4 | 0.927 | 23.7 | 8.3 | 53 | OK- No Action Required | 50 | 50 | 1.51 | 0
BGW2X164 | 2018-10-26 10:54 | 55.9 | 38.9 | 0.6 | 4.6 | 1010 | 49 | 27 | LOW | [5 empty] | -77.7 | 0.274 | 24.9 | 9.6 | 56 | OK- No Action Required | 99 | 99 | 1.44 | 2.33
BGW2N145 | 2018-10-26 11:00 | 47 | 36.7 | 0 | 16.3 | 1009 | 52 | 11 | LOW | [5 empty] | -1.4 | 3.474 | 23.4 | 16.4 | 80 | OK- No Action Required | 10 | 10 | 1.28 | 16.3
BGW2N146 | 2018-10-26 11:02 | 49.3 | 38.2 | 0 | 12.5 | 1009 | 54 | 9 | LOW | [5 empty] | -72.7 | 2.212 | 25 | 27.2 | 140 | OK- No Action Required | 30 | 30 | 1.29 | 12.5
BGW2N143 | 2018-10-26 11:04 | 46.6 | 37.4 | 0 | 16 | 1009 | 58 | 8 | LOW | [5 empty] | -1.7 | 0.883 | 23.3 | 17.8 | 87 | OK- No Action Required | 25 | 25 | 1.25 | 16
BGW2N144 | 2018-10-26 11:06 | 50.3 | 38.2 | 0 | 11.5 | 1009 | 57 | 13 | LOW | [5 empty] | -5.8 | 5.256 | 22.1 | 10 | 53 | OK- No Action Required | 15 | 15 | 1.32 | 11.5
BGW2W257 | 2018-10-26 11:12 | 37.3 | 34.3 | 0 | 28.4 | 1009 | 59 | 6 | LOW | [5 empty] | 0 | 7.284 | 45.6 | 22.6 | 88 | OK- No Action Required | 10 | 5 | 1.09 | 28.4
BGW2W242 | 2018-10-26 11:14 | 51 | 37.6 | 0.1 | 11.3 | 1009 | 60 | 10 | LOW | [5 empty] | -61.8 | 1.131 | 27.7 | 31.9 | 171 | OK- No Action Required | 50 | 50 | 1.36 | 10.92
BGW2W392 | 2018-10-26 11:16 | 0.2 | 0.1 | 20.8 | 78.9 | 1008 | 52 | 2 | LOW | [5 empty] | 0.5 | 0.077 | 22.4 | 2.4 | 0 | Shut/Shut | 0 | 0 | 2 | 0.28
BGW2W246 | 2018-10-26 11:18 | 50.3 | 37.5 | 0 | 12.2 | 1008 | 50 | 22 | LOW | [5 empty] | -0.1 | 1.165 | 23 | 9.5 | 50 | OK- No Action Required | 10 | 10 | 1.34 | 12.2
BGW2W256 | 2018-10-26 11:20 | 46.8 | 35.2 | 3.5 | 14.5 | 1008 | 65 | 10 | LOW | [5 empty] | -50.4 | 1.505 | 36.4 | 36.4 | 178 | OK- No Action Required | 35 | 35 | 1.33 | 1.27
BGW2W261 | 2018-10-26 11:22 | 45.4 | 36.4 | 0 | 18.2 | 1008 | 62 | 10 | LOW | [5 empty] | -1.4 | 2.255 | 28.4 | 13.1 | 62 | OK- No Action Required | 10 | 10 | 1.25 | 18.2
BGW2U243 | 2018-10-26 11:38 | 56 | 39.9 | 0 | 4.1 | 1008 | 69 | 24 | LOW | [5 empty] | -1.7 | 1.794 | 26.4 | 25.5 | 150 | OK- No Action Required | 10 | 20 | 1.4 | 4.1
BGW2U398 | 2018-10-26 11:40 | 48.8 | 37 | 0.5 | 13.7 | 1008 | 81 | 9 | LOW | [5 empty] | -5.5 | 1.533 | 20.9 | 23.6 | 121 | OK- No Action Required | 20 | 20 | 1.32 | 11.81
BGW2U238 | 2018-10-26 11:42 | 50 | 37.2 | 0.1 | 12.7 | 1008 | 86 | 23 | LOW | [5 empty] | -0.6 | 1.567 | 23.8 | 11 | 58 | OK- No Action Required | 20 | 0 | 1.34 | 12.32
BGW2U238 | 2018-10-26 11:42 | 50 | 37.2 | 0.1 | 12.7 | 1008 | 86 | 23 | LOW | [5 empty] | -0.6 | 1.567 | 23.8 | 11 | 58 | OK- No Action Required | 20 | 20 | 1.34 | 12.32
BGW2U227 | 2018-10-26 11:45 | 48 | 36.4 | 0.1 | 15.5 | 1008 | 93 | 13 | LOW | [5 empty] | -4.4 | 9.101 | 24.7 | 26.5 | 133 | OK- No Action Required | 25 | 25 | 1.32 | 15.12
BGW2U232 | 2018-10-26 11:47 | 59.3 | 40.4 | 0.1 | 0.2 | 1008 | 94 | 10 | LOW | [5 empty] | -62 | 2.414 | 38.9 | 46.3 | 287 | OK- No Action Required | 99 | 99 | 1.47 | 0
BGW2U226 | 2018-10-26 11:49 | 60.2 | 43.2 | 0 | 0 | 1008 | 107 | 15 | LOW | [5 empty] | -53.7 | 0.074 | 23.7 | 2.3 | 14 | OK- No Action Required | 10 | 20 | 1.39 | 0
BGW2U439 | 2018-10-26 11:51 | 11.9 | 7.8 | 17 | 63.3 | 1008 | 97 | 5 | LOW | [5 empty] | 0.5 | 0.077 | 21.9 | 2.4 | 3 | Shut/Shut | 0 | 0 | 1.53 | 0
BGW2U241 | 2018-10-26 11:54 | 57.9 | 42.9 | 1.7 | 0 | 1008 | 86 | 12 | LOW | [5 empty] | -21.9 | 0.076 | 33.1 | 5.1 | 31 | OK- No Action Required | 2 | 5 | 1.35 | 0
BGW2U251 | 2018-10-26 11:56 | 51.4 | 40.4 | 0 | 8.2 | 1008 | 97 | 13 | LOW | [5 empty] | -56.7 | 5.674 | 42 | 42.6 | 229 | OK- No Action Required | 99 | 99 | 1.27 | 8.2
BGW2U245 | 2018-10-26 11:58 | 46.2 | 35.5 | 2.3 | 16 | 1008 | 93 | 7 | LOW | [5 empty] | -16.4 | 6.788 | 42.9 | 47.6 | 230 | OK- No Action Required | 40 | 40 | 1.3 | 7.31
BGW2U391 | 2018-10-26 12:01 | 55.2 | 40.9 | 0.1 | 3.8 | 1008 | 92 | 23 | LOW | [5 empty] | 0.1 | 0.603 | 23 | 6.8 | 39 | OK- No Action Required | 5 | 10 | 1.35 | 3.42
BGW2U440 | 2018-10-26 12:04 | 1.8 | 1.4 | 20.5 | 76.3 | 1008 | 77 | 5 | LOW | [5 empty] | -59.5 | 0.067 | 23.4 | 2.2 | 0 | Open/Shut | 5 | 0 | 1.29 | 0
BGW2U284 | 2018-10-26 12:06 | 60.5 | 41.6 | 0.4 | 0 | 1008 | 78 | 5 | LOW | [5 empty] | -62.2 | 0.011 | 26.4 | 1.9 | 12 | OK- No Action Required | 99 | 99 | 1.45 | 0
BGW2U399 | 2018-10-26 12:08 | 43.2 | 32.4 | 4.3 | 20.1 | 1008 | 95 | 14 | LOW | [5 empty] | -20.6 | 2.241 | 47.5 | 27.1 | 123 | OK- No Action Required | 25 | 25 | 1.33 | 3.85
BGW2U351 | 2018-10-26 12:11 | 48.8 | 36.3 | 0.1 | 14.8 | 1008 | 86 | 4 | LOW | [5 empty] | -0.1 | 0.017 | 26.9 | 1.1 | 5 | OK- No Action Required | 0 | 5 | 1.34 | 14.42
BHW2U352 | 2018-10-26 12:13 | 57.8 | 41.1 | 0.3 | 0.8 | 1008 | 85 | 10 | LOW | [5 empty] | -55.1 | 5.885 | 44.9 | 71.5 | 433 | OK- No Action Required | 99 | 99 | 1.41 | 0
BHW2U353 | 2018-10-26 12:15 | 60.3 | 41.8 | 0 | 0 | 1008 | 89 | 11 | LOW | [5 empty] | -54.1 | 6.978 | 45.1 | 47.8 | 302 | OK- No Action Required | 99 | 99 | 1.44 | 0
BHW2U354 | 2018-10-26 12:19 | 46.2 | 35.3 | 2.1 | 16.4 | 1008 | 113 | 8 | LOW | [5 empty] | -46.4 | 19.09 | 53.1 | 77.4 | 374 | OK- No Action Required | 99 | 50 | 1.31 | 8.46
BHW2V407 | 2018-10-26 13:09 | 44.3 | 35.1 | 3.9 | 16.7 | 1008 | 83 | 18 | LOW | [5 empty] | -69 | 0.146 | 19.7 | 7 | 32 | OK- No Action Required | 20 | 20 | 1.26 | 1.96
BGW2V255 | 2018-10-26 13:11 | 47.1 | 32.8 | 3.9 | 16.2 | 1008 | 76 | 24 | LOW | [5 empty] | -69.4 | 0.029 | 20.6 | 1.4 | 7 | OK- No Action Required | 99 | 99 | 1.44 | 1.46
BGW2V262 | 2018-10-26 13:13 | 57.4 | 42.1 | 0.4 | 0.1 | 1008 | 78 | 11 | LOW | [5 empty] | -68.8 | 0.556 | 44.4 | 13.3 | 80 | OK- No Action Required | 99 | 99 | 1.36 | 0
BGW2V390 | 2018-10-26 13:16 | 53.3 | 40 | 0 | 6.7 | 1008 | 85 | 22 | LOW | [5 empty] | -14.1 | 4.398 | 41.7 | 38.5 | 215 | OK- No Action Required | 30 | 30 | 1.33 | 6.7
BGW2V379 | 2018-10-26 13:18 | 48.7 | 37.3 | 0.4 | 13.6 | 1008 | 83 | 6 | LOW | [5 empty] | 0.1 | 3.886 | 29 | 4.3 | 22 | OK- No Action Required | 20 | 20 | 1.31 | 12.09
BGW2V379 | 2018-10-26 13:19 | 48.7 | 37.3 | 0.3 | 13.7 | 1008 | 88 | 6 | LOW | [5 empty] | 0 | 5.765 | 26.5 | 5.3 | 27 | OK- No Action Required | 20 | 20 | 1.31 | 12.57
BHW2V413 | 2018-10-26 13:21 | 10.6 | 7.6 | 16.7 | 65.1 | 1008 | 71 | 2 | LOW | [5 empty] | -3.6 | 0.008 | 23.1 | 0.8 | 0 | Shut/Shut | 0 | 0 | 1.39 | 1.97
BHW2V413 | 2018-10-26 13:24 | 8.4 | 6.2 | 17.5 | 67.9 | 1008 | 61 | 2 | LOW | [5 empty] | -2.1 | 0.056 | 22.4 | 2 | 1 | Shut/Shut | 0 | 0 | 1.35 | 1.75
BHW2V414 | 2018-10-26 13:27 | 17.9 | 12.6 | 14.4 | 55.1 | 1008 | 55 | 4 | LOW | [5 empty] | -69 | 0.153 | 20.1 | 7.2 | 13 | OK- No Action Required | 99 | 2 | 1.42 | 0.67
BGW2V244 | 2018-10-26 13:31 | 23.2 | 16.4 | 12.8 | 47.6 | 1008 | 56 | 5 | LOW | [5 empty] | -69.3 | 0.002 | 21.1 | 0.3 | 0 | OK- No Action Required | 99 | 2 | 1.41 | 0
BHW2V415 | 2018-10-26 13:33 | 60.2 | 41.8 | 0 | 0 | 1008 | 62 | 11 | LOW | [5 empty] | -67.9 | 1.235 | 43.1 | 32.7 | 206 | OK- No Action Required | 99 | 99 | 1.44 | 0
BGW2V267 | 2018-10-26 13:35 | 0.5 | 0.5 | 20.8 | 78.2 | 1008 | 70 | 4 | LOW | [5 empty] | 0.3 | 0.079 | 28.6 | 2.4 | 0 | Shut/Shut | 0 | 0 | 1 | 0
BGW2M435 | 2018-10-26 13:42 | 0.4 | 0.5 | 20.7 | 78.4 | 1007 | 60 | 4 | LOW | [5 empty] | -0.9 | 0.075 | 21.7 | 0.1 | 0 | Shut/Shut | 0 | 0 | 0.8 | 0.15
BGW2M450 | 2018-10-26 13:45 | 58.9 | 42.5 | 1.7 | 0 | 1008 | 71 | 10 | LOW | [5 empty] | -30.3 | 22.019 | 26.5 | 10.2 | 63 | OK- No Action Required | 20 | 30 | 1.39 | 0
BGW2M381 | 2018-10-26 13:47 | 50.3 | 38.6 | 0 | 11.1 | 1008 | 68 | 17 | LOW | [5 empty] | -16.8 | 15.504 | 44.8 | 33.3 | 175 | OK- No Action Required | 30 | 30 | 1.3 | 11.1
BGW2M124 | 2018-10-26 13:49 | 57 | 40.6 | 0.4 | 2 | 1008 | 82 | 27 | LOW | [5 empty] | -0.5 | 0.059 | 26.8 | 4.6 | 27 | OK- No Action Required | 20 | 20 | 1.4 | 0.49
BGW2M397 | 2018-10-26 13:51 | 51.4 | 40.3 | 0 | 8.3 | 1008 | 85 | 18 | LOW | [5 empty] | -44 | 8.176 | 48.7 | 23.6 | 127 | OK- No Action Required | 50 | 50 | 1.28 | 8.3
BGW2M432 | 2018-10-26 13:54 | 52.6 | 40 | 0.8 | 6.6 | 1008 | 86 | 19 | LOW | [5 empty] | -3.8 | 7.812 | 22.5 | 6.2 | 34 | OK- No Action Required | 10 | 10 | 1.32 | 3.58
BGW2M432 | 2018-10-26 13:54 | 52.6 | 40 | 0.8 | 6.6 | 1008 | 86 | 19 | LOW | [5 empty] | -3.8 | 7.812 | 22.5 | 6.2 | 34 | OK- No Action Required | 10 | 15 | 1.32 | 3.58
BGW2M131 | 2018-10-26 13:57 | 38.8 | 33.6 | 0.9 | 26.7 | 1008 | 72 | 10 | LOW | [5 empty] | 0.5 | 1.392 | 26.2 | 5 | 20 | OK- No Action Required | 5 | 2 | 1.15 | 23.3
BGW2M434 | 2018-10-26 13:59 | 51.6 | 38.6 | 0 | 9.8 | 1007 | 69 | 12 | LOW | [5 empty] | -0.9 | 10.672 | 33.9 | 28.4 | 153 | OK- No Action Required | 15 | 20 | 1.34 | 9.8
BGW2M083 | 2018-10-26 14:01 | 48.8 | 35.8 | 3.2 | 12.2 | 1007 | 67 | 12 | LOW | [5 empty] | 0.1 | 0.105 | 31.4 | 9.9 | 51 | OK- No Action Required | 10 | 10 | 1.36 | 0.1
BGW2M128 | 2018-10-26 14:04 | 61.1 | 41.5 | 0.8 | 0 | 1007 | 77 | 14 | LOW | [5 empty] | -14.9 | 0.406 | 20.8 | 5.6 | 36 | OK- No Action Required | 2 | 5 | 1.47 | 0
BGW2J090 | 2018-10-26 14:22 | 53.1 | 37.9 | 0.3 | 8.7 | 1008 | 56 | 7 | LOW | [5 empty] | -4.2 | 10.593 | 31.1 | 28.5 | 159 | OK- No Action Required | 30 | 30 | 1.4 | 7.57
BGW2J087 | 2018-10-26 14:24 | 48.6 | 37.1 | 0.8 | 13.5 | 1008 | 56 | 6 | LOW | [5 empty] | -1 | 2.115 | 23.2 | 6.3 | 32 | OK- No Action Required | 15 | 15 | 1.31 | 10.48
BGW2J091 | 2018-10-26 14:27 | 60 | 40.9 | 0.1 | 0 | 1008 | 60 | 9 | LOW | [5 empty] | 0.5 | 1.157 | 23.7 | 4.7 | 30 | OK- No Action Required | 15 | 15 | 1.47 | 0
BGW2J401 | 2018-10-26 14:30 | 54.9 | 38.5 | 0.7 | 5.9 | 1008 | 65 | 11 | LOW | [5 empty] | -40.6 | 6.4 | 22.1 | 22.1 | 127 | OK- No Action Required | 30 | 30 | 1.43 | 3.25
BGW2J089 | 2018-10-26 14:33 | 37.9 | 31.8 | 2.1 | 28.2 | 1008 | 58 | 8 | LOW | [5 empty] | 0.4 | 1.848 | 25.9 | 11.8 | 47 | OK- No Action Required | 5 | 10 | 1.19 | 20.26
BGW2J430 | 2018-10-26 14:36 | 46.6 | 36.7 | 0 | 16.7 | 1008 | 56 | 14 | LOW | [5 empty] | -2.2 | 1.542 | 21.3 | 10.9 | 53 | OK- No Action Required | 15 | 15 | 1.27 | 16.7
BGW2J408 | 2018-10-26 14:38 | 51 | 37.6 | 1.3 | 10.1 | 1008 | 59 | 4 | LOW | [5 empty] | 0.4 | 5.599 | 21.6 | 5.2 | 28 | OK- No Action Required | 15 | 15 | 1.36 | 5.19
BGW2J400 | 2018-10-26 14:40 | 49.6 | 39.1 | 0 | 11.3 | 1008 | 61 | 5 | LOW | [5 empty] | 0.2 | 1.778 | 27.8 | 11.6 | 60 | OK- No Action Required | 15 | 115 | 1.27 | 11.3
BGW2L380 | 2018-10-26 14:52 | 31.6 | 28.9 | 4.7 | 34.8 | 1007 | 86 | 4 | LOW | [5 empty] | 0 | 6.778 | 19.2 | 1.2 | 4 | OK- No Action Required | 10 | 10 | 1.09 | 17.03
BGW2L134 | 2018-10-26 14:55 | 49.3 | 37 | 0.4 | 13.3 | 1007 | 72 | 11 | LOW | [5 empty] | -0.5 | 0.667 | 34.6 | 15.3 | 79 | OK- No Action Required | 20 | 20 | 1.33 | 11.79
BGW2L133 | 2018-10-26 14:57 | 49.1 | 37.9 | 0.1 | 12.9 | 1007 | 76 | 10 | LOW | [5 empty] | -1.3 | 8.776 | 41.6 | 12.5 | 64 | OK- No Action Required | 20 | 20 | 1.3 | 12.52
BGW2L431 | 2018-10-26 14:59 | 53.8 | 38.7 | 0 | 7.5 | 1007 | 81 | 10 | LOW | [5 empty] | -46.8 | 13.871 | 47.2 | 109.7 | 618 | OK- No Action Required | 15 | 80 | 1.39 | 7.5
BGW2L378 | 2018-10-26 15:01 | 49.2 | 38.8 | 0 | 12 | 1007 | 81 | 7 | LOW | [5 empty] | -0.6 | 3.226 | 46.9 | 15.2 | 78 | OK- No Action Required | 20 | 20 | 1.27 | 12
BGW2L140 | 2018-10-26 15:05 | 57.2 | 42.3 | 0 | 0.5 | 1007 | 82 | 25 | LOW | [5 empty] | -49.7 | 13.999 | 26.1 | 8.1 | 48 | OK- No Action Required | 20 | 40 | 1.35 | 0.5
BGW2L377 | 2018-10-26 15:08 | 50 | 38.8 | 0 | 11.2 | 1007 | 84 | 11 | LOW | [5 empty] | -0.1 | 2.663 | 34.8 | 14.1 | 74 | OK- No Action Required | 10 | 20 | 1.29 | 11.2
BGW2L420 | 2018-10-26 15:11 | 24.5 | 17.5 | 11.3 | 46.7 | 1007 | 76 | 5 | LOW | [5 empty] | 0 | 6.204 | 21.2 | 5.5 | 14 | Open/Shut | 5 | 0 | 1.4 | 3.99
BGW2L359 | 2018-10-26 15:13 | 37.5 | 30.6 | 3.1 | 28.8 | 1007 | 74 | 8 | LOW | [5 empty] | -0.2 | 9.484 | 24.3 | 6.7 | 26 | OK- No Action Required | 10 | 10 | 1.23 | 17.08
BGW2L101 | 2018-10-26 15:15 | 48.3 | 37.3 | 0.2 | 14.2 | 1007 | 83 | 12 | LOW | [5 empty] | -24.3 | 2.434 | 49.7 | 0.7 | 3 | OK- No Action Required | 30 | 30 | 1.29 | 13.44
BGW2L101 | 2018-10-26 15:18 | 2.8 | 1.4 | 19.9 | 75.9 | 1007 | 83 | 3 | LOW | [5 empty] | -0.3 | 0.005 | 19.9 | 0 | 0 | Shut/Shut | 2 | 2 | 2 | 0.68
BGW2L417 | 2018-10-26 15:20 | 44.1 | 31.7 | 4.8 | 19.4 | 1007 | 74 | 6 | LOW | [5 empty] | -3.8 | 2.615 | 26.1 | 30.7 | 142 | OK- No Action Required | 25 | 25 | 1.39 | 1.26
BGW2L056 | 2018-10-26 15:23 | 31.7 | 31.2 | 0 | 37.1 | 1007 | 72 | 8 | LOW | [5 empty] | 0 | 18.323 | 22.6 | 9.3 | 31 | OK- No Action Required | 20 | 5 | 1.02 | 37.1
BGW2L082 | 2018-10-26 15:25 | 58.1 | 41.2 | 0 | 0.7 | 1007 | 72 | 7 | LOW | [5 empty] | -38.3 | 28.583 | 27.5 | 46.4 | 283 | OK- No Action Required | 99 | 99 | 1.41 | 0.7
BGW2L448 | 2018-10-26 15:28 | 52.7 | 38.3 | 0 | 9 | 1007 | 75 | 11 | LOW | [5 empty] | -23.9 | 11.692 | 34.7 | 63.5 | 350 | OK- No Action Required | 45 | 50 | 1.38 | 9
BGW2L150 | 2018-10-26 15:30 | 55.4 | 40.3 | 0 | 4.3 | 1007 | 78 | 6 | LOW | [5 empty] | -66.7 | 2.602 | 38.7 | 47.6 | 276 | OK- No Action Required | 99 | 99 | 1.37 | 4.3
BGW2L376 | 2018-10-26 15:32 | 45.9 | 35.9 | 0.9 | 17.3 | 1006 | 80 | 5 | LOW | [5 empty] | -0.4 | 19.291 | 27.5 | 9.6 | 46 | OK- No Action Required | 2 | 25 | 1.28 | 13.9
BGW2L433 | 2018-10-26 15:34 | 43.3 | 33 | 3.6 | 20.1 | 1006 | 78 | 6 | LOW | [5 empty] | -0.1 | 2.324 | 23.6 | 13.4 | 61 | OK- No Action Required | 0 | 30 | 1.31 | 6.49
BGW2L053 | 2018-10-26 15:35 | 58.9 | 40.1 | 0 | 1 | 1006 | 74 | 11 | LOW | [5 empty] | -68.5 | 0.242 | 24 | 15 | 92 | OK- No Action Required | 99 | 99 | 1.47 | 1
BGW2K429 | 2018-10-29 11:27 | 14.7 | 22.1 | 3.2 | 60 | 1010 | 33 | 2 | LOW | [5 empty] | -0.4 | 0.629 | 21.4 | 1.7 | 2 | OK- No Action Required | 5 | 2 | 0.67 | 47.9
BGW2K372 | 2018-10-29 11:29 | 41.2 | 34 | 1.1 | 23.7 | 1010 | 30 | 12 | LOW | [5 empty] | -0.8 | 6.546 | 27.2 | 5.6 | 24 | OK- No Action Required | 5 | 5 | 1.21 | 19.54
BGW2K375 | 2018-10-29 11:32 | 49 | 37.3 | 0.3 | 13.4 | 1010 | 38 | 16 | LOW | [5 empty] | -29.2 | 20.458 | 38.4 | 82.9 | 425 | OK- No Action Required | 60 | 60 | 1.31 | 12.27
BGW2K428 | 2018-10-29 11:34 | 46.7 | 35 | 1.1 | 17.2 | 1010 | 47 | 9 | LOW | [5 empty] | -0.9 | 3.756 | 34.1 | 16.8 | 82 | OK- No Action Required | 40 | 40 | 1.33 | 13.04
BGW2K427 | 2018-10-29 11:37 | 49 | 36.1 | 0 | 14.9 | 1010 | 45 | 10 | LOW | [5 empty] | -0.6 | 4.924 | 21.3 | 4.9 | 25 | OK- No Action Required | 5 | 10 | 1.36 | 14.9
BGW2K426 | 2018-10-29 11:41 | 50.8 | 36.9 | 0 | 12.3 | 1010 | 43 | 21 | LOW | [5 empty] | -0.2 | 24.449 | 21.7 | 11 | 59 | OK- No Action Required | 25 | 25 | 1.38 | 12.3
BGW2K373 | 2018-10-29 11:43 | 50.4 | 37.3 | 0 | 12.3 | 1010 | 41 | 42 | LOW | [5 empty] | -3.1 | 1.033 | 26.1 | 19.3 | 102 | OK- No Action Required | 25 | 30 | 1.35 | 12.3
BGW2K374 | 2018-10-29 11:47 | 47.1 | 36.1 | 0.2 | 16.6 | 1010 | 45 | 22 | LOW | [5 empty] | -2 | 1.449 | 28.6 | 22.7 | 112 | OK- No Action Required | 30 | 25 | 1.3 | 15.84
BGW2K093 | 2018-10-29 11:50 | 51.1 | 37.2 | 0 | 11.7 | 1010 | 45 | 69 | LOW | [5 empty] | -0.4 | -0.008 | 21.7 | N/A | N/A | OK- No Action Required | 20 | 30 | 1.37 | 11.7
BGW2K095 | 2018-10-29 11:55 | 59.1 | 40 | 0.9 | 0 | 1010 | 46 | 21 | LOW | [5 empty] | -66.6 | 0.085 | 20.6 | 8.9 | 55 | Surge | 90 | 99 | 1.48 | 0
BGW2K094 | 2018-10-29 11:57 | 47.9 | 35.9 | 0.6 | 15.6 | 1010 | 49 | 18 | LOW | [5 empty] | -3.4 | 2.545 | 41.9 | 29.5 | 148 | OK- No Action Required | 40 | 40 | 1.33 | 13.33
BGW2H424 | 2018-10-29 12:15 | 45.4 | 33.6 | 2.3 | 18.7 | 1009 | 41 | 19 | LOW | [5 empty] | -0.6 | 0.86 | 21.1 | 8.2 | 39 | OK- No Action Required | 30 | 30 | 1.35 | 10.01
BGW2H059 | 2018-10-29 12:17 | 53.1 | 39.4 | 0 | 7.5 | 1009 | 45 | 18 | LOW | [5 empty] | 0 | 6.046 | 23.4 | 5.4 | 30 | OK- No Action Required | 30 | 30 | 1.35 | 7.5
BGW2H402 | 2018-10-29 12:21 | 53.2 | 38.8 | 0.4 | 7.6 | 1008 | 47 | 18 | LOW | [5 empty] | -1.3 | 7.87 | 31.2 | 12.1 | 68 | OK- No Action Required | 25 | 30 | 1.37 | 6.09
BGW2H064 | 2018-10-29 12:24 | 53.3 | 38.3 | 0.2 | 8.2 | 1008 | 51 | 12 | LOW | [5 empty] | -0.4 | 3.777 | 24.5 | 8.5 | 47 | OK- No Action Required | 25 | 25 | 1.39 | 7.44
BGW2H423 | 2018-10-29 12:27 | 52.7 | 37.8 | 0 | 9.5 | 1008 | 48 | 12 | LOW | [5 empty] | -1.7 | 9.288 | 26.9 | 26.9 | 148 | OK- No Action Required | 30 | 40 | 1.39 | 9.5
BGW2H363 | 2018-10-29 12:30 | 52.7 | 37.1 | 0.6 | 9.6 | 1008 | 49 | 16 | LOW | [5 empty] | -0.7 | 1.191 | 23.3 | 20.9 | 115 | OK- No Action Required | 30 | 30 | 1.42 | 7.33
BGW2H365 | 2018-10-29 12:32 | 51.1 | 37.6 | 0 | 11.3 | 1008 | 49 | 14 | LOW | [5 empty] | -3.6 | 0.816 | 24.3 | 17.2 | 92 | OK- No Action Required | 25 | 25 | 1.36 | 11.3
BGW2H361 | 2018-10-29 12:35 | 54.4 | 40.1 | 0 | 5.5 | 1008 | 53 | 14 | LOW | [5 empty] | -0.5 | 7.713 | 27.2 | 12.1 | 69 | OK- No Action Required | 25 | 30 | 1.36 | 5.5
BGW2H360 | 2018-10-29 12:37 | 48.3 | 35.7 | 0 | 16 | 1008 | 51 | 3 | LOW | [5 empty] | -0.3 | 4.196 | 20.9 | 4.5 | 23 | OK- No Action Required | 20 | 20 | 1.35 | 16
BGW2H366 | 2018-10-29 12:39 | 48.2 | 32.1 | 3 | 16.7 | 1008 | 48 | 7 | LOW | [5 empty] | -0.4 | 4.902 | 20.5 | 9.8 | 49 | OK- No Action Required | 25 | 25 | 1.5 | 5.36
BGW2H362 | 2018-10-29 12:41 | 49.7 | 37 | 1.3 | 12 | 1008 | 47 | 14 | LOW | [5 empty] | -0.7 | 3.865 | 24.9 | 8.6 | 44 | OK- No Action Required | 25 | 25 | 1.34 | 7.09
BGW2H058 | 2018-10-29 12:44 | 35.9 | 26.3 | 7.6 | 30.2 | 1008 | 47 | 20 | LOW | [5 empty] | -13.1 | 0.356 | 25.6 | 5.2 | 19 | OK- No Action Required | 25 | 10 | 1.37 | 1.47
BGW2H412 | 2018-10-29 12:48 | 28.4 | 22.3 | 7.6 | 41.7 | 1008 | 48 | 3 | LOW | [5 empty] | 0.3 | -0.006 | 20.5 | N/A | N/A | Shut/Open | 0 | 1 | 1.27 | 12.97
BGW2H102 | 2018-10-29 12:51 | 56.3 | 38.6 | 0.9 | 4.2 | 1008 | 44 | 13 | LOW | [5 empty] | -0.3 | 0.025 | 21 | 0.7 | 4 | OK- No Action Required | 5 | 10 | 1.46 | 0.8
BGW2H422 | 2018-10-29 12:53 | 34.1 | 25.8 | 6.1 | 34 | 1007 | 59 | 2 | LOW | [5 empty] | 0.1 | 15.394 | 21.5 | 1.9 | 6 | OK- No Action Required | 10 | 10 | 1.32 | 10.94
BGW2I367 | 2018-10-29 13:47 | 39.8 | 30.1 | 3.1 | 27 | 1008 | 41 | 8 | LOW | [5 empty] | -0.6 | 25.751 | 30.9 | 11.1 | 46 | OK- No Action Required | 30 | 20 | 1.32 | 15.28
BGW2I368 | 2018-10-29 13:49 | 37.7 | 27.3 | 5.8 | 29.2 | 1008 | 50 | 2 | LOW | [5 empty] | 0.2 | 1.027 | 22.9 | 4.4 | 17 | OK- No Action Required | 20 |  | 1.38 | 7.28
BGW2I370 | 2018-10-29 13:53 | 54.5 | 38.3 | 0.1 | 7.1 | 1008 | 54 | 42 | LOW | [5 empty] | 0.1 | 22.966 | 25.7 | 10.7 | 61 | OK- No Action Required | 20 | 25 | 1.42 | 6.72
BGW2I445 | 2018-10-29 13:57 | 59.4 | 39.2 | 0 | 1.4 | 1008 | 60 | 9 | LOW | [5 empty] | -0.3 | 20.479 | 19.3 | 20.3 | 126 | OK- No Action Required | 15 | 20 | 1.52 | 1.4
BGW2I081 | 2018-10-29 14:00 | 55.3 | 36.9 | 0 | 7.8 | 1008 | 56 | 11 | LOW | [5 empty] | 0.4 | 0.003 | 22.6 | 1.1 | 6 | OK- No Action Required | 10 | 15 | 1.5 | 7.8
BGW2I371 | 2018-10-29 14:02 | 49.1 | 35.8 | 0 | 15.1 | 1008 | 56 | 19 | LOW | [5 empty] | -2.7 | 1.264 | 33.3 | 21.1 | 108 | OK- No Action Required | 25 |  | 1.37 | 15.1
BGW2I369 | 2018-10-29 14:05 | 57 | 39.1 | 0 | 3.9 | 1008 | 57 | 22 | LOW | [5 empty] | 0.3 | 9.594 | 26.9 | 6.9 | 41 | OK- No Action Required | 10 | 20 | 1.46 | 3.9
BGW2I396 | 2018-10-29 14:08 | 42.9 | 33.9 | 0 | 23.2 | 1008 | 56 | 18 | LOW | [5 empty] | -12.6 | 5.41 | 32.9 | 43.2 | 194 | OK- No Action Required | 50 | 40 | 1.27 | 23.2
BGW2I442 | 2018-10-29 14:13 | 55 | 39.1 | 0 | 5.9 | 1008 | 56 | 34 | LOW | [5 empty] | 0.6 | 0.461 | 21.3 | 0.3 | 1 | OK- No Action Required | 15 | 20 | 1.41 | 5.9
BHW2F416 | 2018-10-30 15:48 | 40.8 | 31.4 | 3.7 | 24.1 | 1004 | 41 | 4 | LOW | [5 empty] | -29.4 | 0.444 | 36.3 | 19.9 | 85 | Surge | 50 | 50 | 1.3 | 10.11
BGW2F358 | 2018-10-30 15:51 | 57.9 | 41.2 | 0 | 0.9 | 1004 | 45 | 41 | LOW | [5 empty] | 0.1 | 0.36 | 28.6 | 5.3 | 32 | OK- No Action Required | 20 | 25 | 1.41 | 0.9
BGW2C355 | 2018-10-30 09:27 | 49.3 | 36.4 | 1.3 | 13 | 1010 | 22 | 7 | LOW | [5 empty] | -35.2 | 18.824 | 36 | 130.3 | 673 | OK- No Action Required | 80 | 80 | 1.35 | 8.09
BGW2C394 | 2018-10-30 09:30 | 51.8 | 36.9 | 0.1 | 11.2 | 1010 | 26 | 5 | LOW | [5 empty] | -14.5 | 4.312 | 31.2 | 63.8 | 346 | OK- No Action Required | 50 | 55 | 1.4 | 10.82
BHW2C403 | 2018-10-30 09:34 | 62.9 | 38.4 | 0 | 0 | 1010 | 23 | 9 | LOW | [5 empty] | -84.9 | 1.99 | 23.5 | 12.2 | 80 | OK- No Action Required | 99 | 99 | 1.64 | 0
BHW2C404 | 2018-10-30 09:38 | 53 | 38 | 0 | 9 | 1010 | 21 | 2 | LOW | [5 empty] | -4.8 | 2.54 | 29.3 | 49.3 | 274 | OK- No Action Required | 50 | 53 | 1.39 | 9
BHW3A451 | 2018-10-30 09:46 | 57.6 | 43.6 | 1.2 | 0 | 1010 | 70 | 9 | LOW | [5 empty] | -83 | 0.331 | 20.7 | 10.5 | 63 | OK- No Action Required | 99 | 99 | 1.32 | 0
BHW3A452 | 2018-10-30 09:48 | 50.8 | 44 | 0 | 5.2 | 1010 | 123 | 8 | LOW | [5 empty] | -11.1 | 11.648 | 20.6 | 64 | 340 | OK- No Action Required | 50 | 50 | 1.15 | 5.2
BHW3A453 | 2018-10-30 09:51 | 64.4 | 44.4 | 0 | 0 | 1010 | 107 | 11 | LOW | [5 empty] | -74 | 10.969 | 23.6 | 100.5 | 678 | OK- No Action Required | 99 | 99 | 1.45 | 0
BHW3A454 | 2018-10-30 09:53 | 63.1 | 44.1 | 0 | 0 | 1010 | 101 | 20 | LOW | [5 empty] | -76.2 | 7.774 | 29.6 | 51.1 | 338 | Change Orife Plate Required | 99 | 99 | 1.43 | 0
BHW3A455 | 2018-10-30 09:55 | 62.6 | 43.3 | 0 | 0 | 1010 | 127 | 21 | LOW | [5 empty] | -78.6 | 4.852 | 32.6 | 40.2 | 263 | Change Orife Plate Required | 99 | 99 | 1.45 | 0
BGW2G052 | 2018-10-30 10:11 | 42.4 | 33.6 | 1.2 | 22.8 | 1010 | 128 | 0 | LOW | [5 empty] | -0.1 | 0.037 | 18.7 | 0.8 | 3 | OK- No Action Required | 20 | 20 | 1.26 | 18.26
BGW2G054 | 2018-10-30 10:14 | 48.2 | 38.4 | 0.5 | 12.9 | 1010 | 128 | 9 | LOW | [5 empty] | -69.6 | 15.819 | 45.7 | 70.2 | 354 | OK- No Action Required | 70 | 70 | 1.26 | 11.01
BGW2G418 | 2018-10-30 10:16 | 39 | 32 | 1.2 | 27.8 | 1010 | 123 | 1 | LOW | [5 empty] | -0.8 | 0.058 | 27.2 | 2.1 | 8 | OK- No Action Required | 20 | 20 | 1.22 | 23.26
BGW2G419 | 2018-10-30 10:18 | 48.4 | 36.9 | 0.2 | 14.5 | 1010 | 115 | 6 | LOW | [5 empty] | -5.1 | 2.564 | 31.1 | 30 | 152 | OK- No Action Required | 40 | 40 | 1.31 | 13.74
BGW2G421 | 2018-10-30 10:21 | 43.1 | 30.9 | 4.2 | 21.8 | 1010 | 109 | 7 | LOW | [5 empty] | -5 | 3.597 | 28.5 | 35.8 | 161 | OK- No Action Required | 25 | 20 | 1.39 | 5.92
BGW2E356 | 2018-10-30 10:35 | 35.8 | 27 | 6.2 | 31 | 1010 | 75 | 0 | LOW | [5 empty] | -0.1 | 0.124 | 20.2 | 3.1 | 11 | OK- No Action Required | 10 | 10 | 1.33 | 7.56
BGW2E395 | 2018-10-30 10:38 | 48.9 | 35.5 | 0.5 | 15.1 | 1010 | 73 | 20 | LOW | [5 empty] | -14.8 | 10.161 | 28 | 27.9 | 143 | OK- No Action Required | 35 | 35 | 1.38 | 13.21
BGW2E357 | 2018-10-30 10:41 | 5 | 5.2 | 17.7 | 72.1 | 1010 | 65 | 1 | LOW | [5 empty] | -7.1 | 0.058 | 21 | 2.1 | 1 | Shut/Shut | 0 | 0 | 0.96 | 5.19
BGW2X459 | 2018-10-30 11:14 | 41.1 | 32.8 | 0.3 | 25.8 | 1011 | 54 | 4 | LOW | [5 empty] | -0.1 | 4.214 | 26.2 | 8.9 | 38 | OK- No Action Required | 25 | 10 | 1.25 | 24.67
BLW2X467 | 2018-10-30 11:21 | 1.8 | 4.2 | 17.2 | 76.8 | 1011 | 45 | 0 | LOW | [5 empty] | -66 | 0.364 | 32.7 | 4.9 | 0 | Shut/Shut | 0 | 0 | 0.43 | 11.78
BLW2X466 | 2018-10-30 11:25 | 0.1 | 0.1 | 20.7 | 79.1 | 1011 | 42 | 0 | LOW | [5 empty] | -66.5 | -0.062 | 27.2 | N/A | N/A | Shut/Shut | 0 | 0 | 1 | 0.85
BGW2X458 | 2018-10-30 11:29 | 36.9 | 32.4 | 0.1 | 30.6 | 1011 | 44 | 21 | LOW | [5 empty] | -4.6 | 8.938 | 33.5 | 12.7 | 49 | OK- No Action Required | 15 | 15 | 1.14 | 30.22
BLW2X465 | 2018-10-30 11:34 | 55.3 | 38.6 | 0.2 | 5.9 | 1011 | 48 | 6 | LOW | [5 empty] | -67.6 | 8.357 | 29.7 | 53.2 | 308 | OK- No Action Required | 40 | 40 | 1.43 | 5.14
BGW2K117 | 2018-10-30 11:38 | 40.8 | 34.6 | 0 | 24.6 | 1011 | 52 | 12 | LOW | [5 empty] | -5 | 6.732 | 24.2 | 22.6 | 96 | OK- No Action Required | 15 | 15 | 1.18 | 24.6
BLW2X464 | 2018-10-30 11:47 | 0.6 | 9 | 15.5 | 74.9 | 1011 | 49 | 0 | LOW | [5 empty] | -65.1 | 0.308 | 20.7 | 4.6 | 0 | Shut/Shut | 0 | 0 | 0.07 | 16.31
BGW2X457 | 2018-10-30 11:50 | 50 | 36.9 | 0 | 13.1 | 1011 | 44 | 19 | LOW | [5 empty] | -9 | 21.529 | 33.8 | 40.3 | 211 | OK- No Action Required | 40 | 40 | 1.36 | 13.1
BGW2K115 | 2018-10-30 12:00 | 16.6 | 26.1 | 0 | 57.3 | 1010 | 40 | 30 | LOW | [5 empty] | 0.1 | 0.105 | 25.7 | 2.7 | 4 | OK- No Action Required | 5 | 5 | 0.64 | 57.3
BLW2X463 | 2018-10-30 12:06 | 0.2 | 2.6 | 19.8 | 77.4 | 1011 | 37 | 2 | LOW | [5 empty] | -56.5 | -0.054 | 22.3 | N/A | N/A | Shut/Shut | 0 | 0 | 0.08 | 2.56
BLW2X462 | 2018-10-30 12:10 | 0.1 | 0 | 20.7 | 79.2 | 1011 | 32 | 0 | LOW | [5 empty] | -58.4 | -0.23 | 21.4 | N/A | N/A | Shut/Shut | 0 | 0 | >>>> | 0.95
BGW2X456 | 2018-10-30 12:15 | 49.5 | 31.8 | 3.6 | 15.1 | 1011 | 45 | 6 | LOW | [5 empty] | 0.2 | 1.56 | 29.6 | 11.1 | 57 | OK- No Action Required | 5 | 2 | 1.56 | 1.49
BLW2X461 | 2018-10-30 12:22 | 54.7 | 37.6 | 1.5 | 6.2 | 1011 | 44 | 6 | LOW | [5 empty] | -60.8 | 8.543 | 28.2 | 88.5 | 507 | OK- No Action Required | 60 | 60 | 1.45 | 0.53
BGW2X249 | 2018-10-30 12:30 | 54.4 | 35.5 | 0 | 10.1 | 1011 | 45 | 25 | LOW | [5 empty] | -2.8 | 8.038 | 27.1 | 25.3 | 144 | OK- No Action Required | 40 | 50 | 1.53 | 10.1
BGW2X160 | 2018-10-30 12:42 | 35.8 | 25.2 | 7.2 | 31.8 | 1010 | 45 | 7 | LOW | [5 empty] | 0 | 7.786 | 25.4 | 1.3 | 5 | Shut/Open | 0 | 2 | 1.42 | 4.58
BGW2X166 | 2018-10-30 12:46 | 46.1 | 36.3 | 0 | 17.6 | 1010 | 41 | 73 | LOW | [5 empty] | 0 | 0.439 | 37.2 | 12.3 | 59 | OK- No Action Required | 15 | 15 | 1.27 | 17.6
BGW2X159 | 2018-10-30 12:53 | 45.8 | 34.9 | 0 | 19.3 | 1010 | 51 | 47 | LOW | [5 empty] | -1.3 | 5.354 | 37 | 20 | 96 | OK- No Action Required | 303 | 30 | 1.31 | 19.3
BGW2X162 | 2018-10-30 12:59 | 40.5 | 32.3 | 0 | 27.2 | 1011 | 46 | 21 | LOW | [5 empty] | -1 | 1.275 | 42.2 | 9.6 | 40 | OK- No Action Required | 30 | 30 | 1.25 | 27.2
BGW2X161 | 2018-10-30 13:03 | 42.1 | 31.7 | 0 | 26.2 | 1011 | 47 | 26 | LOW | [5 empty] | -2.9 | 2.274 | 32.9 | 6.5 | 28 | OK- No Action Required | 15 | 15 | 1.33 | 26.2
BGW2X167 | 2018-10-30 13:07 | 46.3 | 34.2 | 0.1 | 19.4 | 1011 | 59 | 25 | LOW | [5 empty] | -3.8 | 0.647 | 47.9 | 14.7 | 71 | OK- No Action Required | 151 | 15 | 1.35 | 19.02
BGW2X168 | 2018-10-30 13:14 | 51.2 | 36.7 | 0 | 12.1 | 1010 | 57 | 53 | LOW | [5 empty] | -58.76 |  | 34.5 | 0 | 0 | OK- No Action Required | 100 |  | 1.4 | 12.1

## Well Reads
Location | Monitor Class | Section | Asset | Date/Time | Methane | Carbon Dioxide | Oxygen | Balance Gas | Pressure | Vacuum | Atmospheric Pressure | Differential Pressure | LFG Flow | Energy | Valve Position | Temperature | Comments
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-07-31 14:32 | 56.6 | 40.7 | 0 | 2.7 | 0 | 0 | 998 | 22.16 | 2.3 | 13 | 3 | 16.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-07-31 14:31 | 53.4 | 39.6 | 0 | 7 | -1.5 | 1.5 | 998 | -0.365 | 0 | 0 | 25 | 29.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-07-31 14:29 | 60.3 | 41.1 | 0 | 0 | -0.3 | 0.3 | 999 | 6.164 | 11.2 | 70 | 25 | 14.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-07-31 14:26 | 57.3 | 40.8 | 0 | 1.9 | -0.3 | 0.3 | 999 | 21.122 | 10.2 | 61 | 20 | 24.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-07-31 14:24 | 55.6 | 39.7 | 0 | 4.7 | -0.2 | 0.2 | 998 | 2.188 | 6.5 | 38 | 10 | 19.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-07-31 14:20 | 56.5 | 40 | 0 | 3.5 | -0.2 | 0.2 | 998 | 19.853 | 10 | 59 | 12 | 17.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-07-31 14:18 | 42 | 36 | 0 | 22 | 0 | 0 | 997 | 2.396 | 3.4 | 15 | 5 | 17.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-07-31 14:15 | 48.1 | 39.1 | 0.7 | 12.1 | -0.2 | 0.2 | 998 | 2.08 | 12.5 | 63 | 25 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-07-31 14:14 | 59.2 | 42.9 | 0 | 0 | -0.1 | 0.1 | 998 | 1.229 | 10 | 62 | 12 | 15.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-07-31 14:12 | 48 | 37.7 | 0.8 | 13.5 | 0 | 0 | 998 | 1.854 | 12 | 60 | 15 | 21.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-07-31 14:10 | 60.1 | 41.9 | 0 | 0 | -52.1 | 52.1 | 997 | 3.697 | 16.9 | 106 | 45 | 17.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-07-31 14:08 | 50.7 | 39.7 | 1.1 | 8.5 | -2.1 | 2.1 | 996 | 3.359 | 4.1 | 21 | 15 | 17.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-07-31 14:05 | 57.9 | 40.7 | 0.6 | 0.8 | -1 | 1 | 996 | 2.299 | 29.3 | 178 | 25 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-07-31 14:03 | 58.1 | 42.7 | 0 | 0 | 0 | 0 | 997 | 19.96 | 10 | 61 | 5 | 16.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-07-31 14:01 | 52.1 | 38.2 | 0.1 | 9.6 | 0 | 0 | 998 | 20.566 | 10.2 | 56 | 5 | 15.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-07-31 13:57 | 51.5 | 38.3 | 0 | 10.2 | -0.6 | 0.6 | 998 | 5.418 | 5.2 | 28 | 25 | 17.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-07-31 13:31 | 49.4 | 39.2 | 0.1 | 11.3 | -0.4 | 0.4 | 999 | 1.048 | 9 | 46 | 15 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-07-31 13:27 | 56.2 | 39.1 | 0 | 4.7 | 0 | 0 | 998 | 3.978 | 8.8 | 52 | 20 | 20.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-07-31 13:23 | 43.3 | 36.7 | 0 | 20 | -2.6 | 2.6 | 998 | 4.181 | 17.7 | 80 | 25 | 28.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-07-31 13:21 | 47.6 | 37.6 | 0 | 14.8 | -1.1 | 1.1 | 998 | 1.487 | 10.7 | 53 | 15 | 20.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-07-31 13:17 | 58.8 | 43.5 | 1 | 0 | -60.2 | 60.2 | 999 | 0.072 | 5 | 31 | 25 | 17.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-07-31 13:11 | 7.2 | 5.9 | 17.6 | 69.3 | -0.1 | 0.1 | 999 | 0.012 | 0.9 | 0 | 0 | 15.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-07-31 13:10 | 12.9 | 13.5 | 11 | 62.6 | -4.8 | 4.8 | 999 | 1.19 | 0.5 | 0 | 5 | 15.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-07-31 13:07 | 39.9 | 30.7 | 6.2 | 23.2 | -4 | 4 | 999 | 0.952 | 2.1 | 9 | 10 | 18.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-07-31 13:05 | 46.7 | 37.4 | 0 | 15.9 | -3.8 | 3.8 | 999 | 3.277 | 33.7 | 164 | 40 | 33.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-07-31 13:03 | 61.4 | 42.3 | 0 | 0 | -0.1 | 0.1 | 999 | 3.496 | 4.2 | 27 | 10 | 17 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-07-31 12:58 | 57.2 | 40.1 | 0 | 2.7 | -49.7 | 49.7 | 1000 | 23.421 | 146.1 | 875 | 90 | 32.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-07-31 12:54 | 59.2 | 42.1 | 0 | 0 | -0.5 | 0.5 | 1000 | 0.048 | 1.9 | 12 | 10 | 18.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-07-31 12:52 | 60.9 | 39.9 | 0 | 0 | -0.2 | 0.2 | 1000 | 0.101 | 2.9 | 18 | 5 | 16.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-07-31 12:50 | 44.4 | 36.2 | 0.1 | 19.3 | -5.6 | 5.6 | 1000 | 3.307 | 15.9 | 74 | 30 | 22.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-07-31 12:48 | 48 | 37 | 0 | 15 | -0.3 | 0.3 | 1000 | 2.399 | 6.8 | 34 | 20 | 19.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-07-31 12:41 | 57.2 | 36.1 | 1.4 | 5.3 | -0.2 | 0.2 | 1001 | 2.825 | 15 | 89 | 10 | 30.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-07-31 11:48 | 47.5 | 36 | 0.3 | 16.2 | -16.2 | 16.2 | 1000 | 10.786 | 28.6 | 142 | 42 | 26.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-07-31 11:46 | 45.3 | 32.1 | 3.9 | 18.7 | 0 | 0 | 999 | 0.096 | 2.7 | 13 | 10 | 16.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y482 | 2018-07-31 11:40 | 46.9 | 39.2 | 0 | 13.9 | -0.6 | 0.6 | 1000 | 7.774 | 24.2 | 119 | 42 | 26.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y481 | 2018-07-31 11:38 | 18 | 29.4 | 0 | 52.6 | 0 | 0 | 999 | 0.08 | 2.4 | 4 | 5 | 15.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y483 | 2018-07-31 11:36 | 1.5 | 4.9 | 16.6 | 77 | -0.2 | 0.2 | 1000 | 1.893 | 12 | 1 | 10 | 16 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-07-31 11:34 | 52.5 | 38.6 | 0.3 | 8.6 | -4.7 | 4.7 | 1001 | 2.94 | 14.6 | 80 | 20 | 43.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-07-31 11:28 | 50.4 | 37.3 | 1.1 | 11.2 | 0.1 | -0.1 | 1001 | 1.014 | 4.4 | 23 | 10 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-07-31 11:26 | 50.8 | 35.1 | 1.9 | 12.2 | -2.5 | 2.5 | 1001 | 4.932 | 42.2 | 224 | 40 | 30.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-07-31 11:23 | 59.4 | 40.1 | 0.2 | 0.3 | -0.3 | 0.3 | 1001 | >>>> | 0 | 0 | 10 | 16.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-07-31 11:21 | 52.5 | 38.5 | 0 | 9 | -31.7 | 31.7 | 1002 | 9.795 | 58.4 | 321 | 80 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-07-31 11:10 | 30.1 | 26.9 | 1.6 | 41.4 | -44.1 | 44.1 | 1002 | 0.878 | 17.5 | 55 | 30 | 14.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-07-31 11:08 | 51.5 | 37.8 | 1 | 9.7 | -0.8 | 0.8 | 1002 | 0.128 | 11.3 | 61 | 30 | 17.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-07-31 11:05 | 44.2 | 35.2 | 0.8 | 19.8 | -5.8 | 5.8 | 1002 | -0.025 | 0 | 0 | 10 | 14.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-07-31 11:02 | 56.7 | 40 | 0.2 | 3.1 | 0 | 0 | 1002 | 0.078 | 2.5 | 15 | 10 | 14.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-07-31 11:00 | 39.9 | 31.3 | 0 | 28.8 | -0.8 | 0.8 | 1002 | 0.03 | 0.7 | 3 | 5 | 14 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-07-31 10:59 | 31.5 | 26.8 | 0.2 | 41.5 | -0.4 | 0.4 | 1002 | 2.876 | 0.8 | 2 | 8 | 14.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-07-31 10:56 | 61.9 | 38.9 | 0 | 0 | -48.8 | 48.8 | 1002 | 0.597 | 6.9 | 44 | 40 | 15.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-07-31 10:54 | 41.1 | 30.9 | 0 | 28 | -11.5 | 11.5 | 1002 | 2.026 | 27.2 | 117 | 45 | 18.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-07-31 10:52 | 4.6 | 6.4 | 13.1 | 75.9 | -0.2 | 0.2 | 1003 | 0.066 | 1.1 | 0 | 2 | 15.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-07-31 10:41 | 42.2 | 34.1 | 0 | 23.7 | -0.6 | 0.6 | 1003 | 5.4 | 10.1 | 44 | 15 | 23.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2018-07-26 13:34 | 61.9 | 42.2 | 0 | 0 | -33.5 | 33.5 | 1008 | 12.4 | 107.4 | 697 | 99 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2018-07-26 13:33 | 61.7 | 42.5 | 0 | 0 | -44.1 | 44.1 | 1008 | -0.14 | 0 | 0 | 99 | 23.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2018-07-26 13:32 | 58.7 | 41.4 | 0 | 0 | -30.2 | 30.2 | 1008 | 20.8 | 140 | 860 | 99 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2018-07-26 13:31 | 60.1 | 42.5 | 0 | 0 | -32.7 | 32.7 | 1008 | 17.35 | 126.9 | 799 | 99 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2018-07-26 13:28 | 57.2 | 38.5 | 0 | 4.3 | -5.8 | 5.8 | 1008 | 3.82 | 17.4 | 104 | 28 | 25.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2018-07-26 13:26 | 50.4 | 36.5 | 0 | 13.1 | -0.2 | 0.2 | 1008 | 2.3 | 13.4 | 70 | 20 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2018-07-26 13:24 | 55.6 | 37.9 | 0 | 6.5 | -0.2 | 0.2 | 1008 | 2.05 | 12.7 | 74 | 25 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2018-07-26 13:22 | 51.1 | 36.7 | 0 | 12.2 | -1.7 | 1.7 | 1008 | 8.79 | 26.2 | 140 | 40 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2018-07-26 13:20 | 33.8 | 26.9 | 3.9 | 35.4 | 0 | 0 | 1008 | 0.21 | 4 | 14 | 10 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2018-07-26 13:18 | 47.3 | 34.3 | 0.7 | 17.7 | 0 | 0 | 1009 | 1.38 | 10.4 | 51 | 25 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-07-26 13:09 | 45.2 | 35.4 | 0 | 19.4 | -2.1 | 2.1 | 1007 | 4.34 | 18.2 | 86 | 15 | 26.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-07-26 13:08 | 47.1 | 35.3 | 0.4 | 17.2 | -19.9 | 19.9 | 1007 | 16.21 | 35 | 173 | 30 | 27.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-07-26 13:05 | 45.4 | 31.9 | 3.7 | 19 | -0.4 | 0.4 | 1007 | 0.78 | 7.9 | 37 | 5 | 17.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2018-07-26 12:08 | 41.2 | 34.2 | 0 | 24.6 | -4.3 | 4.3 | 1008 | 8.96 | 12.7 | 55 | 10 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2018-07-26 12:06 | 0.2 | 0.1 | 20.4 | 79.3 | -64.7 | 64.7 | 1008 | -0.03 | 0 | 0 | 0 | 25.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2018-07-26 12:05 | 0.2 | 0.1 | 20.2 | 79.5 | -64.6 | 64.6 | 1009 | -0.14 | 0 | 0 | 0 | 23.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2018-07-26 12:03 | 0.6 | 0.4 | 20.1 | 78.9 | -65.6 | 65.6 | 1009 | -0.04 | 0 | 0 | 0 | 24.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-07-26 12:02 | 58.8 | 39.8 | 0.1 | 1.3 | -69.2 | 69.2 | 1008 | 26.27 | 44.4 | 273 | 40 | 23 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2018-07-26 12:00 | 45.9 | 36 | 0 | 18.1 | -4.5 | 4.5 | 1008 | 6.74 | 23 | 110 | 25 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2018-07-26 11:57 | 50.2 | 37.2 | 0 | 12.6 | -0.1 | 0.1 | 1009 | 0.08 | 2.5 | 13 | 5 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2018-07-26 11:55 | 55.2 | 38.3 | 0 | 6.5 | -8.2 | 8.2 | 1009 | 21.47 | 40.5 | 234 | 50 | 34 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-07-26 11:52 | 42.6 | 27.9 | 5.8 | 23.7 | -0.4 | 0.4 | 1009 | 3.3 | 16 | 71 | 12 | 29.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2018-07-26 11:50 | 0.1 | 0.1 | 20.5 | 79.3 | -65.6 | 65.6 | 1009 | -0.09 | 0 | 0 | 0 | 22.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-07-26 11:49 | 0.1 | 0 | 20.5 | 79.4 | -65.2 | 65.2 | 1009 | 0.02 | 3.7 | 0 | 5 | 21.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2018-07-26 11:47 | 50.2 | 34.8 | 3.1 | 11.9 | -66.2 | 66.2 | 1010 | 3.17 | 54.3 | 286 | 99 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-07-26 11:44 | 0.1 | 0.1 | 20.7 | 79.1 | -66.8 | 66.8 | 1007 | -0.02 | 0 | 0 | 99 | 18.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2018-07-26 11:37 | 60 | 43.5 | 0 | 0 | -62.1 | 62.1 | 1007 | 0.61 | 23.4 | 147 | 99 | 29.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2018-07-26 11:35 | 57.8 | 41.8 | 0.2 | 0.2 | 0 | 0 | 1007 | -0.03 | 0 | 0 | 0 | 23.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2018-07-26 11:34 | 60.2 | 43.8 | 0 | 0 | -59.2 | 59.2 | 1007 | 1.87 | 11.6 | 73 | 99 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2018-07-26 11:33 | 56.8 | 39.9 | 1.3 | 2 | -62.6 | 62.6 | 1007 | 0.15 | 3.3 | 20 | 99 | 16.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2018-07-26 11:32 | 51.1 | 37.6 | 0 | 11.3 | -40.4 | 40.4 | 1007 | 8.36 | 54.6 | 292 | 50 | 18.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2018-07-26 11:30 | 61.2 | 43 | 0 | 0 | -61.9 | 61.9 | 1007 | 0.38 | 5.3 | 34 | 99 | 20.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2018-07-26 11:29 | 0.2 | 2.8 | 18.7 | 78.3 | -2.6 | 2.6 | 1007 | -0.02 | 0 | 0 | 0 | 29.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2018-07-26 11:28 | 48.7 | 37.2 | 0.4 | 13.7 | -23.5 | 23.5 | 1007 | 4.71 | 39.6 | 202 | 40 | 41.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2018-07-26 11:26 | 48.3 | 37.3 | 0 | 14.4 | -60.7 | 60.7 | 1007 | 3.74 | 56.9 | 288 | 99 | 38.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-07-26 11:25 | 51.8 | 40 | 0.2 | 8 | -0.6 | 0.6 | 1007 | 1.44 | 10.2 | 55 | 40 | 41.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y482 | 2018-07-26 10:54 | 44.8 | 38.4 | 0 | 16.8 | -1.6 | 1.6 | 1008 | 8.95 | 26 | 122 | 25 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y480 | 2018-07-26 10:53 | 54.8 | 41.3 | 0 | 3.9 | -1.4 | 1.4 | 1008 | 5.33 | 20.4 | 117 | 25 | 22.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y481 | 2018-07-26 10:52 | 14 | 28.2 | 0 | 57.8 | -0.4 | 0.4 | 1008 | 0.81 | 7.7 | 11 | 5 | 15.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y478 | 2018-07-26 10:50 | 51.3 | 40 | 0 | 8.7 | -0.9 | 0.9 | 1008 | 0.63 | 7.1 | 38 | 10 | 15.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y483 | 2018-07-26 10:49 | 1 | 5 | 16.6 | 77.4 | -0.4 | 0.4 | 1008 | 0.17 | 3.6 | 0 | 2 | 15.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2018-07-26 10:47 | 57.4 | 41.1 | 0 | 1.5 | -38.4 | 38.4 | 1008 | 29.51 | 167.6 | 1007 | 99 | 21.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-07-26 10:46 | 48.8 | 36.9 | 0.6 | 13.7 | -1.8 | 1.8 | 1008 | 2.8 | 14.3 | 73 | 15 | 44 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2018-07-26 10:41 | 0.7 | 0.7 | 19.8 | 78.8 | -8.3 | 8.3 | 1008 | -0.04 | 0 | 0 | 0 | 16.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2018-07-26 10:40 | 0.4 | 0.4 | 19.2 | 80 | -19.4 | 19.4 | 1008 | -1.1 | 0 | 0 | 0 | 24.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2018-07-26 10:38 | 57.9 | 42.1 | 0 | 0 | -39.4 | 39.4 | 1008 | 28.09 | 157.2 | 954 | 99 | 44.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2018-07-26 10:37 | 19.9 | 27.6 | 4.5 | 48 | -0.1 | 0.1 | 1009 | 0 | 0 | 0 | 5 | 17.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2018-07-26 10:33 | 60.6 | 39 | 0.4 | 0 | -16.7 | 16.7 | 1009 | 0.1 | 6.1 | 39 | 10 | 19 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2018-07-26 10:32 | 47.7 | 35.6 | 0 | 16.7 | -12.5 | 12.5 | 1009 | 19.33 | 38.1 | 190 | 50 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-07-26 10:30 | 51.3 | 36.5 | 0 | 12.2 | -10.1 | 10.1 | 1010 | 18.63 | 80.8 | 434 | 60 | 36 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-07-26 10:29 | 47.1 | 36.4 | 0 | 16.5 | -3 | 3 | 1009 | 12.87 | 30.6 | 151 | 40 | 42.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-07-26 10:28 | 51.1 | 38.6 | 0 | 10.3 | -41.9 | 41.9 | 1009 | 22.86 | 86.2 | 462 | 99 | 45.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2018-07-26 10:26 | 23.7 | 27.8 | 0 | 48.5 | -58.3 | 58.3 | 1009 | 0.3 | 9.7 | 24 | 99 | 34.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-07-26 10:25 | 2.8 | 21 | 0 | 76.2 | -1.5 | 1.5 | 1009 | -0.22 | 0 | 0 | 5 | 28.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2018-07-26 10:24 | 62.9 | 39.8 | 0 | 0 | -44.1 | 44.1 | 1009 | 6.76 | 22.7 | 150 | 99 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2018-07-26 10:22 | 53.1 | 37 | 0 | 9.9 | -24.6 | 24.6 | 1009 | 7.42 | 50.9 | 283 | 40 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-07-26 10:21 | 50.5 | 37.6 | 0.2 | 11.7 | -3.3 | 3.3 | 1009 | 13.57 | 32.7 | 173 | 40 | 20.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-07-26 10:19 | 55.3 | 39.7 | 0.1 | 4.9 | -22 | 22 | 1009 | 15.77 | 33.9 | 196 | 40 | 42.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-07-26 09:31 | 36 | 29 | 4.4 | 30.6 | -0.5 | 0.5 | 1009 | 4.39 | 9 | 34 | 15 | 26.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-07-26 09:29 | 47.3 | 33.3 | 3.1 | 16.3 | -3.5 | 3.5 | 1009 | 6.32 | 47.4 | 235 | 40 | 31.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-07-26 09:26 | 25.2 | 18.2 | 13.3 | 43.3 | -60.6 | 60.6 | 1009 | -0.15 | 0 | 0 | 50 | 18.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P477 | 2018-07-26 09:25 | 53.2 | 39.4 | 0 | 7.4 | -4 | 4 | 1009 | 3.69 | 36.3 | 202 | 40 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-07-26 09:24 | 48.1 | 37.2 | 0.2 | 14.5 | -32.9 | 32.9 | 1009 | 5.39 | 42.5 | 214 | 50 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-07-26 09:22 | 59.1 | 39.8 | 0.2 | 0.9 | -0.3 | 0.3 | 1009 | 22.08 | 2.3 | 14 | 12 | 16 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2018-07-26 09:20 | 44 | 36 | 0 | 20 | -1.9 | 1.9 | 1009 | 1.73 | 5.7 | 26 | 10 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2018-07-26 09:18 | 62 | 40.4 | 0 | 0 | -60.4 | 60.4 | 1009 | 0.77 | 27.4 | 178 | 99 | 16.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2018-07-26 09:17 | 0.3 | 0.3 | 20.5 | 78.9 | -41 | 41 | 1009 | 0.95 | 0.4 | 0 | 0 | 15.1 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-07-26 09:15 | 55.6 | 38.4 | 0 | 6 | -4.8 | 4.8 | 1009 | 7.76 | 24.9 | 145 | 25 | 20.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-07-26 09:14 | 39.9 | 28.7 | 5.9 | 25.5 | -1 | 1 | 1009 | 1.22 | 21.1 | 88 | 20 | 21.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2018-07-26 09:12 | 54.5 | 40.2 | 0 | 5.3 | -0.7 | 0.7 | 1009 | 1.74 | 11.5 | 66 | 25 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2018-07-26 09:10 | 54 | 38.8 | 0 | 7.2 | -31.2 | 31.2 | 1008 | 9.56 | 94.7 | 536 | 80 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-07-26 09:08 | 21 | 19.2 | 10 | 49.8 | -0.9 | 0.9 | 1008 | 0.63 | 6.8 | 15 | 0 | 31.8 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2018-07-26 09:06 | 48.2 | 39 | 0 | 12.8 | -37.1 | 37.1 | 1008 | 30.54 | 162.2 | 819 | 99 | 44.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-07-26 09:05 | 11.4 | 13.5 | 11.7 | 63.4 | -8.5 | 8.5 | 1008 | 11.06 | 1.6 | 1 | 5 | 13.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-07-26 09:02 | 44.5 | 33.5 | 5.2 | 16.8 | -6.6 | 6.6 | 1009 | 19.32 | 9.8 | 45 | 10 | 18.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2018-07-26 09:00 | 48 | 38.5 | 0 | 13.5 | -3.2 | 3.2 | 1009 | 1.46 | 22.4 | 112 | 20 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-07-26 08:59 | 45.6 | 37.4 | 0 | 17 | -4.9 | 4.9 | 1008 | 3.3 | 34.4 | 164 | 25 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-07-26 08:49 | 48 | 36.7 | 2.3 | 13 | -0.2 | 0.2 | 1008 | 3.7 | 8.4 | 42 | 15 | 19.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2018-07-26 08:47 | 51.7 | 37.8 | 0 | 10.5 | -7.6 | 7.6 | 1008 | 5.23 | 43.6 | 236 | 40 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2018-07-26 08:46 | 50.2 | 38.4 | 0 | 11.4 | -61.2 | 61.2 | 1008 | 0.45 | 12.3 | 65 | 70 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-07-26 08:44 | 51.6 | 37.7 | 0.5 | 10.2 | -3 | 3 | 1008 | 1.03 | 19.8 | 107 | 25 | 10.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-07-26 08:43 | 39.3 | 29.6 | 5.1 | 26 | -0.2 | 0.2 | 1009 | 4.56 | 4.7 | 19 | 5 | 17.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-07-26 08:41 | 37.9 | 34.6 | 0 | 27.5 | -0.6 | 0.6 | 1008 | 7 | 5.7 | 22 | 10 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-07-25 15:55 | 38.1 | 34.1 | 1.3 | 26.5 | -1.4 | 1.4 | 1004 | 3.18 | 15.3 | 61 | 22 | 29.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2018-07-25 15:53 | 47.5 | 38 | 0 | 14.5 | -2.6 | 2.6 | 1004 | 1.27 | 10 | 50 | 25 | 14.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-07-25 15:52 | 47.1 | 36.5 | 2.5 | 13.9 | -0.2 | 0.2 | 1004 | 1.53 | 11 | 54 | 15 | 14.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-07-25 15:50 | 28.4 | 27.5 | 3.8 | 40.3 | -0.5 | 0.5 | 1004 | 3.47 | 16.2 | 48 | 15 | 22.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-07-25 15:48 | 21.5 | 15.4 | 11.4 | 51.7 | -62.8 | 62.8 | 1004 | 0.13 | 3.1 | 7 | 40 | 17.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-07-25 15:47 | 46.6 | 36.1 | 0.3 | 17 | -1.3 | 1.3 | 1004 | 0.35 | 18.5 | 90 | 25 | 22.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2018-07-25 15:46 | 50.3 | 39 | 0.7 | 10 | -0.8 | 0.8 | 1004 | 3.07 | 7.7 | 40 | 15 | 19.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2018-07-25 15:44 | 51.2 | 37.7 | 0.4 | 10.7 | -4.8 | 4.8 | 1004 | 9.64 | 27.1 | 145 | 25 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2018-07-25 15:35 | 51.4 | 36.2 | 2.8 | 9.6 | -12.8 | 12.8 | 1003 | 0.05 | 2 | 11 | 5 | 16.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2018-07-25 15:34 | 59.5 | 42.9 | 0 | 0 | -0.4 | 0.4 | 1003 | 0 | 0 | 0 | 5 | 27.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2018-07-25 15:33 | 55.3 | 40.1 | 0 | 4.6 | -1.5 | 1.5 | 1003 | 10.42 | 28.3 | 164 | 25 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-07-25 15:31 | 41.1 | 35.2 | 0 | 23.7 | -0.1 | 0.1 | 1003 | 6.53 | 11 | 47 | 15 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-07-25 15:30 | 45.4 | 37.4 | 1 | 16.2 | -3.9 | 3.9 | 1003 | 3.69 | 4.2 | 20 | 5 | 17.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2018-07-25 15:27 | 49.3 | 40 | 0 | 10.7 | -46.8 | 46.8 | 1003 | 7.85 | 23 | 118 | 60 | 49.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2018-07-25 15:26 | 53 | 39.6 | 1.2 | 6.2 | -2.4 | 2.4 | 1003 | 0.05 | 4.2 | 23 | 20 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2018-07-25 15:25 | 54.1 | 40.9 | 0 | 5 | -19.1 | 19.1 | 1003 | 16.05 | 33.9 | 192 | 40 | 45 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-07-25 15:23 | 55.7 | 41.3 | 1.1 | 1.9 | -45.9 | 45.9 | 1004 | 4.13 | 4.4 | 25 | 25 | 22.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2018-07-25 15:22 | 0.7 | 0.6 | 20.3 | 78.4 | -1.6 | 1.6 | 1003 | 0 | 0 | 0 | 0 | 15.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-07-25 15:19 | 58.1 | 41.1 | 0 | 0.8 | -66.4 | 66.4 | 1003 | -0.01 | 0 | 0 | 40 | 22.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2018-07-25 15:18 | 38.9 | 30.9 | 4.6 | 25.6 | -1.3 | 1.3 | 1003 | 6.5 | 22.3 | 91 | 22 | 24.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-07-25 15:16 | 45.2 | 36.8 | 0.6 | 17.4 | -0.6 | 0.6 | 1003 | 15.3 | 8.6 | 41 | 12 | 23 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2018-07-25 15:14 | 54.2 | 40.5 | 0 | 5.3 | -64.3 | 64.3 | 1003 | 2.49 | 46.4 | 264 | 99 | 39.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2018-07-25 15:13 | 53.5 | 39.7 | 0 | 6.8 | -18.9 | 18.9 | 1003 | 9.94 | 58.8 | 330 | 50 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2018-07-25 15:11 | 58.4 | 42 | 0 | 0 | -40.1 | 40.1 | 1003 | 18.45 | 37.5 | 229 | 99 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-07-25 15:10 | 29.8 | 31.6 | 0 | 38.6 | -0.1 | 0.1 | 1003 | 22.13 | 10.2 | 32 | 15 | 21.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-07-25 15:09 | 44.9 | 32.9 | 4.5 | 17.7 | -1.3 | 1.3 | 1003 | 1.8 | 25.7 | 121 | 30 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2018-07-25 15:07 | 51.2 | 38.8 | 0.2 | 9.8 | -32.8 | 32.8 | 1003 | 1.75 | 41.1 | 220 | 50 | 15.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-07-25 15:06 | 36 | 31.7 | 1.7 | 30.6 | -0.3 | 0.3 | 1003 | 6.71 | 5.7 | 21 | 5 | 15.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-07-25 15:04 | 9.8 | 7.2 | 16.8 | 66.2 | -0.2 | 0.2 | 1003 | 15.84 | 8.8 | 9 | 5 | 15.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2018-07-25 15:02 | 50.4 | 39.1 | 0 | 10.5 | -0.2 | 0.2 | 1003 | 1.7 | 11.3 | 60 | 20 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L101 | 2018-07-25 15:01 | 1.5 | 1.1 | 19.9 | 77.5 | -0.1 | 0.1 | 1003 | 0 | 0 | 0 | 0 | 17.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-07-25 15:00 | 59.5 | 43.7 | 0 | 0 | -38.5 | 38.5 | 1003 | 0.87 | 2 | 12 | 5 | 22.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-07-25 14:58 | 50.3 | 39.7 | 0 | 10 | -0.8 | 0.8 | 1003 | 2.89 | 14.4 | 76 | 15 | 46.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2018-07-25 14:57 | 55.1 | 39.4 | 0 | 5.5 | -46.1 | 46.1 | 1003 | 12.26 | 103.2 | 596 | 80 | 47.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-07-25 14:55 | 48.8 | 38.3 | 0 | 12.9 | -1 | 1 | 1003 | 7.72 | 11.8 | 60 | 25 | 40.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-07-25 14:54 | 46.7 | 36.7 | 0.2 | 16.4 | -0.7 | 0.7 | 1004 | 0.61 | 14.6 | 71 | 15 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2018-07-25 14:52 | 38.6 | 34.2 | 2.2 | 25 | 0 | 0 | 1004 | -4.95 | 0 | 0 | 5 | 13.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-07-25 11:49 | 63.2 | 43.9 | 0 | 0 | -70.2 | 70.2 | 1005 | 3.82 | 36 | 239 | 99 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-07-25 11:47 | 62.1 | 45.5 | 0 | 0 | -69 | 69 | 1005 | 6.75 | 47.7 | 310 | 99 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-07-25 11:46 | 62.5 | 46.2 | 0 | 0 | -58.1 | 58.1 | 1005 | 22.41 | 88.5 | 580 | 99 | 19 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2018-07-25 11:45 | 48.3 | 43.4 | 0 | 8.3 | -7.9 | 7.9 | 1005 | 9 | 56.4 | 285 | 50 | 17.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2018-07-25 11:44 | 58.1 | 47 | 0 | 0 | -75.3 | 75.3 | 1005 | -0.07 | 0 | 0 | 99 | 17.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2018-07-25 11:40 | 49 | 37.7 | 1.3 | 12 | -45 | 45 | 1005 | 18.48 | 76.2 | 391 | 99 | 53 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2018-07-25 11:38 | 59.8 | 42.3 | 0 | 0 | -51.8 | 51.8 | 1005 | 7.8 | 50.6 | 317 | 99 | 44.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2018-07-25 11:37 | 57.9 | 41.7 | 0.2 | 0.2 | -50.9 | 50.9 | 1005 | 8.33 | 85.2 | 517 | 99 | 44.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2018-07-25 11:36 | 42 | 33.1 | 2 | 22.9 | -3.4 | 3.4 | 1005 | -3.32 | 0 | 0 | 0 | 32.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-07-25 11:34 | 41.2 | 32.3 | 4.9 | 21.6 | -27.7 | 27.7 | 1005 | -1.21 | 0 | 0 | 15 | 46.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-07-25 11:32 | 61.4 | 42.8 | 0 | 0 | -59.9 | 59.9 | 1005 | 0.37 | 11.1 | 71 | 99 | 37.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2018-07-25 11:31 | 0.4 | 0.3 | 20.3 | 79 | -52.2 | 52.2 | 1005 | 0.07 | 2.2 | 0 | 0 | 16.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-07-25 11:30 | 47.1 | 38.6 | 0.5 | 13.8 | -1 | 1 | 1005 | 1.02 | 8.9 | 44 | 20 | 17.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-07-25 11:28 | 46.8 | 36.4 | 2.1 | 14.7 | -26.4 | 26.4 | 1005 | 0.7 | 15.2 | 74 | 50 | 41.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-07-25 11:27 | 53.6 | 41.7 | 0 | 4.7 | -58.3 | 58.3 | 1005 | 4.63 | 38.5 | 216 | 99 | 41.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2018-07-25 11:26 | 0.2 | 0.1 | 20.9 | 78.8 | -22.1 | 22.1 | 1005 | -0.06 | 0 | 0 | 0 | 17.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2018-07-25 11:25 | 0.3 | 0.2 | 20.3 | 79.2 | 0 | 0 | 1005 | -0.1 | 0 | 0 | 0 | 17.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2018-07-25 11:24 | 20.6 | 14.2 | 18.1 | 47.1 | -55.4 | 55.4 | 1005 | -0.07 | 0 | 0 | 0 | 20.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2018-07-25 11:22 | 60.1 | 41.8 | 0 | 0 | -60.6 | 60.6 | 1005 | 1.87 | 40.8 | 257 | 99 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2018-07-25 11:21 | 49.3 | 37.9 | 0 | 12.8 | -5.5 | 5.5 | 1005 | 8.99 | 26.6 | 137 | 25 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-07-25 11:20 | 45.2 | 35.9 | 0.5 | 18.4 | -2.9 | 2.9 | 1005 | 4.22 | 18.1 | 86 | 15 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-07-25 11:18 | 47.7 | 37.4 | 0.6 | 14.3 | -6.2 | 6.2 | 1005 | 1.4 | 22.6 | 113 | 25 | 16.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-07-25 11:17 | 55.4 | 40.6 | 0 | 4 | -2.8 | 2.8 | 1005 | 1.58 | 24.1 | 140 | 25 | 19.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2018-07-25 10:33 | 46.4 | 35.8 | 0 | 17.8 | -2.7 | 2.7 | 1006 | 4.2 | 9 | 43 | 10 | 18.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-07-25 10:32 | 52.3 | 35.5 | 0 | 12.2 | -1 | 1 | 1006 | 0.57 | 14.8 | 81 | 10 | 14.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-07-25 10:30 | 49.5 | 36.4 | 3.1 | 11 | -0.8 | 0.8 | 1006 | 0.15 | 3.4 | 17 | 12 | 17.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-07-25 10:29 | 12.4 | 8.8 | 16.2 | 62.6 | -67.3 | 67.3 | 1006 | -0.07 | 0 | 0 | 99 | 16.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-07-25 10:27 | 46 | 31.7 | 4.6 | 17.7 | -0.2 | 0.2 | 1006 | 0.06 | 2.2 | 10 | 5 | 16.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-07-25 10:26 | 45.6 | 36.3 | 0 | 18.1 | -6.5 | 6.5 | 1006 | 4.09 | 17.8 | 85 | 25 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-07-25 10:24 | 43.3 | 35.5 | 2 | 19.2 | -0.7 | 0.7 | 1006 | 3.56 | 8.2 | 37 | 22 | 17.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2018-07-25 10:22 | 0.3 | 0.3 | 20.7 | 78.7 | -0.2 | 0.2 | 1006 | 0.05 | 2 | 0 | 0 | 15.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2018-07-25 10:21 | 45.9 | 33.1 | 0 | 21 | -0.8 | 0.8 | 1006 | 2.07 | 12.9 | 62 | 15 | 14.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-07-25 10:20 | 10.8 | 6.6 | 17 | 65.6 | 0 | 0 | 1006 | 0 | 0 | 0 | 0 | 16.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-07-25 10:19 | 53.9 | 38.6 | 0.7 | 6.8 | -11.7 | 11.7 | 1006 | 4.36 | 18.6 | 105 | 25 | 18.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2018-07-25 10:17 | 51.3 | 40 | 0.2 | 8.5 | -1 | 1 | 1007 | 1.32 | 10.1 | 54 | 20 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2018-07-25 10:15 | 44.3 | 36.4 | 0 | 19.3 | -0.5 | 0.5 | 1007 | 0.4 | 11.7 | 54 | 15 | 29.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2018-07-25 10:13 | 45.9 | 35.9 | 0 | 18.2 | -1.8 | 1.8 | 1007 | 5.72 | 20.6 | 99 | 20 | 36 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2018-07-25 10:10 | 0.2 | 0.1 | 20.7 | 79 | -0.4 | 0.4 | 1007 | 0.25 | 0.2 | 0 | 0 | 13.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2018-07-25 10:06 | 48 | 34.8 | 0 | 17.2 | -4 | 4 | 1007 | 2.04 | 6.2 | 31 | 15 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2018-07-25 10:04 | 50.2 | 36.2 | 0 | 13.6 | -1.6 | 1.6 | 1007 | 1.39 | 10.6 | 56 | 20 | 15.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2018-07-25 10:02 | 50.8 | 37.7 | 0.1 | 11.4 | -4.8 | 4.8 | 1007 | 1.49 | 22.4 | 119 | 30 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-07-25 09:59 | 60.4 | 41.2 | 0 | 0 | -55.1 | 55.1 | 1007 | 0.29 | 10.2 | 64 | 99 | 14.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-07-25 09:57 | 55.2 | 36.7 | 0.1 | 8 | -3.6 | 3.6 | 1007 | 1 | 9.1 | 52 | 15 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2018-07-25 09:56 | 1.4 | 6.7 | 18.7 | 73.2 | 0 | 0 | 1007 | -0.02 | 0 | 0 | 0 | 13.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-07-25 09:55 | 31.1 | 28.1 | 1.6 | 39.2 | -49.9 | 49.9 | 1007 | 1.04 | 19 | 62 | 20 | 14.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-07-25 09:53 | 0.2 | 0.2 | 21 | 78.6 | -8.7 | 8.7 | 1007 | 0.14 | 0.1 | 0 | 5 | 15.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-07-25 09:52 | 48.5 | 36.3 | 1.8 | 13.4 | -1.8 | 1.8 | 1007 | 0.3 | 17.2 | 87 | 17 | 17.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-07-25 09:50 | 59.6 | 40.3 | 4.9 | 0 | 0 | 0 | 1007 | 0.05 | 2 | 12 | 0 | 25.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2018-07-25 09:49 | 60.2 | 41.7 | 0 | 0 | -43.1 | 43.1 | 1007 | 8.94 | 55.3 | 349 | 99 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-07-25 09:47 | 48.8 | 36 | 0 | 15.2 | -15.1 | 15.1 | 1007 | 0.47 | 12.9 | 66 | 20 | 22.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-07-25 09:46 | 34.9 | 31 | 2.4 | 31.7 | -5.2 | 5.2 | 1007 | 0.08 | 2.5 | 9 | 7 | 14.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-07-25 09:44 | 58.2 | 40.3 | 0 | 1.5 | 0 | 0 | 1007 | 0.11 | 3 | 18 | 10 | 14.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-07-25 09:41 | 51 | 37.5 | 0 | 11.5 | -4.7 | 4.7 | 1007 | 4.07 | 39 | 208 | 40 | 15.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-07-25 09:40 | 35.2 | 28.8 | 2.6 | 33.4 | -1.9 | 1.9 | 1007 | 0.1 | 1.3 | 5 | 2 | 14.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-07-25 09:38 | 25 | 24.5 | 0.7 | 49.8 | -1.1 | 1.1 | 1007 | 6.12 | 1.2 | 3 | 5 | 14.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-07-25 09:36 | 59.7 | 38.5 | 0 | 1.8 | -25 | 25 | 1007 | 0.36 | 5.4 | 34 | 30 | 15.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-07-25 09:34 | 38.3 | 30.8 | 0 | 30.9 | -16.4 | 16.4 | 1007 | 3.59 | 35.9 | 144 | 40 | 18.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-07-25 09:32 | 16.6 | 12.7 | 10 | 60.7 | -0.3 | 0.3 | 1007 | 0.09 | 1.3 | 2 | 2 | 14.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2018-07-25 09:31 | 51.1 | 32.5 | 0 | 16.4 | -9.8 | 9.8 | 1007 | >>>> | 0 | 0 | 99 | 14.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-07-25 09:29 | 31 | 23.2 | 6.8 | 39 | -49.3 | 49.3 | 1007 | 0.21 | 8.6 | 28 | 2 | 17.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-07-24 14:15 | 55.8 | 38.9 | 0 | 5.3 | 0.3 | -0.3 | 995 | 3.36 | 8.1 | 47 | 15 | 19.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-07-24 14:12 | 61.7 | 41 | 0 | 0 | 0 | 0 | 996 | 1.45 | 5.4 | 34 | 15 | 19.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-07-24 14:08 | 55 | 36.5 | 0 | 8.5 | -3.2 | 3.2 | 994 | 7.15 | 24.2 | 139 | 25 | 17.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2018-07-24 14:00 | 57.3 | 40.9 | 0 | 1.8 | -73.6 | 73.6 | 995 | -0.51 | 0 | 0 | 99 | 21.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2018-07-24 13:58 | 52 | 38.5 | 0 | 9.5 | -38.3 | 38.3 | 995 | 2.22 | 12.9 | 70 | 50 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2018-07-24 13:57 | 18 | 10.4 | 15.2 | 56.4 | -0.5 | 0.5 | 994 | -0.22 | 0 | 0 | 0 | 16.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-07-24 13:56 | 42.2 | 34.3 | 0 | 23.5 | -13.2 | 13.2 | 994 | 6.85 | 5.7 | 25 | 15 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2018-07-24 13:55 | 53 | 40.2 | 0 | 6.8 | -27.4 | 27.4 | 994 | 5.11 | 19.3 | 107 | 40 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-07-24 13:53 | 52.8 | 39.7 | 0 | 7.5 | -22.2 | 22.2 | 994 | 7.55 | 24.1 | 133 | 40 | 22.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-07-24 13:52 | 59.4 | 42.5 | 0 | 0 | -3.7 | 3.7 | 994 | -0.25 | 0 | 0 | 8 | 21.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-07-24 13:50 | 59.3 | 41.2 | 0 | 0 | -33.3 | 33.3 | 995 | 17.13 | 126.4 | 786 | 90 | 31.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-07-24 13:47 | 47.7 | 37.6 | 0 | 14.7 | -0.1 | 0.1 | 995 | 0.82 | 8 | 40 | 10 | 19.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-07-24 13:46 | 49.4 | 37.9 | 0.1 | 12.6 | -12.5 | 12.5 | 995 | 1.16 | 20.6 | 106 | 15 | 16.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-07-24 13:44 | 51.3 | 37.7 | 0 | 11 | -20.9 | 20.9 | 995 | 0.04 | 3.7 | 20 | 15 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2018-07-24 13:43 | 49.2 | 36.7 | 0 | 14.1 | -6.2 | 6.2 | 995 | 5.53 | 44.5 | 229 | 40 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-07-24 13:42 | 40.3 | 31.5 | 2.7 | 25.5 | 0 | 0 | 995 | 11.28 | 7.4 | 31 | 5 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2018-07-24 13:39 | 45 | 36.1 | 0 | 18.9 | -63.6 | 63.6 | 995 | 0.11 | 10 | 47 | 99 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2018-07-24 11:34 | 54.6 | 38.2 | 0 | 7.2 | -4 | 4 | 996 | 2.33 | 47.5 | 272 | 40 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2018-07-24 11:33 | 63.9 | 38.2 | 0 | 0 | -63.8 | 63.8 | 996 | 5.56 | 20.8 | 139 | 99 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2018-07-24 11:31 | 53.8 | 38 | 0 | 8.2 | -12.4 | 12.4 | 996 | 3.83 | 61 | 344 | 50 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-07-24 11:30 | 54.6 | 39.8 | 0 | 5.6 | -27.7 | 27.7 | 996 | 18.45 | 129.8 | 743 | 90 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-07-24 11:28 | 58.2 | 42.5 | 0 | 0 | 0 | 0 | 996 | 0.13 | 3.2 | 19 | 8 | 20.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-07-24 11:26 | 49.5 | 38.1 | 0.2 | 12.2 | -31.2 | 31.2 | 996 | 3.71 | 57.6 | 299 | 50 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2018-07-24 11:22 | 3.8 | 3.3 | 19.3 | 73.6 | -10.9 | 10.9 | 996 | -0.11 | 0 | 0 | 0 | 33.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2018-07-24 11:21 | 60.9 | 42.6 | 0 | 0 | -63.9 | 63.9 | 996 | 0.92 | 28.3 | 181 | 99 | 42.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2018-07-24 11:20 | 0.9 | 0.8 | 19.9 | 78.4 | -65.6 | 65.6 | 996 | -0.07 | 0 | 0 | 99 | 13.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2018-07-24 11:19 | 6.8 | 4.5 | 19.2 | 69.5 | -65.3 | 65.3 | 996 | -0.11 | 0 | 0 | 99 | 13.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2018-07-24 11:18 | 2.2 | 1.9 | 19.9 | 76 | -0.9 | 0.9 | 996 | -0.11 | 0 | 0 | 0 | 14.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2018-07-24 11:17 | 50.7 | 38.8 | 0.1 | 10.4 | -0.5 | 0.5 | 995 | 9.23 | 6.7 | 35 | 10 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-07-24 11:16 | 54 | 41.1 | 0 | 4.9 | -14.7 | 14.7 | 996 | 4.05 | 37 | 209 | 40 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2018-07-24 11:14 | 56.6 | 42.3 | 0.8 | 0.3 | -65.4 | 65.4 | 995 | 0.16 | 7.1 | 42 | 99 | 39.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2018-07-24 11:13 | 59.5 | 42.8 | 0 | 0 | -65.1 | 65.1 | 996 | -0.11 | 0 | 0 | 99 | 14.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2018-07-24 11:12 | 42 | 32.2 | 5.4 | 20.4 | -65.4 | 65.4 | 995 | -0.15 | 0 | 0 | 20 | 13.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2018-07-24 11:04 | 53.1 | 39.5 | 0.4 | 7 | -5.5 | 5.5 | 997 | 4.72 | 9.6 | 53 | 15 | 16.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-07-24 11:03 | 55.7 | 40.4 | 0 | 3.9 | -2.2 | 2.2 | 997 | 0.84 | 17.7 | 103 | 25 | 16.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-07-24 11:02 | 55.4 | 40.9 | 0 | 3.7 | -71.1 | 71.1 | 997 | 2.23 | 27.8 | 161 | 40 | 17.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-07-24 11:00 | 0.5 | 0.5 | 20.4 | 78.6 | 0 | 0 | 997 | -0.31 | 0 | 0 | 0 | 18.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-07-24 10:58 | 59.9 | 42.7 | 0 | 0 | 0.6 | -0.6 | 996 | -0.33 | 0 | 0 | 25 | 17.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-07-24 10:55 | 43.7 | 36.4 | 0 | 19.9 | -3.1 | 3.1 | 996 | 4.86 | 19.1 | 87 | 25 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-07-24 10:54 | 50.5 | 39.5 | 1.4 | 8.6 | -39.3 | 39.3 | 996 | 0.66 | 24.2 | 128 | 40 | 35.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-07-24 10:52 | 47.2 | 37.2 | 0.2 | 15.4 | -1.6 | 1.6 | 997 | 1.4 | 10.4 | 51 | 15 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2018-07-24 10:50 | 1.6 | 1.3 | 14.1 | 83 | 0 | 0 | 997 | -0.31 | 0 | 0 | 0 | 22.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2018-07-24 10:49 | 52.4 | 39.5 | 0 | 8.1 | -59.7 | 59.7 | 997 | 2.17 | 44.4 | 244 | 99 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-07-24 10:48 | 44.2 | 38.2 | 0 | 17.6 | 0 | 0 | 996 | 6.53 | 21.6 | 100 | 20 | 43.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-07-24 09:46 | 58.7 | 41.7 | 0 | 0 | 0 | 0 | 997 | 5.35 | 1.1 | 7 | 7 | 17.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2018-07-24 09:44 | 54.1 | 38.9 | 0 | 7 | -12.6 | 12.6 | 997 | 5.44 | 43.8 | 248 | 40 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-07-24 09:43 | 57.7 | 40.9 | 0 | 1.4 | -1.2 | 1.2 | 998 | -0.72 | 0 | 0 | 12 | 26 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2018-07-24 09:39 | 51.6 | 38.5 | 0 | 9.9 | -3.7 | 3.7 | 998 | 1.34 | 21.8 | 118 | 20 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-07-24 09:37 | 53.2 | 37.9 | 0 | 8.9 | -1.4 | 1.4 | 998 | 0.06 | 4.7 | 26 | 15 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-07-24 09:36 | 46.2 | 34.5 | 2.9 | 16.4 | -0.3 | 0.3 | 998 | 5.44 | 10.4 | 50 | 12 | 13.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-07-24 09:34 | 59.6 | 42 | 0 | 0 | -0.2 | 0.2 | 997 | 18.64 | 9.7 | 60 | 15 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-07-24 09:33 | 42 | 33.2 | 3.1 | 21.7 | -0.1 | 0.1 | 997 | 0.98 | 4.2 | 18 | 5 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-07-24 09:31 | 55.8 | 39.9 | 0 | 4.3 | -1.3 | 1.3 | 998 | 16.53 | 9 | 52 | 15 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2018-07-24 09:28 | 49.3 | 38.4 | 0.2 | 12.1 | -3.4 | 3.4 | 998 | 2.65 | 29.9 | 154 | 25 | 42 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2018-07-24 09:26 | 25.9 | 14.1 | 12.7 | 47.3 | -61.1 | 61.1 | 998 | -0.29 | 0 | 0 | 99 | 14.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2018-07-24 09:25 | 57.4 | 41.3 | 0 | 1.3 | -0.1 | 0.1 | 998 | -0.22 | 0 | 0 | 20 | 14.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-07-24 09:23 | 50.3 | 38.9 | 0 | 10.8 | -1.6 | 1.6 | 997 | 0.82 | 17.2 | 90 | 25 | 24.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-07-24 09:22 | 52.7 | 39.6 | 0 | 7.7 | -2.8 | 2.8 | 998 | 0.73 | 16.3 | 90 | 20 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-07-24 09:20 | 57.1 | 40.4 | 0 | 2.5 | 0 | 0 | 998 | 16.16 | 9.1 | 54 | 10 | 15.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2018-07-24 09:19 | 55.4 | 39.3 | 0 | 5.3 | -0.5 | 0.5 | 998 | 4.3 | 4.7 | 27 | 5 | 16.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2018-07-24 09:17 | 54 | 39.3 | 0 | 6.7 | -0.7 | 0.7 | 998 | 3.98 | 17.5 | 99 | 25 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2018-07-24 09:16 | 49.7 | 39.3 | 0.2 | 10.8 | -26.2 | 26.2 | 997 | 18.9 | 79.6 | 414 | 80 | 37.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2018-07-24 09:14 | 54.4 | 41.6 | 0 | 4 | -0.3 | 0.3 | 997 | 5.04 | 5 | 28 | 10 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-07-24 09:13 | 42 | 35.4 | 0.6 | 22 | 0 | 0 | 997 | 2.21 | 3.3 | 14 | 5 | 15.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2018-07-24 09:03 | 5.9 | 7.4 | 17.3 | 69.4 | -0.2 | 0.2 | 997 | 13.85 | 1.8 | 1 | 5 | 11.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2018-07-24 09:02 | 54.6 | 39.8 | 1.1 | 4.5 | -0.4 | 0.4 | 997 | 0.14 | 1.6 | 9 | 10 | 14.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2018-07-24 09:00 | 23.6 | 23.6 | 6.7 | 46.1 | 0 | 0 | 997 | 0.5 | 6.2 | 15 | 0 | 12.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2018-07-24 08:58 | 42.7 | 33.4 | 4.8 | 19.1 | -11.6 | 11.6 | 997 | -0.72 | 0 | 0 | 10 | 20.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2018-07-24 08:57 | 52.9 | 41 | 0.2 | 5.9 | -0.2 | 0.2 | 997 | 2.47 | 6.9 | 38 | 15 | 16 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-07-24 08:55 | 47.6 | 34.1 | 2.7 | 15.6 | -0.7 | 0.7 | 997 | 4.52 | 9.4 | 47 | 20 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-07-24 08:54 | 42.8 | 35.8 | 0 | 21.4 | -1.1 | 1.1 | 997 | 5.11 | 5 | 22 | 15 | 16 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2018-07-24 08:53 | 50.1 | 40.3 | 0 | 9.6 | -1.3 | 1.3 | 997 | 0.97 | 18.6 | 97 | 25 | 25.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2018-07-24 08:51 | 51.3 | 39.9 | 0 | 8.8 | -3.3 | 3.3 | 997 | 1.14 | 20.3 | 109 | 25 | 19 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-07-24 08:49 | 53.5 | 39.6 | 0.5 | 6.4 | -2.6 | 2.6 | 997 | -0.88 | 0 | 0 | 20 | 17.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2018-07-24 08:47 | 54.8 | 40.6 | 0 | 4.6 | -2 | 2 | 997 | 8.11 | 25.3 | 145 | 40 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-07-24 08:45 | 50.8 | 39.1 | 0.2 | 9.9 | -0.8 | 0.8 | 997 | 8.26 | 12.5 | 67 | 20 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2018-07-24 08:44 | 51.8 | 40.6 | 0 | 7.6 | -1.6 | 1.6 | 997 | 7.98 | 12.2 | 66 | 20 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2018-07-24 08:42 | 53.2 | 41.3 | 0 | 5.5 | -0.1 | 0.1 | 997 | 1.45 | 10.7 | 59 | 10 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2018-07-24 08:41 | 56 | 41.6 | 0 | 2.4 | 0 | 0 | 998 | 0.03 | 1.5 | 8 | 12 | 15.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-07-24 08:36 | 54.9 | 39.2 | 0.4 | 5.5 | -6.1 | 6.1 | 998 | 3.51 | 35.8 | 206 | 40 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2018-07-24 08:34 | 49 | 38.6 | 0.1 | 12.3 | -5.2 | 5.2 | 998 | 1.88 | 25.8 | 132 | 40 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-07-24 08:32 | 42.1 | 35.5 | 0.4 | 22 | -1.6 | 1.6 | 998 | 0.27 | 4.5 | 19 | 10 | 21.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2018-07-24 08:31 | 49.6 | 40 | 0.1 | 10.3 | -61.6 | 61.6 | 998 | 11.78 | 60.7 | 316 | 70 | 45.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2018-07-24 08:28 | 33.9 | 26.6 | 8.3 | 31.2 | -0.1 | 0.1 | 998 | 0.02 | 0.6 | 2 | 20 | 16.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-06-28 14:54 | 45.3 | 35.8 | 0 | 18.9 | -3 | 3 | 1012 | 13.463 | 31.3 | 161 | 45 | 42.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-06-28 14:52 | 55.7 | 38.4 | 0 | 5.9 | -3 | 3 | 1012 | 15.116 | 35 | 182 | 40 | 18.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y483 | 2018-06-28 14:47 | 46 | 35.6 | 1.8 | 16.6 | -0.5 | 0.5 | 1011 | 0.144 | 3.3 | 37 | 10 | 15.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y482 | 2018-06-28 14:45 | 46 | 38.6 | 0 | 15.4 | -1.4 | 1.4 | 1011 | 9.461 | 26.6 | 145 | 40 | 28.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-06-28 14:43 | 51.6 | 37.2 | 0.2 | 11 | -2.4 | 2.4 | 1012 | 5.642 | 20.3 | 101 | 20 | 44.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P477 | 2018-06-28 14:38 | 56.7 | 39.7 | 0 | 3.6 | -3.7 | 3.7 | 1012 | 3.838 | 37.3 | 204 | 42 | 28.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-06-28 14:36 | 57.8 | 39.7 | 0 | 2.5 | -0.5 | 0.5 | 1012 | 3.972 | 8.8 | 40 | 15 | 23.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-06-28 14:32 | 62.5 | 40.9 | 0 | 0 | -0.1 | 0.1 | 1012 | 4.138 | 4.6 | 11 | 5 | 17.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-06-28 14:29 | 59.7 | 38.5 | 0 | 1.8 | -4.5 | 4.5 | 1012 | 8.344 | 26.1 | 133 | 37 | 19.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-06-28 14:28 | 50.6 | 34.9 | 2.6 | 11.9 | -0.8 | 0.8 | 1012 | 1.506 | 23.6 | 125 | 25 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-06-28 14:25 | 32.7 | 28.4 | 4.5 | 34.4 | -0.7 | 0.7 | 1012 | 0.757 | 7.4 | 39 | 15 | 34.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-06-28 14:23 | 17.7 | 17.2 | 9.2 | 55.9 | -12.7 | 12.7 | 1012 | 0.027 | 1.4 | 7 | 5 | 16.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-06-28 14:21 | 51.8 | 37.9 | 2.4 | 7.9 | -2 | 2 | 1012 | 0.226 | 9.1 | 49 | 10 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-06-28 14:19 | 48.4 | 37.3 | 0 | 14.3 | -4.4 | 4.4 | 1012 | 3.624 | 35.5 | 187 | 40 | 34.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-06-28 14:18 | 61.7 | 42.3 | 0 | 0 | 0.1 | -0.1 | 1012 | 3.739 | 8.6 | 46 |  | 22 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-06-28 14:16 | 59.9 | 42.8 | 0 | 0 | -0.1 | 0.1 | 1011 | 8.316 | 6.4 | 29 | 15 | 25.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-06-28 14:11 | 56.6 | 40.8 | 0 | 2.6 | -2.4 | 2.4 | 1010 | 1.474 | 23.4 | 129 | 30 | 19.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-06-28 14:06 | 55.7 | 40.4 | 0 | 3.9 | -13.1 | 13.1 | 1010 | 4.463 | 39.1 | 202 | 40 | 40.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-06-28 13:42 | 58.4 | 39.7 | 0 | 1.9 | -1.1 | 1.1 | 1012 | 16.835 | 9.1 | 47 | 25 | 28.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-06-28 13:40 | 44.3 | 33.7 | 0 | 22 | -1 | 1 | 1012 | 0.113 | 6.4 | 34 | 20 | 22.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-06-28 13:35 | 51.3 | 38.4 | 0 | 10.3 | -1.6 | 1.6 | 1012 | 1.328 | 21.9 | 114 | 30 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-06-28 13:34 | 52.4 | 38.4 | 0 | 9.2 | -2.6 | 2.6 | 1012 | 1.102 | 20 | 109 | 20 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-06-28 13:33 | 60.2 | 40.3 | 0 | 0 | -0.1 | 0.1 | 1012 | 17.371 | 9.5 | 52 | 15 | 15.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-06-28 13:30 | 46.4 | 36.9 | 0 | 16.7 | 0 | 0 | 1012 | 2.658 | 3.7 | 18 | 10 | 3.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-06-28 13:27 | 60.3 | 43 | 0 | 0 | -2.3 | 2.3 | 1012 | 2.674 | 14.5 | 62 | 20 | 23.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-06-28 13:25 | 55.7 | 40.3 | 0.5 | 3.5 | -0.1 | 0.1 | 1012 | 1.749 | 11.9 | 68 | 20 | 14.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-06-28 13:23 | 59 | 41.4 | 0 | 0 | -0.1 | 0.1 | 1012 | 3.563 | 16.9 | 74 | 20 | 20.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-06-28 13:21 | 46.1 | 36.3 | 0.2 | 17.4 | -1.2 | 1.2 | 1011 | 0.6 | 24 | 121 | 22 | 23.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-06-28 13:17 | 52.9 | 39.4 | 0 | 7.7 | -0.1 | 0.1 | 1011 | 16.347 | 9 | 50 | 15 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-06-28 13:15 | 42.3 | 36.6 | 0 | 21.1 | 0 | 0 | 1012 | 0.338 | 10.9 | 49 | 15 | 22.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-06-28 13:11 | 52.8 | 38.8 | 0.1 | 8.3 | -0.5 | 0.5 | 1012 | 8.394 | 12.7 | 70 | 25 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-06-28 13:06 | 57.9 | 39.2 | 0 | 2.9 | -4.6 | 4.6 | 1013 | 3.779 | 37.4 | 204 | 40 | 24.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-06-28 13:04 | 52.3 | 38.2 | 0 | 9.5 | -0.4 | 0.4 | 1013 | 0.158 | 3.5 | 21 | 20 | 16 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-06-28 13:01 | 61.5 | 39.7 | 0 | 0 | -0.2 | 0.2 | 1014 | 0.657 | 7.4 | 22 | 5 | 15.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-06-28 12:12 | 56.8 | 39.9 | 0 | 3.3 | -28.6 | 28.6 | 1013 | 18.558 | 130.8 | 704 | 85 | 35.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-06-28 12:09 | 61.3 | 42.3 | 0 | 0 | 0 | 0 | 1014 | 0.529 | 6.5 | 20 | 7 | 18.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-06-28 12:03 | 51.1 | 38.8 | 0.1 | 10 | -1.7 | 1.7 | 1013 | 6.326 | 22.6 | 121 | 25 | 13.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-06-28 12:00 | 45 | 36.7 | 0 | 18.3 | -3 | 3 | 1013 | 5.208 | 19.8 | 103 | 25 | 29.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-06-28 11:57 | 47.9 | 37.8 | 0 | 14.3 | -1.2 | 1.2 | 1014 | 2.119 | 12.9 | 63 | 15 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-06-28 11:53 | 30 | 29.4 | 0 | 40.6 | -12.8 | 12.8 | 1014 | 8.526 | 6.4 | 30 | 25 | 15.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-06-28 11:50 | 43.3 | 36.3 | 0 | 20.4 | -0.3 | 0.3 | 1014 | 1.071 | 9.1 | 51 | 15 | 20.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-06-28 11:48 | 47.7 | 37.2 | 0 | 15.1 | -12.4 | 12.4 | 1014 | 1.506 | 23.2 | 132 | 20 | 22.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-06-28 11:46 | 54 | 37.1 | 0.9 | 8 | -0.1 | 0.1 | 1015 | 7.52 | 6.2 | 25 | 10 | 17.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-06-28 11:42 | 42.5 | 33.1 | 0 | 24.4 | -1.2 | 1.2 | 1015 | 0.361 | 11.6 | 62 | 15 | 12.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-06-28 11:35 | 54.9 | 36.7 | 0.1 | 8.3 | -3.4 | 3.4 | 1015 | 1.721 | 11.9 | 66 | 15 | 14.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-06-28 11:33 | 55.2 | 38.2 | 0.8 | 5.8 | -1.2 | 1.2 | 1016 | 0.207 | 14.4 | 85 | 25 | 17.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-06-28 11:31 | 45.8 | 34.3 | 0 | 19.9 | -6.6 | 6.6 | 1016 | 4.02 | 38.6 | 206 | 40 | 16 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-06-28 11:28 | 41.7 | 30.4 | 0 | 27.9 | -18.7 | 18.7 | 1015 | 3.325 | 34.8 | 168 | 45 | 19.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2018-06-25 12:08 | 62.5 | 42.5 | 0 | 0 | -32.2 | 32.2 | 1023 | 12.21 | 106.8 | 700 | 99 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2018-06-25 12:07 | 25.7 | 14.1 | 10.3 | 49.9 | -40.2 | 40.2 | 1023 | 0.17 | 3.6 | 9 | 99 | 21.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2018-06-25 12:06 | 59.7 | 41.7 | 0 | 0 | -29.3 | 29.3 | 1023 | 18.87 | 133.9 | 837 | 99 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2018-06-25 12:05 | 61.2 | 42.9 | 0 | 0 | -29.7 | 29.7 | 1024 | 18.79 | 132.6 | 850 | 99 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2018-06-25 12:02 | 58.9 | 39.5 | 0 | 1.6 | -5.9 | 5.9 | 1024 | 3.14 | 15.9 | 98 | 22 | 21.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2018-06-25 12:00 | 52.1 | 37.2 | 0.1 | 10.6 | -0.5 | 0.5 | 1024 | 2.38 | 13.7 | 75 | 30 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2018-06-25 11:58 | 54.3 | 37.4 | 0.2 | 8.1 | -0.7 | 0.7 | 1024 | 1.73 | 11.7 | 67 | 25 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2018-06-25 11:56 | 52.1 | 37.1 | 0 | 10.8 | -1.7 | 1.7 | 1024 | 8.21 | 25.5 | 139 | 50 | 21.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2018-06-25 11:54 | 34 | 27.1 | 3.9 | 35 | -0.3 | 0.3 | 1024 | 0.82 | 7.9 | 28 | 20 | 21.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2018-06-25 11:52 | 47.3 | 34.1 | 1 | 17.6 | -0.1 | 0.1 | 1024 | 1.17 | 9.6 | 48 | 20 | 20.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2018-06-25 11:46 | 61.5 | 39 | 0.5 | 0 | -12.9 | 12.9 | 1023 | 0.06 | 4.9 | 31 | 10 | 18.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2018-06-25 11:45 | 48.9 | 35.6 | 0 | 15.5 | -12.6 | 12.6 | 1023 | 19.62 | 38.4 | 197 | 50 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-06-25 11:43 | 52.7 | 36.7 | 0 | 10.6 | -10.6 | 10.6 | 1023 | 19.3 | 84.7 | 468 | 50 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-06-25 11:42 | 45.4 | 35.9 | 0 | 18.7 | -3.4 | 3.4 | 1023 | 15.9 | 34 | 161 | 40 | 42.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-06-25 11:41 | 50.7 | 38.8 | 0 | 10.5 | -43.8 | 43.8 | 1023 | 22.37 | 85.1 | 452 | 99 | 44.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2018-06-25 11:39 | 49.4 | 36.4 | 0 | 14.2 | -59.9 | 59.9 | 1023 | 0.12 | 6.4 | 33 | 99 | 17 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-06-25 11:38 | 17.4 | 25.7 | 0 | 56.9 | -1.3 | 1.3 | 1023 | 0.12 | 2.9 | 5 | 5 | 29.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2018-06-25 11:36 | 63.5 | 39.7 | 0 | 0 | -44.2 | 44.2 | 1023 | 8.2 | 25.1 | 167 | 99 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2018-06-25 11:35 | 53.1 | 36.8 | 0 | 10.1 | -24.5 | 24.5 | 1023 | 7.31 | 50.6 | 281 | 40 | 33.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-06-25 11:33 | 56.1 | 38.2 | 0 | 5.7 | -2.2 | 2.2 | 1022 | 8.69 | 26.6 | 156 | 28 | 17.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-06-25 11:32 | 53.9 | 39.2 | 0.3 | 6.6 | -26.7 | 26.7 | 1023 | 13.81 | 31.6 | 179 | 40 | 41.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y483 | 2018-06-25 11:23 | 37.2 | 30.8 | 4.1 | 27.9 | -0.9 | 0.9 | 1022 | 1.31 | 10.1 | 39 | 10 | 15.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y481 | 2018-06-25 11:20 | 54.5 | 41.5 | 0 | 4 | -1.5 | 1.5 | 1022 | 5.31 | 20.4 | 116 | 25 | 22.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y482 | 2018-06-25 11:19 | 42 | 37.9 | 0 | 20.1 | -2.2 | 2.2 | 1022 | 15.56 | 33.9 | 149 | 25 | 29.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2018-06-25 11:17 | 56.7 | 41 | 0 | 2.3 | -37.7 | 37.7 | 1022 | 31.22 | 165.5 | 984 | 99 | 46.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-06-25 11:15 | 41.1 | 32.6 | 1.8 | 24.5 | -5.4 | 5.4 | 1022 | 5.49 | 20.5 | 88 | 10 | 25.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2018-06-25 11:14 | 0.6 | 0.7 | 20.7 | 78 | -14.8 | 14.8 | 1022 | -0.01 | 0 | 0 | 0 | 15.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2018-06-25 11:12 | 0.4 | 0.1 | 20.6 | 78.9 | -58.4 | 58.4 | 1022 | 0.07 | 4.7 | 0 | 2 | 18.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2018-06-25 11:10 | 57 | 42 | 0 | 1 | -40.6 | 40.6 | 1022 | 28.18 | 157.1 | 939 | 99 | 44.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2018-06-25 11:09 | 12.3 | 25.8 | 5.7 | 56.2 | -0.3 | 0.3 | 1024 | -0.03 | 0 | 0 | 10 | 15.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P477 | 2018-06-25 10:37 | 56.3 | 39.8 | 0 | 3.9 | -3.2 | 3.2 | 1023 | 2.87 | 32.3 | 190 | 42 | 27.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-06-25 10:35 | 45.8 | 34.1 | 2.2 | 17.9 | -0.2 | 0.2 | 1023 | 1.94 | 6.1 | 29 | 8 | 22.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-06-25 10:33 | 50.2 | 33.7 | 2.8 | 13.3 | -3.5 | 3.5 | 1023 | 6.72 | 49.2 | 259 | 40 | 30.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-06-25 10:32 | 35.5 | 24.3 | 9 | 31.2 | -62.2 | 62.2 | 1023 | 0.06 | 2.1 | 7 | 50 | 22.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-06-25 10:30 | 48.5 | 37.2 | 0.2 | 14.1 | -28.5 | 28.5 | 1023 | 7.64 | 50.8 | 258 | 50 | 36.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-06-25 10:28 | 62.3 | 41.2 | 0 | 0 | 0.1 | -0.1 | 1023 | -0.01 | 0 | 0 | 8 | 15.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2018-06-25 10:27 | 46.2 | 36.3 | 0 | 17.5 | -1.6 | 1.6 | 1023 | 1.93 | 6 | 29 | 15 | 22.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2018-06-25 10:26 | 62.8 | 39.9 | 0 | 0 | -62.2 | 62.2 | 1023 | 2 | 44.1 | 290 | 99 | 18 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2018-06-25 10:24 | 0.4 | 0.2 | 20.8 | 78.6 | -33.5 | 33.5 | 1023 | -1 | 0 | 0 | 5 | 15.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-06-25 10:22 | 59.9 | 38.9 | 0 | 1.2 | -2.9 | 2.9 | 1023 | 4.28 | 18.7 | 117 | 40 | 18.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-06-25 10:18 | 42.3 | 30.3 | 5 | 22.4 | -1.2 | 1.2 | 1023 | 1.85 | 26 | 115 | 35 | 22.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2018-06-25 10:16 | 54.7 | 40 | 0 | 5.3 | -0.3 | 0.3 | 1023 | 1.93 | 12.2 | 70 | 30 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2018-06-25 10:14 | 51.8 | 37.8 | 0 | 10.4 | -39.4 | 39.4 | 1023 | 30.04 | 101.8 | 553 | 99 | 29.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-06-25 10:03 | 30.3 | 27.8 | 4.8 | 37.1 | -3.6 | 3.6 | 1022 | 3.41 | 15.6 | 49 | 10 | 37.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2018-06-25 10:01 | 47.7 | 38.9 | 0 | 13.4 | -41.5 | 41.5 | 1022 | 30.41 | 161.2 | 806 | 99 | 44.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-06-25 10:00 | 20 | 21.9 | 5.9 | 52.2 | -10.8 | 10.8 | 1022 | 0.84 | 7.9 | 16 | 5 | 16.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-06-25 09:57 | 39 | 30.1 | 6.3 | 24.6 | -3.3 | 3.3 | 1022 | 0.19 | 8 | 32 | 12 | 35.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2018-06-25 09:55 | 47.9 | 38.1 | 0 | 14 | -3.2 | 3.2 | 1022 | 1.48 | 22.5 | 113 | 20 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-06-25 09:53 | 46 | 37.2 | 0 | 16.8 | -4.9 | 4.9 | 1022 | 3.88 | 36.6 | 176 | 30 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-06-25 09:52 | 41.2 | 32.7 | 3.5 | 22.6 | -0.3 | 0.3 | 1022 | 4.97 | 9.7 | 42 | 5 | 22.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2018-06-25 09:49 | 54 | 38.4 | 0 | 7.6 | -7.7 | 7.7 | 1022 | 5.27 | 43.8 | 248 | 40 | 24.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2018-06-25 09:47 | 7.1 | 4.9 | 18.4 | 69.6 | -62.3 | 62.3 | 1022 | -0.17 | 0 | 0 | 50 | 12.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-06-25 09:46 | 53.9 | 37.9 | 0.3 | 7.9 | -2.9 | 2.9 | 1022 | 1.19 | 21.3 | 120 | 25 | 12.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-06-25 09:45 | 45.6 | 32.7 | 3.8 | 17.9 | -0.1 | 0.1 | 1022 | 4.62 | 4.8 | 23 | 5 | 16.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-06-25 09:43 | 39.4 | 34.8 | 0 | 25.8 | -0.5 | 0.5 | 1022 | 5.21 | 4.9 | 20 | 8 | 24.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-06-25 09:08 | 9.4 | 7.2 | 16.7 | 66.7 | -0.3 | 0.3 | 1022 | 0.45 | 5.8 | 5 | 5 | 21.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-06-25 09:06 | 49.6 | 37.6 | 0.5 | 12.3 | -32.1 | 32.1 | 1022 | 2.5 | 47.4 | 246 | 50 | 36.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-06-25 08:53 | 63.5 | 44.6 | 0 | 0 | -71.9 | 71.9 | 1021 | 2.9 | 31.5 | 209 | 99 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-06-25 08:52 | 62.4 | 46.5 | 0 | 0 | -66.9 | 66.9 | 1021 | 6.05 | 45.4 | 297 | 99 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-06-25 08:50 | 62.9 | 47.4 | 0 | >>>> | -59.1 | 59.1 | 1021 | 22.58 | 89.7 | 591 | 99 | 12.3 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2018-06-25 08:49 | 47.6 | 44.7 | 0 | 7.7 | -7.9 | 7.9 | 1021 | 8.92 | 56.6 | 283 | 50 | 10.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2018-06-25 08:47 | 56.7 | 45.9 | 0.3 | 0 | -75.6 | 75.6 | 1022 | -0.22 | 0 | 0 | 99 | 12.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2018-06-25 08:25 | 60.1 | 43.8 | 0 | 0 | -62.8 | 62.8 | 1021 | 0.7 | 25 | 157 | 99 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2018-06-25 08:23 | 14.5 | 12.7 | 13.3 | 59.5 | -0.5 | 0.5 | 1021 | 0.01 | 0.2 | 0 | 0 | 22.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2018-06-25 08:22 | 60.3 | 43.9 | 0 | 0 | -58.2 | 58.2 | 1021 | 2.7 | 14 | 88 | 99 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2018-06-25 08:21 | 4.8 | 4.1 | 19.7 | 71.4 | -63.3 | 63.3 | 1021 | 0.05 | 1.9 | 0 | 99 | 12.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2018-06-25 08:20 | 51.6 | 38.5 | 0 | 9.9 | -33.3 | 33.3 | 1021 | 9.04 | 57.2 | 309 | 50 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2018-06-25 08:18 | 61.5 | 43.1 | 0 | 0 | -62.5 | 62.5 | 1021 | 0.16 | 3.4 | 22 | 99 | 16.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2018-06-25 08:16 | 0.4 | 3 | 18.6 | 78 | -3.2 | 3.2 | 1021 | 0.01 | 1.7 | 0 |  | 26.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2018-06-25 08:15 | 49.1 | 37.6 | 0.6 | 12.7 | -27.8 | 27.8 | 1021 | 6.37 | 46 | 237 | 40 | 41.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2018-06-25 08:13 | 48.4 | 37.7 | 0 | 13.9 | -60.9 | 60.9 | 1021 | 3.27 | 53.2 | 269 | 99 | 38.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-06-25 08:11 | 49.8 | 39.3 | 0.3 | 10.6 | -1.3 | 1.3 | 1021 | 1.54 | 10.5 | 55 | 40 | 43.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-06-22 13:52 | 51.6 | 37.1 | 0 | 11.3 | 0 | 0 | 1017 | 2.79 | 7.3 | 39 | 15 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-06-22 13:49 | 55.8 | 38.2 | 0 | 6 | 0 | 0 | 1017 | 0.9 | 4.2 | 24 | 5 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2018-06-22 13:42 | 49.7 | 36.3 | 0 | 14 | -2 | 2 | 1017 | 4.2 | 9.1 | 47 | 10 | 16.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-06-22 13:41 | 43.2 | 33.5 | 0 | 23.3 | -1.7 | 1.7 | 1017 | 0.79 | 17.1 | 77 | 20 | 15.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-06-22 13:39 | 51.8 | 37.1 | 2.5 | 8.6 | -0.4 | 0.4 | 1017 | 0.21 | 4.1 | 22 | 10 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-06-22 13:38 | 7 | 4.8 | 18.5 | 69.7 | -63.6 | 63.6 | 1017 | -0.02 | 0 | 0 | 99 | 15.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-06-22 13:37 | 49.9 | 33.6 | 3.3 | 13.2 | -0.2 | 0.2 | 1017 | 0.07 | 2.4 | 12 | 5 | 17.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-06-22 13:35 | 47.4 | 36.6 | 0 | 16 | -6.1 | 6.1 | 1017 | 4.29 | 18.2 | 90 | 25 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-06-22 13:34 | 51.3 | 37.9 | 0 | 10.8 | -0.6 | 0.6 | 1017 | 4.78 | 9.6 | 52 | 20 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2018-06-22 13:32 | 0.4 | 0.2 | 20.5 | 78.9 | -0.1 | 0.1 | 1017 | 0.02 | 1.1 | 0 | 0 | 14.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2018-06-22 13:31 | 46.5 | 33.5 | 0 | 20 | -0.8 | 0.8 | 1017 | 2.17 | 13.2 | 64 | 15 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-06-22 13:30 | 1.9 | 1.4 | 20 | 76.7 | -0.2 | 0.2 | 1017 | 0.02 | 0.5 | 0 | 0 | 17.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-06-22 13:29 | 55.3 | 38.4 | 0.7 | 5.6 | -10.8 | 10.8 | 1017 | 4.51 | 18.9 | 110 | 25 | 20.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2018-06-22 13:28 | 53.4 | 39.8 | 0.1 | 6.7 | -0.6 | 0.6 | 1018 | 1.4 | 10.4 | 58 | 20 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2018-06-22 13:25 | 45.2 | 36.3 | 0 | 18.5 | -0.4 | 0.4 | 1018 | 0.4 | 11.7 | 55 | 15 | 35.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-06-22 13:22 | 53.9 | 35.7 | 0 | 10.4 | -2.9 | 2.9 | 1018 | 6.41 | 22.8 | 128 | 40 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2018-06-22 13:19 | 48 | 36.1 | 0 | 15.9 | -1.8 | 1.8 | 1018 | 5.71 | 20.6 | 103 | 30 | 37.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2018-06-22 12:10 | 55.3 | 39.4 | 0 | 5.3 | -82.8 | 82.8 | 1017 | -0.22 | 0 | 0 | 99 | 28.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2018-06-22 12:09 | 48.8 | 37.2 | 0 | 14 | -40.2 | 40.2 | 1017 | 4.46 | 18.1 | 92 | 50 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2018-06-22 12:07 | 29.1 | 18.2 | 11.5 | 41.2 | -0.1 | 0.1 | 1017 | -0.02 | 0 | 0 | 0 | 17.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-06-22 12:06 | 28.1 | 28.3 | 0.2 | 43.4 | -19.6 | 19.6 | 1017 | 27.27 | 11.3 | 33 | 30 | 18.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2018-06-22 12:03 | 50.2 | 38.1 | 0 | 11.7 | -14.8 | 14.8 | 1017 | 6.38 | 21.6 | 114 | 40 | 37.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-06-22 12:02 | 52.7 | 38.9 | 0 | 8.4 | -22.4 | 22.4 | 1017 | 8.3 | 25.2 | 139 | 40 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-06-22 12:00 | 0.4 | 0.2 | 20.4 | 79 | -1.9 | 1.9 | 1017 | 0 | 0.5 | 0 | 0 | 27.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-06-22 11:59 | 53.9 | 38.1 | 0.3 | 7.7 | -44 | 44 | 1017 | 14.08 | 112.9 | 638 | 80 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-06-22 11:58 | 43.2 | 35.8 | 0 | 21 | -0.3 | 0.3 | 1017 | 1.43 | 10.5 | 47 | 10 | 22.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-06-22 11:56 | 46.7 | 36.7 | 0.1 | 16.5 | -13 | 13 | 1017 | 1.4 | 22.3 | 109 | 20 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-06-22 11:55 | 49.2 | 36.4 | 0 | 14.4 | -21.1 | 21.1 | 1018 | 0.83 | 16.8 | 86 | 15 | 36.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2018-06-22 11:53 | 47.2 | 35.6 | 0 | 17.2 | -6.7 | 6.7 | 1018 | 5.49 | 44.2 | 218 | 40 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-06-22 11:52 | 33 | 25.3 | 5.5 | 36.2 | -0.3 | 0.3 | 1018 | 7.99 | 6.2 | 21 | 5 | 23.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2018-06-22 11:51 | 43.5 | 35.7 | 0 | 20.8 | -65 | 65 | 1018 | 0.51 | 21 | 95 | 99 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2018-06-22 11:12 | 51.5 | 38.2 | 1 | 9.3 | -43.4 | 43.4 | 1017 | 18.51 | 76.7 | 414 | 99 | 52.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2018-06-22 11:11 | 60.8 | 41.9 | 0 | 0 | -49.2 | 49.2 | 1017 | 7.5 | 49.8 | 317 | 99 | 43.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2018-06-22 11:10 | 59.3 | 41.6 | 0.1 | 0 | -50.5 | 50.5 | 1017 | 10.14 | 94.3 | 585 | 99 | 44.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2018-06-22 11:08 | 45.5 | 36 | 0.4 | 18.1 | -3.2 | 3.2 | 1017 | 0.04 | 1.6 | 7 | 0 | 21.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-06-22 11:05 | 60.9 | 42.2 | 0.2 | 0 | -59.4 | 59.4 | 1017 | 0.48 | 12.6 | 80 | 99 | 38.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2018-06-22 11:03 | 33.2 | 24.3 | 11.9 | 30.6 | -59.4 | 59.4 | 1017 | 0.01 | 0.6 | 2 | 0 | 17.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-06-22 11:02 | 50.7 | 38.9 | 0.4 | 10 | -0.9 | 0.9 | 1017 | 1.1 | 9.3 | 49 | 20 | 17.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-06-22 11:00 | 50.1 | 37.8 | 1.3 | 10.8 | -14.4 | 14.4 | 1017 | 6.35 | 46.2 | 242 | 50 | 42.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-06-22 10:59 | 56.9 | 42.5 | 0 | 0.6 | -54.5 | 54.5 | 1017 | 6.39 | 45.5 | 271 | 99 | 42 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2018-06-22 10:57 | 0.3 | 0.2 | 20.5 | 79 | -23.9 | 23.9 | 1017 | 0.08 | 5.1 | 0 | 0 | 19.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2018-06-22 10:56 | 0.5 | 0.2 | 19.8 | 79.5 | 0 | 0 | 1017 | 0.04 | 1.7 | 0 | 0 | 17.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2018-06-22 10:55 | 60.6 | 44 | 0 | 0 | -54 | 54 | 1017 | 0.04 | 1.8 | 11 | 20 | 18.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2018-06-22 10:53 | 60.5 | 41.6 | 0 | 0 | -61.2 | 61.2 | 1017 | 1.58 | 37.5 | 237 | 99 | 38 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2018-06-22 10:52 | 50.7 | 38.4 | 0.1 | 10.8 | -5.2 | 5.2 | 1017 | 9.1 | 26.8 | 142 | 25 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-06-22 10:50 | 48.6 | 37.2 | 0.3 | 13.9 | -2.6 | 2.6 | 1017 | 4.37 | 18.5 | 94 | 20 | 21.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-06-22 10:48 | 48.4 | 37.7 | 0.5 | 13.4 | -5.9 | 5.9 | 1018 | 1.38 | 22.5 | 114 | 25 | 15.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-06-22 10:47 | 56.3 | 40.6 | 0 | 3.1 | -2.6 | 2.6 | 1018 | 1.38 | 22.6 | 133 | 25 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-06-22 10:44 | 42.7 | 36.1 | 0 | 21.2 | -3.7 | 3.7 | 1018 | 6.39 | 21.8 | 98 | 25 | 29.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-06-22 10:42 | 53.3 | 39.8 | 0.6 | 6.3 | -32.2 | 32.2 | 1018 | 2.43 | 46.7 | 261 | 40 | 37.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-06-22 10:41 | 47 | 36.7 | 0.7 | 15.6 | -1.5 | 1.5 | 1018 | 1.68 | 11.4 | 56 | 15 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2018-06-22 10:39 | 0.7 | 1.3 | 18.8 | 79.2 | 0 | 0 | 1018 | 0.01 | 0.7 | 0 | 0 | 18.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2018-06-22 10:38 | 54 | 39.4 | 0.2 | 6.4 | -65.8 | 65.8 | 1018 | 0.8 | 27.2 | 154 | 99 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-06-22 10:36 | 36 | 34.4 | 0 | 29.6 | -0.4 | 0.4 | 1018 | 6.97 | 22.1 | 83 | 25 | 43.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2018-06-22 10:29 | 51.6 | 39 | 0.5 | 8.9 | -6 | 6 | 1018 | 4.91 | 9.8 | 53 | 15 | 15.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-06-22 10:28 | 46.5 | 38.2 | 0 | 15.3 | -3.2 | 3.2 | 1018 | 1.03 | 19.4 | 94 | 20 | 14.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-06-22 10:27 | 58 | 41.7 | 0 | 0.3 | -78.7 | 78.7 | 1018 | 0.17 | 7.7 | 47 | 50 | 15.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-06-22 10:25 | 47.5 | 37.6 | 0.3 | 14.6 | -2.4 | 2.4 | 1018 | 6.2 | 22.1 | 110 | 25 | 16.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-06-22 10:22 | 49.9 | 37.2 | 2.1 | 10.8 | -0.8 | 0.8 | 1018 | 0.42 | 12.1 | 63 | 20 | 38.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2018-06-22 09:58 | 11.8 | 8.7 | 17.8 | 61.7 | -0.2 | 0.2 | 1018 | 0.01 | 1 | 1 | 99 | 15.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2018-06-22 09:57 | 61.9 | 42.4 | 0.2 | 0 | -67 | 67 | 1018 | 1.36 | 35.9 | 233 | 99 | 16.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2018-06-22 09:55 | 2.2 | 1.8 | 20.1 | 75.9 | -67.1 | 67.1 | 1018 | -0.06 | 0 | 0 | 99 | 13.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2018-06-22 09:54 | 8.1 | 5.5 | 18.5 | 67.9 | -67.1 | 67.1 | 1018 | 0.04 | 3.7 | 3 | 99 | 13.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2018-06-22 09:53 | 1.2 | 1.1 | 18.6 | 79.1 | -3.2 | 3.2 | 1018 | 0.02 | 1.2 | 0 | 0 | 15.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2018-06-22 09:52 | 49 | 38 | 0.4 | 12.6 | -0.6 | 0.6 | 1018 | 9.89 | 6.9 | 35 | 15 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-06-22 09:50 | 56.6 | 41.2 | 0 | 2.2 | -12.7 | 12.7 | 1018 | 3.12 | 32.7 | 194 | 25 | 40.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2018-06-22 09:49 | 60.1 | 44 | 0 | 0 | -67.4 | 67.4 | 1018 | 0.04 | 3.5 | 22 | 99 | 35.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2018-06-22 09:47 | 11.3 | 8.3 | 17.5 | 62.9 | -67.8 | 67.8 | 1018 | -0.02 | 0 | 0 | 99 | 11.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2018-06-22 09:46 | 43.4 | 34.4 | 5.1 | 17.1 | -67.6 | 67.6 | 1018 | 0.02 | 2.3 | 10 | 20 | 10.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2018-06-21 15:55 | 41.2 | 34.9 | 0 | 23.9 | -4.9 | 4.9 | 1018 | 9.09 | 12.8 | 55 | 15 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2018-06-21 15:54 | 0.6 | 0.4 | 20.6 | 78.4 | -65.4 | 65.4 | 1018 | 0.08 | 2.3 | 0 | 0 | 24.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2018-06-21 15:52 | 0.6 | 0.7 | 20 | 78.7 | -65.8 | 65.8 | 1018 | 0.01 | 1 | 0 | 0 | 20.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2018-06-21 15:51 | 0.8 | 0.5 | 20.3 | 78.4 | -65.8 | 65.8 | 1018 | -0.04 | 0 | 0 | 0 | 20.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-06-21 15:49 | 57.2 | 39.2 | 0.4 | 3.2 | -70.9 | 70.9 | 1017 | 30.92 | 48.3 | 290 | 40 | 18.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2018-06-21 15:47 | 44.4 | 35.8 | 0 | 19.8 | -4.9 | 4.9 | 1017 | 6.48 | 22.7 | 105 | 25 | 14.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2018-06-21 15:45 | 31.6 | 31.8 | 0 | 36.6 | 0 | 0 | 1018 | 0.02 | 1.1 | 3 | 5 | 18.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2018-06-21 15:43 | 52.8 | 38.2 | 0 | 9 | -8.6 | 8.6 | 1018 | 21.73 | 40.6 | 224 | 50 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-06-21 15:40 | 39.5 | 26.6 | 6.3 | 27.6 | -2 | 2 | 1018 | 6.38 | 22 | 91 | 15 | 34.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2018-06-21 15:37 | 0.6 | 0.4 | 20.8 | 78.2 | -65.8 | 65.8 | 1018 | 0.03 | 5.4 | 0 | 5 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-06-21 15:36 | 0.2 | 0.1 | 20.9 | 78.8 | -65.8 | 65.8 | 1018 | 0 | 0.7 | 0 | 5 | 21.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2018-06-21 15:34 | 0.3 | 0.1 | 20.8 | 78.8 | -66.1 | 66.1 | 1019 | -0.13 | 0 | 0 | 20 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-06-21 15:31 | 60.5 | 40.7 | 0.1 | 0 | -69.1 | 69.1 | 1015 | 10.89 | 100.7 | 638 | 99 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2018-06-21 15:24 | 60.1 | 41.3 | 0 | 0 | -13.3 | 13.3 | 1015 | -0.01 | 0 | 0 | 5 | 18.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2018-06-21 15:22 | 59.5 | 42.6 | 0 | 0 | -0.4 | 0.4 | 1015 | -0.05 | 0 | 0 | 5 | 30.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2018-06-21 15:21 | 54.8 | 39.5 | 0 | 5.7 | -1.5 | 1.5 | 1015 | 10.21 | 28 | 161 | 25 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-06-21 15:20 | 42.7 | 35.5 | 0 | 21.8 | -0.1 | 0.1 | 1015 | 6.57 | 11 | 49 | 15 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-06-21 15:19 | 49.1 | 38 | 1 | 11.9 | -2.6 | 2.6 | 1015 | 5.02 | 5 | 25 | 10 | 17 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2018-06-21 15:16 | 49.7 | 39.6 | 0 | 10.7 | -47.1 | 47.1 | 1015 | 8.27 | 23.7 | 123 | 50 | 49.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2018-06-21 15:15 | 51.6 | 38.8 | 1.1 | 8.5 | -2.9 | 2.9 | 1015 | 0.54 | 14 | 75 | 25 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2018-06-21 15:14 | 49.8 | 38.9 | 0 | 11.3 | -19 | 19 | 1015 | 16.72 | 34.4 | 179 | 40 | 45.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-06-21 15:13 | 49.6 | 36.8 | 2.9 | 10.7 | -29.9 | 29.9 | 1015 | 4.96 | 4.8 | 25 | 25 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2018-06-21 15:11 | 0.6 | 0.5 | 20.3 | 78.6 | -1.4 | 1.4 | 1015 | -0.02 | 0 | 0 | 0 | 18.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-06-21 14:41 | 55.6 | 39.3 | 0 | 5.1 | 0 | 0 | 1017 | 5.63 | 1.1 | 6 | 20 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2018-06-21 14:40 | 45.9 | 36 | 0 | 18.1 | -12.9 | 12.9 | 1017 | 5.82 | 44.8 | 215 | 40 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-06-21 14:38 | 54.7 | 39.1 | 0 | 6.2 | -0.3 | 0.3 | 1017 | -0.06 | 0 | 0 | 25 | 30.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2018-06-21 14:37 | 49.6 | 37 | 0 | 13.4 | -3.4 | 3.4 | 1017 | 1.43 | 22.4 | 116 | 25 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-06-21 14:36 | 31.8 | 30.2 | 0 | 38 | -1.9 | 1.9 | 1017 | 0.12 | 6.6 | 22 | 20 | 21.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-06-21 14:34 | 50.3 | 35.2 | 2.3 | 12.2 | -0.1 | 0.1 | 1017 | 6.02 | 10.9 | 57 | 25 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-06-21 14:33 | 55.7 | 39.5 | 0 | 4.8 | -0.2 | 0.2 | 1017 | 17.58 | 9.3 | 54 | 20 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-06-21 14:32 | 47.5 | 34.2 | 2.6 | 15.7 | 0 | 0 | 1017 | 1 | 4.3 | 21 | 15 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-06-21 14:30 | 56.6 | 39.3 | 0 | 4.1 | -0.9 | 0.9 | 1017 | 12.35 | 7.8 | 46 | 20 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2018-06-21 14:21 | 47.4 | 36.5 | 0.5 | 15.6 | -3.6 | 3.6 | 1017 | 2.93 | 32.6 | 162 | 40 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2018-06-21 14:20 | 14 | 9.9 | 16.9 | 59.2 | -63.9 | 63.9 | 1017 | 0.01 | 3.2 | 4 | 99 | 19.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2018-06-21 14:19 | 53.2 | 39.5 | 0 | 7.3 | -0.2 | 0.2 | 1017 | 0.09 | 0.6 | 3 | 25 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-06-21 14:17 | 47.7 | 37 | 0.4 | 14.9 | -1.7 | 1.7 | 1017 | 1.09 | 19.7 | 98 | 25 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-06-21 14:15 | 47.9 | 37 | 0.3 | 14.8 | -4.1 | 4.1 | 1017 | 1.38 | 22.2 | 111 | 22 | 25.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-06-21 14:13 | 58.9 | 40.2 | 0 | 0.9 | 0 | 0 | 1017 | 7.51 | 6.2 | 38 | 15 | 18.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2018-06-21 14:11 | 48.8 | 36.6 | 0 | 14.6 | -0.8 | 0.8 | 1017 | 4.98 | 4.9 | 25 | 10 | 21.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2018-06-21 14:09 | 48.9 | 36.8 | 0.5 | 13.8 | -0.9 | 0.9 | 1017 | 4.41 | 18.3 | 94 | 25 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2018-06-21 14:08 | 48.9 | 38.1 | 0.2 | 12.8 | -29 | 29 | 1017 | 22.61 | 86.9 | 445 | 77 | 38.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2018-06-21 14:05 | 48.3 | 38.1 | 0.3 | 13.3 | -0.4 | 0.4 | 1017 | 6.4 | 5.5 | 28 | 10 | 25.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-06-21 14:02 | 29.6 | 30.1 | 0.3 | 40 | -0.3 | 0.3 | 1015 | 6.35 | 5.5 | 17 | 5 | 20.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-06-21 13:58 | 57.3 | 40.1 | 0.3 | 2.3 | -65.7 | 65.7 | 1016 | 0.02 | 4.3 | 26 | 40 | 24.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2018-06-21 13:57 | 49.9 | 38.1 | 0.7 | 11.3 | -1.3 | 1.3 | 1015 | 6.41 | 22.2 | 116 | 20 | 27.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-06-21 13:56 | 47.9 | 37.7 | 0.2 | 14.2 | -0.2 | 0.2 | 1016 | 16.25 | 8.8 | 44 | 10 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2018-06-21 13:54 | 54.8 | 40.2 | 0 | 5 | -64.7 | 64.7 | 1016 | 3.13 | 52 | 299 | 99 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2018-06-21 13:53 | 52.8 | 39.1 | 0 | 8.1 | -19.8 | 19.8 | 1016 | 10.37 | 60 | 332 | 50 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2018-06-21 13:51 | 57.5 | 41.5 | 0 | 1 | -39.2 | 39.2 | 1016 | 18.61 | 37.5 | 226 | 99 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-06-21 13:50 | 43.5 | 37.2 | 0 | 19.3 | 0.2 | -0.2 | 1016 | 0.12 | 6.4 | 29 | 8 | 23.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-06-21 13:49 | 49.4 | 35.1 | 3.1 | 12.4 | -0.8 | 0.8 | 1016 | 2.9 | 32.7 | 169 | 30 | 21.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2018-06-21 13:47 | 50.7 | 38.6 | 0.1 | 10.6 | -23.3 | 23.3 | 1016 | 1.43 | 37 | 196 | 40 | 19.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-06-21 13:45 | 49.1 | 37.8 | 0.7 | 12.4 | 0 | 0 | 1016 | 6.65 | 5.7 | 29 | 40 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-06-21 13:43 | 56.3 | 40 | 0 | 3.7 | 0.2 | -0.2 | 1016 | 0.59 | 1.7 | 10 | 8 | 20.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2018-06-21 13:41 | 50.7 | 39.4 | 0 | 9.9 | -0.1 | 0.1 | 1016 | 1.29 | 9.8 | 52 | 20 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L101 | 2018-06-21 13:40 | 1 | 0.9 | 19.7 | 78.4 | 0 | 0 | 1016 | -0.03 | 0 | 0 | 0 | 23.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-06-21 13:39 | 58.7 | 43.8 | 0 | 0 | -47.8 | 47.8 | 1016 | 0.77 | 1.8 | 11 | 5 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-06-21 13:36 | 52.5 | 41 | 0 | 6.5 | -0.4 | 0.4 | 1016 | 3.27 | 15.3 | 84 | 15 | 47.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2018-06-21 13:35 | 54.9 | 39.5 | 0.1 | 5.5 | -47.8 | 47.8 | 1016 | 13.95 | 109.7 | 631 | 80 | 48.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-06-21 13:33 | 50.6 | 39.7 | 0 | 9.7 | -0.8 | 0.8 | 1016 | 8.18 | 12.1 | 64 | 20 | 41.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-06-21 13:32 | 50.1 | 38.5 | 0.3 | 11.1 | -0.7 | 0.7 | 1016 | 0.76 | 16.2 | 85 | 20 | 35.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2018-06-21 13:30 | 48.2 | 39.6 | 0.3 | 11.9 | 0 | 0 | 1016 | 3.53 | 0.9 | 4 | 5 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2018-06-21 12:11 | 51.3 | 37.5 | 0 | 11.2 | -4.3 | 4.3 | 1018 | 2.54 | 49.4 | 266 | 40 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2018-06-21 12:10 | 64 | 38.3 | 0 | 0 | -54 | 54 | 1018 | 13.35 | 32.3 | 217 | 99 | 24.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2018-06-21 12:08 | 53 | 38 | 0 | 9 | -12.8 | 12.8 | 1018 | 3.92 | 61.5 | 342 | 40 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-06-21 12:07 | 56.7 | 40.4 | 0 | 2.9 | -18.5 | 18.5 | 1017 | 12.55 | 107.9 | 641 | 85 | 35.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-06-20 11:53 | 59 | 43 | 0 | 0 | -0.3 | 0.3 | 1017 | 1.64 | 11.3 | 70 | 20 | 22.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2018-06-20 11:52 | 46.2 | 37.7 | 0 | 16.1 | -2.6 | 2.6 | 1017 | 1.43 | 10.6 | 51 | 20 | 13.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-06-20 11:50 | 46.2 | 35.8 | 2.7 | 15.3 | -0.3 | 0.3 | 1017 | 1.73 | 11.7 | 57 | 25 | 14.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-06-20 11:48 | 35.7 | 31.8 | 2.1 | 30.4 | -0.3 | 0.3 | 1017 | 2.12 | 12.7 | 47 | 12 | 22.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-06-20 11:46 | 55.4 | 39.5 | 0.5 | 4.6 | -51.3 | 51.3 | 1017 | 2.78 | 14.6 | 84 | 30 | 17.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-06-20 11:45 | 44.8 | 36.1 | 0.3 | 18.8 | -1.7 | 1.7 | 1017 | 1.01 | 31.1 | 146 | 25 | 24.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2018-06-20 11:43 | 53.6 | 40.3 | 0.3 | 5.8 | -0.2 | 0.2 | 1017 | 2 | 6.2 | 35 | 10 | 18.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2018-06-20 11:41 | 52 | 38.3 | 0.1 | 9.6 | -4.5 | 4.5 | 1017 | 10.11 | 27.8 | 151 | 30 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2018-06-20 11:27 | 22.9 | 17.3 | 9.7 | 50.1 | 0 | 0 | 1017 | >>>> | 0 | 0 | 5 | 13.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2018-06-20 11:24 | 55.6 | 39.2 | 1 | 4.2 | -0.8 | 0.8 | 1017 | 0 | 0.2 | 1 | 5 | 15.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2018-06-20 11:23 | 44.3 | 31.6 | 4.6 | 19.5 | 0.1 | -0.1 | 1017 | 0.01 | 1 | 4 | 0 | 12 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2018-06-20 11:20 | 44.8 | 33.7 | 4.8 | 16.7 | -8.1 | 8.1 | 1017 | -0.05 | 0 | 0 | 10 | 13.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2018-06-20 11:18 | 50 | 39.1 | 0.7 | 10.2 | -0.2 | 0.2 | 1017 | 2.55 | 7 | 36 | 20 | 17.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-06-20 11:16 | 49.5 | 34.4 | 2.5 | 13.6 | -0.7 | 0.7 | 1017 | 4.6 | 9.5 | 49 | 40 | 17.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-06-20 11:14 | 45.5 | 36.7 | 0 | 17.8 | -0.9 | 0.9 | 1017 | 0.02 | 3 | 14 | 25 | 16.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2018-06-20 11:13 | 50 | 39.7 | 0 | 10.3 | -1.1 | 1.1 | 1017 | 1.16 | 20.6 | 108 | 40 | 15.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2018-06-20 11:11 | 50.4 | 38.8 | 0 | 10.8 | -3.6 | 3.6 | 1017 | 0.79 | 16.9 | 89 | 20 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-06-20 11:10 | 54.5 | 38.8 | 0.8 | 5.9 | -0.7 | 0.7 | 1017 | 1.02 | 19.5 | 111 | 25 | 19.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2018-06-20 11:08 | 53.3 | 39.6 | 0 | 7.1 | -2 | 2 | 1017 | 8.78 | 26.2 | 146 | 40 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-06-20 11:06 | 47.5 | 37.5 | 0.6 | 14.4 | -1 | 1 | 1017 | 8.27 | 12.5 | 62 | 25 | 25.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2018-06-20 11:05 | 51.3 | 39.6 | 0.4 | 8.7 | -2.1 | 2.1 | 1017 | 8.69 | 12.7 | 68 | 25 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2018-06-20 11:03 | 48 | 39.2 | 0 | 12.8 | -0.1 | 0.1 | 1017 | 0.57 | 6.6 | 33 | 25 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2018-06-20 11:02 | 51.8 | 39.1 | 0.4 | 8.7 | 0 | 0 | 1017 | 0.09 | 2.6 | 14 | 20 | 16.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2018-06-20 09:54 | 0.3 | 0.1 | 20.8 | 78.8 | -0.5 | 0.5 | 1019 | 0.41 | 0.3 | 0 | 5 | 8.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2018-06-20 09:50 | 49.4 | 35.9 | 0 | 14.7 | -4 | 4 | 1019 | 2.25 | 6.5 | 34 | 20 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2018-06-20 09:48 | 49.9 | 36.9 | 0 | 13.2 | -1.7 | 1.7 | 1019 | 1.36 | 10.5 | 55 | 25 | 11 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2018-06-20 09:45 | 51.3 | 37.2 | 0 | 11.5 | -4.9 | 4.9 | 1019 | 1.64 | 23.5 | 126 | 40 | 46.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-06-20 09:42 | 0.9 | 0.7 | 20.1 | 78.3 | -54.8 | 54.8 | 1019 | 0.09 | 5.7 | 0 | 99 | 10.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-06-20 09:41 | 55.9 | 37.9 | 0 | 6.2 | -3.3 | 3.3 | 1019 | 0.59 | 7 | 41 | 10 | 13.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2018-06-20 09:40 | 48.4 | 36.8 | 0 | 14.8 | 0 | 0 | 1019 | 2.6 | 3.6 | 18 | 5 | 13 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-06-20 09:38 | 54.5 | 40.3 | 0 | 5.2 | -62.7 | 62.7 | 1019 | 0.04 | 3.7 | 21 | 40 | 13.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-06-20 09:36 | 0.4 | 0.3 | 21 | 78.3 | -12.8 | 12.8 | 1019 | 0.05 | 0.1 | 0 | 5 | 12.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-06-20 09:35 | 56.7 | 39.7 | 0.6 | 3 | -1 | 1 | 1019 | 0.27 | 16.5 | 98 | 25 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-06-20 09:33 | 0.4 | 0.2 | 20.9 | 78.5 | -4.3 | 4.3 | 1019 | 14.25 | 32.9 | 1 | 20 | 22.6 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2018-06-20 09:31 | 61.1 | 42 | 0 | 0 | -52.1 | 52.1 | 1019 | 7.75 | 51.3 | 328 | 99 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-06-20 09:29 | 49.7 | 36.6 | 0 | 13.7 | -15 | 15 | 1019 | 0.93 | 18.3 | 95 | 25 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-06-20 09:27 | 0.4 | 0.3 | 20.5 | 78.8 | -11.3 | 11.3 | 1019 | 0 | 0 | 0 | 10 | 9.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-06-20 09:26 | 54.3 | 38.8 | 0 | 6.9 | 0 | 0 | 1019 | 0.1 | 2.8 | 16 | 10 | 11.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-06-20 09:24 | 46.1 | 35.5 | 0 | 18.4 | -9 | 9 | 1019 | 4.58 | 41.2 | 199 | 40 | 14.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-06-20 09:23 | 43.1 | 30.5 | 0.1 | 26.3 | -3.1 | 3.1 | 1019 | 0.07 | 1.2 | 5 | 5 | 9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-06-20 09:21 | 38.6 | 13.1 | 0.6 | 47.7 | 3.2 | -3.2 | 1019 | 0.14 | 0.1 | 0 | 10 | 7.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-06-20 09:19 | 63.3 | 39.6 | 0 | 0 | -42.6 | 42.6 | 1019 | 0.07 | 2.4 | 15 | 15 | 10.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-06-20 09:16 | 41.2 | 31.1 | 0 | 27.7 | -20.6 | 20.6 | 1019 | 3.87 | 37.4 | 161 | 40 | 18.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-06-20 09:15 | 36.4 | 22.1 | 0 | 41.5 | -1.2 | 1.2 | 1019 | 0.05 | 0.9 | 3 | 5 | 9.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2018-06-20 09:14 | 58.9 | 36 | 0 | 5.1 | -37.5 | 37.5 | 1019 | 16.55 | 2 | 12 | 99 | 11.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-06-20 09:12 | 46.6 | 34.8 | 0 | 18.6 | -64.3 | 64.3 | 1019 | 0.09 | 5.7 | 28 | 40 | 13 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-06-19 08:57 | 47.6 | 37.3 | 0 | 15.1 | -2.6 | 2.6 | 1020 | 4.23 | 17.9 | 89 | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-06-19 08:56 | 48.7 | 37.5 | 0.4 | 13.4 | -20.3 | 20.3 | 1020 | 15.64 | 34.2 | 175 | 40 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-06-19 08:54 | 37 | 27.6 | 6.4 | 29 | -0.6 | 0.6 | 1020 | 0.39 | 5.6 | 21 | 5 | 16.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-06-19 08:49 | 58.2 | 40.2 | 0 | 1.6 | -5.2 | 5.2 | 1020 | 2.57 | 30.8 | 188 | 45 | 23.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2018-06-19 08:46 | 50.3 | 38.9 | 0.1 | 10.7 | -5.1 | 5.1 | 1020 | 2.36 | 29 | 152 | 40 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-06-19 08:43 | 41.8 | 35.1 | 0.8 | 22.3 | -1.9 | 1.9 | 1020 | 0.35 | 5.1 | 22 | 17 | 22.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2018-06-19 08:41 | 48.9 | 39.8 | 0.2 | 11.1 | -68 | 68 | 1020 | 7.26 | 47.5 | 243 | 80 | 45.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2018-06-19 08:38 | 41 | 31.7 | 5.2 | 22.1 | -0.2 | 0.2 | 1020 | -0.02 | 0 | 0 | 10 | 11.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2018-05-24 14:26 | 56.1 | 38.2 | 0 | 5.7 | -3.6 | 3.6 | 1016 | 2.36 | 13.6 | 80 | 40 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2018-05-24 14:24 | 63.8 | 38.7 | 0 | 0 | -39.8 | 39.8 | 1016 | 19.61 | 39.4 | 263 | 99 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2018-05-24 14:23 | 58.5 | 38.4 | 0 | 3.1 | -7.9 | 7.9 | 1016 | 2.21 | 13.3 | 81 | 30 | 24.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-05-24 14:21 | 62.2 | 41.3 | 0 | 0 | -9.4 | 9.4 | 1017 | 6.31 | 22 | 144 | 65 | 35 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2018-05-24 14:12 | 62.3 | 42.4 | 0 | 0 | -32 | 32 | 1018 | 13.23 | 111.2 | 726 | 99 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2018-05-24 14:11 | 62.1 | 42.7 | 0 | 0 | -38.8 | 38.8 | 1018 | -0.13 | 0 | 0 | 99 | 19.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2018-05-24 14:10 | 59.7 | 41.8 | 0 | 0 | -32.4 | 32.4 | 1018 | 15.66 | 121.8 | 762 | 99 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2018-05-24 14:08 | 61 | 42.9 | 0 | 0 | -32.5 | 32.5 | 1018 | 15.85 | 121.8 | 779 | 99 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2018-05-24 14:05 | 59.8 | 39.5 | 0 | 0.7 | -2.8 | 2.8 | 1018 | 1.87 | 12.3 | 77 | 25 | 22.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2018-05-24 14:03 | 49 | 35.9 | 0.1 | 15 | -0.3 | 0.3 | 1018 | 2.37 | 13.6 | 70 | 25 | 22.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2018-05-24 14:02 | 52.6 | 36.7 | 0.2 | 10.5 | -0.6 | 0.6 | 1018 | 1.76 | 11.8 | 65 | 30 | 22.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2018-05-24 14:00 | 51.2 | 36.7 | 0 | 12.1 | -1.9 | 1.9 | 1018 | 7.57 | 24.4 | 131 | 40 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2018-05-24 13:58 | 32.8 | 25.9 | 4.7 | 36.6 | -0.2 | 0.2 | 1018 | 0.34 | 5.1 | 17 | 15 | 23.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2018-05-24 13:55 | 47.3 | 33.9 | 1.1 | 17.7 | 0 | 0 | 1018 | 1.13 | 9.4 | 46 | 20 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-05-24 13:53 | 52.8 | 36.5 | 0.2 | 10.5 | -0.9 | 0.9 | 1017 | 5.09 | 20.1 | 111 | 25 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y478 | 2018-05-24 13:29 | 46.6 | 37.5 | 0.9 | 15 | -0.7 | 0.7 | 1016 | 0.48 | 6.1 | 29 | 5 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y480 | 2018-05-24 13:28 | 56.1 | 41.7 | 0 | 2.2 | -1.1 | 1.1 | 1016 | 5.15 | 20 | 117 | 20 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y483 | 2018-05-24 13:27 | 50.4 | 39.2 | 0.9 | 9.5 | -1 | 1 | 1016 | 2.4 | 13.7 | 72 | 12 | 19.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y481 | 2018-05-24 13:23 | 38.5 | 39.7 | 0 | 21.8 | -0.3 | 0.3 | 1016 | 0.5 | 6 | 24 | 10 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y482 | 2018-05-24 13:22 | 51.4 | 41 | 0 | 7.6 | -1.8 | 1.8 | 1016 | 15.28 | 33.9 | 182 | 40 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2018-05-24 13:20 | 56.7 | 41.1 | 0 | 2.2 | -36.2 | 36.2 | 1016 | 30.73 | 170.1 | 1011 | 99 | 24.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-05-24 13:19 | 42.3 | 32.9 | 1.7 | 23.1 | -13.5 | 13.5 | 1016 | 12.09 | 29.5 | 131 | 20 | 42.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2018-05-24 13:17 | 29.3 | 21.8 | 11 | 37.9 | -0.2 | 0.2 | 1016 | 0.01 | 2.6 | 8 | 0 | 17.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2018-05-24 13:14 | 56.5 | 39.3 | 1.4 | 2.8 | -32.7 | 32.7 | 1016 | 0 | 0 | 0 | 10 | 25.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2018-05-24 13:12 | 57.7 | 42.7 | 0 | 0 | -38.4 | 38.4 | 1016 | 27.61 | 161.8 | 978 | 99 | 20.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2018-05-24 13:10 | 24.2 | 31.7 | 2.9 | 41.2 | -0.2 | 0.2 | 1017 | 0.01 | 1 | 2 | 10 | 19.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2018-05-24 13:07 | 46.9 | 32.6 | 4.3 | 16.2 | -14.5 | 14.5 | 1017 | 0.74 | 16.3 | 80 | 10 | 25.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2018-05-24 13:04 | 49.2 | 35.8 | 0 | 15 | -12.3 | 12.3 | 1017 | 19.01 | 37.8 | 195 | 40 | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-05-24 13:03 | 52.2 | 36.5 | 0 | 11.3 | -9.7 | 9.7 | 1017 | 19.01 | 83.5 | 456 | 60 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-05-24 13:02 | 44.2 | 36.4 | 0 | 19.4 | -4.2 | 4.2 | 1017 | 21.91 | 39.7 | 183 | 40 | 43.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-05-24 13:00 | 53.7 | 40 | 0 | 6.3 | -41.6 | 41.6 | 1017 | 18.01 | 76.7 | 431 | 99 | 44.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2018-05-24 12:59 | 34.2 | 32.8 | 0 | 33 | -57.5 | 57.5 | 1017 | -0.12 | 0 | 0 | 99 | 19.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-05-24 12:58 | 14 | 26.6 | 0 | 59.4 | 0 | 0 | 1017 | -0.02 | 0 | 0 | 5 | 25 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2018-05-24 12:56 | 63 | 39.2 | 0 | 0 | -29.9 | 29.9 | 1017 | 4.19 | 18 | 119 | 99 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2018-05-24 12:55 | 54.8 | 36.9 | 0 | 8.3 | -20.3 | 20.3 | 1017 | 27.87 | 46.1 | 264 | 60 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-05-24 12:54 | 55.7 | 38 | 0.3 | 6 | -1.2 | 1.2 | 1018 | 25.78 | 22.6 | 132 | 25 | 19.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-05-24 12:52 | 55.8 | 39.4 | 0.7 | 4.1 | -17.9 | 17.9 | 1018 | 16.22 | 34.5 | 202 | 40 | 41 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P477 | 2018-05-24 12:07 | 57.1 | 39.8 | 0 | 3.1 | -1.7 | 1.7 | 1018 | 1.91 | 26.3 | 157 | 42 | 28.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-05-24 12:05 | 48.2 | 35.5 | 1.6 | 14.7 | 0 | 0 | 1018 | 2.21 | 6.5 | 32 | 5 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-05-24 12:03 | 48.1 | 33.7 | 2.2 | 16 | -3.1 | 3.1 | 1018 | 6.39 | 47.6 | 240 | 40 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-05-24 12:02 | 47.2 | 31.4 | 4.1 | 17.3 | -58.8 | 58.8 | 1018 | -0.11 | 0 | 0 | 50 | 21.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-05-24 12:00 | 48.6 | 37.2 | 0.3 | 13.9 | -31.3 | 31.3 | 1018 | 6.62 | 47.1 | 240 | 50 | 37.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-05-24 11:58 | 17.7 | 12.1 | 14.8 | 55.4 | 0 | 0 | 1018 | 0.09 | 0.6 | 1 | 2 | 20.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2018-05-24 11:57 | 45 | 36 | 0 | 19 | -1.6 | 1.6 | 1018 | 1.88 | 5.9 | 28 | 15 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2018-05-24 11:56 | 55.3 | 38 | 0 | 6.7 | -51.9 | 51.9 | 1018 | 7.11 | 81.5 | 472 | 99 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2018-05-24 11:54 | 45.9 | 32 | 0 | 22.1 | -0.8 | 0.8 | 1018 | 7.26 | 1.3 | 6 | 5 | 19.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-05-24 11:53 | 45.7 | 34.8 | 0 | 19.5 | -2.9 | 2.9 | 1018 | 4.4 | 18.5 | 88 | 20 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-05-24 11:52 | 36.8 | 27.4 | 5.2 | 30.6 | -3.4 | 3.4 | 1018 | 4.16 | 38.3 | 147 | 35 | 30.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2018-05-24 11:49 | 53.4 | 39.1 | 0 | 7.5 | -0.3 | 0.3 | 1018 | 2.13 | 12.7 | 71 | 25 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2018-05-24 11:48 | 49.6 | 36.8 | 0 | 13.6 | -37.8 | 37.8 | 1017 | 27.81 | 97.6 | 507 | 99 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-05-24 11:46 | 41.8 | 35.5 | 0.7 | 22 | -6 | 6 | 1017 | 4.04 | 17.1 | 75 | 25 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2018-05-24 11:44 | 49.4 | 39.4 | 0 | 11.2 | -37.4 | 37.4 | 1017 | 30.22 | 161.3 | 835 | 99 | 45.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-05-24 11:43 | 29 | 29.2 | 1.8 | 40 | -4.9 | 4.9 | 1018 | 2.88 | 14.6 | 44 | 10 | 24.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-05-24 11:40 | 47.5 | 34.8 | 3.6 | 14.1 | -1.2 | 1.2 | 1018 | 0.41 | 12.2 | 61 | 10 | 23.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2018-05-24 11:38 | 48.8 | 38.2 | 0 | 13 | -2.7 | 2.7 | 1018 | 1.36 | 22.1 | 113 | 25 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-05-24 11:37 | 43.9 | 35.8 | 0 | 20.3 | -5.4 | 5.4 | 1018 | 4.64 | 39.8 | 183 | 40 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-05-24 11:36 | 51.2 | 37.7 | 1.2 | 9.9 | -0.1 | 0.1 | 1018 | 4.92 | 9.7 | 52 | 10 | 26.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2018-05-24 11:34 | 53 | 37.8 | 0 | 9.2 | -7.8 | 7.8 | 1018 | 5.42 | 44.2 | 245 | 40 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2018-05-24 11:33 | 59.8 | 40.6 | 0 | 0 | -58.6 | 58.6 | 1018 | -0.02 | 0 | 0 | 70 | 27 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-05-24 11:31 | 52 | 37 | 0.4 | 10.6 | -4.5 | 4.5 | 1018 | 1.32 | 22.2 | 121 | 20 | 18.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-05-24 11:30 | 50.4 | 35.5 | 2.4 | 11.7 | 0 | 0 | 1018 | 4.72 | 4.8 | 25 | 5 | 21.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-05-24 11:29 | 46.7 | 38 | 0 | 15.3 | -0.2 | 0.2 | 1018 | 5.13 | 4.9 | 24 | 10 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2018-05-24 10:56 | 60.1 | 43.4 | 0 | 0 | -60 | 60 | 1017 | 0.93 | 28.7 | 181 | 99 | 33.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2018-05-24 10:55 | 12.7 | 12.1 | 13.7 | 61.5 | -0.5 | 0.5 | 1017 | 0.01 | 0.2 | 0 | 0 | 26.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2018-05-24 10:54 | 60.2 | 43.7 | 0 | 0 | -56.7 | 56.7 | 1017 | 2.05 | 12.1 | 76 | 99 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2018-05-24 10:52 | 9.2 | 6.5 | 17.6 | 66.7 | -60.4 | 60.4 | 1017 | 0.31 | 4.7 | 4 | 99 | 17 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2018-05-24 10:51 | 48.7 | 37.3 | 0 | 14 | -24 | 24 | 1017 | 10.9 | 62.3 | 318 | 50 | 21.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2018-05-24 10:50 | 61.3 | 43.2 | 0 | 0 | -60.2 | 60.2 | 1017 | 0.62 | 6.8 | 43 | 99 | 19.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2018-05-24 10:48 | 0.6 | 3.5 | 18 | 77.9 | -3.7 | 3.7 | 1017 | 0.02 | 2.4 | 0 | 5 | 25.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2018-05-24 10:47 | 50 | 37.9 | 0.5 | 11.6 | -26.6 | 26.6 | 1017 | 6.39 | 46 | 241 | 50 | 43.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2018-05-24 10:46 | 49.8 | 38.2 | 0 | 12 | -57.4 | 57.4 | 525 | 3.23 | 52.9 | 276 | 99 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-05-24 10:44 | 51.4 | 39.9 | 0.3 | 8.4 | -1.3 | 1.3 | 1017 | 1.93 | 11.8 | 63 | 40 | 46 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2018-05-24 10:41 | 51.5 | 38.8 | 0.8 | 8.9 | -42.5 | 42.5 | 1017 | 18.56 | 76.8 | 415 | 99 | 51.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2018-05-24 10:40 | 60.5 | 42.2 | 0 | 0 | -50.4 | 50.4 | 1017 | 8.08 | 51.6 | 327 | 99 | 43.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2018-05-24 10:39 | 58.6 | 41.6 | 0.1 | 0 | -49.5 | 49.5 | 1017 | 10.47 | 95.8 | 588 | 99 | 44.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2018-05-24 10:37 | 40.2 | 32.2 | 3.4 | 24.2 | -1.8 | 1.8 | 1017 | 0.01 | 0.6 | 2 | 0 | 31.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-05-24 10:36 | 44.5 | 33.8 | 4.2 | 17.5 | -28.2 | 28.2 | 1017 | 5.01 | 40.3 | 188 | 40 | 47.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-05-24 10:34 | 61.6 | 42.8 | 0 | 0 | -58.8 | 58.8 | 1017 | 0.46 | 12.3 | 79 | 99 | 38.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2018-05-24 10:33 | 0.7 | 0.4 | 19.5 | 79.4 | -58.3 | 58.3 | 1017 | 0.05 | 1.8 | 0 | 0 | 16.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-05-24 10:32 | 51.9 | 40.2 | 0.2 | 7.7 | -0.6 | 0.6 | 1017 | 1.23 | 9.8 | 53 | 15 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-05-24 10:30 | 50.9 | 38.5 | 0.9 | 9.7 | -21.8 | 21.8 | 1017 | 5.83 | 44.1 | 235 | 50 | 43.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-05-24 10:28 | 56 | 42.6 | 0 | 1.4 | -54 | 54 | 1017 | 7.26 | 48.4 | 284 | 99 | 41.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-05-24 10:27 | 56 | 42.6 | 0 | 1.4 | -54 | 54 | 1017 | 7.26 | 48.4 | 284 | 99 | 41.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2018-05-24 10:26 | 2.9 | 2.4 | 20.6 | 74.1 | -27.7 | 27.7 | 1017 | 0.02 | 2.3 | 0 | 0 | 15.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2018-05-24 10:24 | 2.8 | 2.1 | 20.1 | 75 | 0 | 0 | 1017 | 0 | 0.1 | 0 | 0 | 15 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2018-05-24 10:23 | 1.1 | 1.1 | 20.6 | 77.2 | -54.8 | 54.8 | 1017 | 0.05 | 1.8 | 0 | 5 | 22 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2018-05-24 10:21 | 60.7 | 41.9 | 0 | 0 | -58.6 | 58.6 | 1017 | 1.44 | 35.8 | 227 | 99 | 39 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2018-05-24 10:20 | 51.5 | 38.7 | 0.2 | 9.6 | -5.1 | 5.1 | 1017 | 8.66 | 26 | 140 | 25 | 22.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-05-24 10:18 | 49.1 | 37.5 | 0.2 | 13.2 | -2.6 | 2.6 | 1017 | 4.07 | 17.7 | 91 | 15 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-05-24 10:17 | 48.7 | 37.8 | 0.5 | 13 | -5.9 | 5.9 | 1017 | 1.51 | 23.4 | 119 | 25 | 19.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-05-24 10:15 | 56.4 | 41 | 0 | 2.6 | -2.4 | 2.4 | 1017 | 1.33 | 21.9 | 129 | 40 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2018-05-24 09:39 | 47.1 | 36 | 0 | 16.9 | -2.5 | 2.5 | 1018 | 3.86 | 8.6 | 42 | 10 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-05-24 09:38 | 43.3 | 33.5 | 0 | 23.2 | -1.8 | 1.8 | 1019 | 0.89 | 18.1 | 82 | 15 | 17.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-05-24 09:37 | 45.9 | 33.6 | 4.5 | 16 | -1.3 | 1.3 | 1019 | 0.2 | 3.9 | 19 | 10 | 19.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-05-24 09:34 | 8.6 | 5.8 | 15.2 | 70.4 | -65.3 | 65.3 | 1019 | 0.24 | 15 | 13 | 99 | 13.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-05-24 09:33 | 45.8 | 31 | 4.8 | 18.4 | -0.7 | 0.7 | 1019 | 0.12 | 3.1 | 14 | 5 | 16.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-05-24 09:31 | 48 | 37 | 0 | 15 | -6.3 | 6.3 | 1019 | 4.15 | 17.8 | 89 | 25 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-05-24 09:29 | 45.4 | 36.3 | 0.3 | 18 | -1 | 1 | 1019 | 4.74 | 9.5 | 45 | 20 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2018-05-24 09:28 | 0.4 | 0.3 | 20.8 | 78.5 | -0.1 | 0.1 | 1019 | 0 | 0 | 0 | 5 | 14.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2018-05-24 09:27 | 46.6 | 33.9 | 0 | 19.5 | -0.9 | 0.9 | 1019 | 2.13 | 13 | 63 | 15 | 17.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-05-24 09:25 | 5.3 | 3.1 | 19.3 | 72.3 | -0.4 | 0.4 | 1019 | 0 | 0 | 0 | 0 | 18.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-05-24 09:24 | 55.7 | 38.9 | 0.7 | 4.7 | -11 | 11 | 1019 | 4.66 | 19.2 | 112 | 25 | 22.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2018-05-24 09:23 | 51 | 39.6 | 0.1 | 9.3 | -0.9 | 0.9 | 1019 | 1.31 | 10 | 53 | 20 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2018-05-24 09:20 | 45.6 | 36.7 | 0 | 17.7 | -0.5 | 0.5 | 1019 | 0.37 | 11.4 | 54 | 15 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2018-05-24 09:18 | 49.7 | 37.3 | 0 | 13 | -1.8 | 1.8 | 1019 | 5.62 | 20.5 | 107 | 25 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-05-24 09:15 | 55.5 | 36.5 | 0 | 8 | -3 | 3 | 1018 | 7.25 | 24.3 | 141 | 40 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2018-05-24 09:11 | 52.9 | 38.6 | 0 | 8.5 | -83.1 | 83.1 | 1018 | 0.02 | 2.2 | 12 | 99 | 23.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2018-05-24 09:09 | 49.5 | 37.7 | 0 | 12.8 | -39.9 | 39.9 | 1018 | 3.69 | 16.5 | 85 | 50 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2018-05-24 09:08 | 10 | 6.1 | 18.3 | 65.6 | -3.4 | 3.4 | 1018 | 0.06 | 2.1 | 2 | 0 | 18.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-05-24 09:06 | 0.4 | 0.2 | 20.8 | 78.6 | -50.9 | 50.9 | 1018 | -0.57 | 0 | 0 | 2 | 28.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2018-05-24 09:05 | 45.7 | 37.4 | 0 | 16.9 | -13.6 | 13.6 | 1018 | 6.96 | 22.4 | 107 | 40 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-05-24 09:04 | 51.3 | 39.3 | 0 | 9.4 | -23.3 | 23.3 | 1018 | 8.22 | 24.9 | 134 | 40 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-05-24 09:02 | 0.4 | 0.2 | 20.8 | 78.6 | -2.5 | 2.5 | 1018 | 0.04 | 1.8 | 0 | 3 | 29.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-05-24 09:01 | 54.3 | 38.6 | 0.3 | 6.8 | -42.1 | 42.1 | 1018 | 14.74 | 115.6 | 658 | 90 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-05-24 08:59 | 38.7 | 34.7 | 0 | 26.6 | -1.1 | 1.1 | 1018 | 1.85 | 11.8 | 47 | 22 | 25.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-05-24 08:58 | 45.1 | 36.5 | 0.4 | 18 | -15.6 | 15.6 | 1018 | 1.83 | 25.3 | 119 | 22 | 26.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-05-24 08:55 | 46.2 | 36 | 0.2 | 17.6 | -26.3 | 26.3 | 1018 | 1.85 | 24.9 | 120 | 22 | 37.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2018-05-24 08:53 | 49.3 | 36.7 | 0 | 14 | -6.7 | 6.7 | 1018 | 5.57 | 44.5 | 230 | 40 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-05-24 08:52 | 33.5 | 28.4 | 3.4 | 34.7 | -0.2 | 0.2 | 1018 | 6.22 | 5.5 | 19 | 7 | 22.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2018-05-24 08:50 | 43.5 | 35.9 | 0 | 20.6 | -63.5 | 63.5 | 1018 | 0.89 | 27.7 | 126 | 99 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2018-05-22 15:02 | 5.8 | 12.3 | 10.7 | 71.2 | -64.4 | 64.4 | 1015 | 0.05 | 1.7 | 1 | 2 | 21.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2018-05-22 15:01 | 0.8 | 0.6 | 20 | 78.6 | -64.3 | 64.3 | 1015 | 0.04 | 1.7 | 0 | 0 | 22.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2018-05-22 14:59 | 42.7 | 35.3 | 0 | 22 | -4.7 | 4.7 | 1015 | 9.26 | 13 | 58 | 25 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-05-22 14:56 | 59 | 39.9 | 0.3 | 0.8 | -64.4 | 64.4 | 1015 | 14.49 | 33 | 204 | 45 | 22.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2018-05-22 14:54 | 1 | 0.7 | 20.2 | 78.1 | -54.5 | 54.5 | 1015 | -0.04 | 0 | 0 | 5 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2018-05-22 14:51 | 39.7 | 34.2 | 0 | 26.1 | 0 | 0 | 1015 | -0.02 | 0 | 0 | 5 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2018-05-22 14:49 | 56.6 | 38.7 | 0 | 4.7 | -7.6 | 7.6 | 1015 | 19.29 | 38.5 | 228 | 40 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-05-22 14:46 | 41.4 | 28.6 | 5.1 | 24.9 | -5.7 | 5.7 | 1015 | 13.68 | 31.9 | 138 | 15 | 38.5
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2018-05-22 14:43 | 1.8 | 1.3 | 20.1 | 76.8 | -66.1 | 66.1 | 1015 | -0.05 | 0 | 0 | 5 | 22.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-05-22 14:42 | 0.2 | 0.1 | 20.6 | 79.1 | -65 | 65 | 1015 | -0.03 | 0 | 0 | 5 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2018-05-22 14:40 | 0.2 | 0.1 | 20.7 | 79 | -66.1 | 66.1 | 1016 | 0.01 | 3.5 | 0 | 5 | 21.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-05-22 14:38 | 60.1 | 40.3 | 0.2 | 0 | -69.4 | 69.4 | 1015 | 10.92 | 101.3 | 638 | 99 | 21 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-05-22 14:12 | 45.5 | 35.2 | 0 | 19.3 | -0.2 | 0.2 | 1015 | 1.99 | 6.2 | 29 | 15 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2018-05-22 14:09 | 45.9 | 36.2 | 0 | 17.9 | -4.9 | 4.9 | 1014 | 6.34 | 22.2 | 107 | 25 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-05-22 14:06 | 49.6 | 36.6 | 0 | 13.8 | -0.4 | 0.4 | 1015 | 1.95 | 6.1 | 32 | 10 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2018-05-22 14:04 | 35.8 | 25.7 | 7.8 | 30.7 | -0.6 | 0.6 | 1015 | 7.2 | 1.3 | 4 | 7 | 15.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2018-05-22 13:59 | 50.2 | 35.6 | 0 | 14.2 | -3.9 | 3.9 | 1015 | 2.01 | 6.2 | 32 | 20 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2018-05-22 13:56 | 54 | 36.7 | 0 | 9.3 | -1.7 | 1.7 | 1015 | 1.27 | 10.2 | 57 | 25 | 16.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2018-05-22 13:54 | 48.6 | 36.1 | 0.1 | 15.2 | -5 | 5 | 1015 | 1.6 | 23.1 | 118 | 25 | 46.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-05-22 13:47 | 61.4 | 40.6 | 0 | 0 | -62.1 | 62.1 | 1015 | 0.14 | 7.1 | 45 | 99 | 17.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-05-22 13:46 | 59.7 | 38.1 | 0 | 2.2 | -1.7 | 1.7 | 1015 | 0.58 | 6.9 | 43 | 12 | 18.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2018-05-22 13:44 | 44.1 | 34.8 | 0 | 21.1 | -0.1 | 0.1 | 1015 | 2.69 | 3.6 | 16 | 10 | 19 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-05-22 13:43 | 51 | 37.7 | 0.1 | 11.2 | -50 | 50 | 1015 | 1.42 | 22.3 | 119 | 40 | 20.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-05-22 13:41 | 0.4 | 0.3 | 20.4 | 78.9 | -10.6 | 10.6 | 1015 | 0.75 | 0.4 | 0 | 3 | 18.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-05-22 13:40 | 51.9 | 37.2 | 1.2 | 9.7 | -1.6 | 1.6 | 1015 | 1.23 | 34.7 | 189 | 20 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-05-22 13:38 | 53.5 | 38.3 | 0.4 | 7.8 | -0.9 | 0.9 | 1015 | 5.8 | 21.2 | 119 | 25 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2018-05-22 13:37 | 60.7 | 41.3 | 0 | 0 | -52.7 | 52.7 | 1015 | 9.89 | 57.7 | 367 | 99 | 37.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-05-22 13:36 | 50 | 36.1 | 0 | 13.9 | -8.3 | 8.3 | 1015 | 0.45 | 12.7 | 67 | 25 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-05-22 13:34 | 0.4 | 0.3 | 20.4 | 78.9 | -26.2 | 26.2 | 1015 | -0.06 | 0 | 0 | 10 | 17.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-05-22 13:33 | 43.9 | 34.4 | 0.9 | 20.8 | -0.3 | 0.3 | 1015 | 0.28 | 4.7 | 21 | 5 | 19.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-05-22 13:31 | 50.9 | 37 | 0 | 12.1 | -5.8 | 5.8 | 1015 | 4.86 | 42.3 | 226 | 40 | 20.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-05-22 13:30 | 47.2 | 33 | 0.7 | 19.1 | -6.3 | 6.3 | 1015 | 0.31 | 2.4 | 12 | 7 | 18.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-05-22 13:28 | 17 | 20.5 | 1.6 | 60.9 | -0.2 | 0.2 | 1015 | 1.08 | 0.5 | 0 | 3 | 16.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-05-22 13:26 | 52.7 | 33.3 | 2.8 | 11.2 | -50.6 | 50.6 | 1015 | 0.01 | 0.6 | 3 | 5 | 17.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-05-22 13:24 | 42.5 | 31.7 | 0 | 25.8 | -16.3 | 16.3 | 1015 | 4.02 | 38 | 169 | 50 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-05-22 13:22 | 25.6 | 17.9 | 5.9 | 50.6 | -2 | 2 | 1015 | 0.13 | 1.6 | 4 | 5 | 18.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2018-05-22 13:21 | 54.6 | 34.1 | 0 | 11.3 | -29.3 | 29.3 | 1016 | 31.21 | 2.7 | 15 | 99 | 19.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-05-22 13:20 | 48.9 | 34 | 0 | 17.1 | -61.7 | 61.7 | 1015 | 0.17 | 7.6 | 39 | 40 | 20.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2018-05-22 11:52 | 61.3 | 41.9 | 0 | 0 | -9.8 | 9.8 | 1012 | 0.04 | 1.8 | 11 | 5 | 17.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2018-05-22 11:50 | 59.7 | 42.8 | 0 | 0 | -0.4 | 0.4 | 1013 | 0 | 1.8 | 11 | 10 | 27.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2018-05-22 11:49 | 54 | 39.6 | 0 | 6.4 | -1.3 | 1.3 | 1013 | 10.76 | 28.6 | 162 | 25 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-05-22 11:47 | 42.4 | 35.8 | 0 | 21.8 | 0 | 0 | 1012 | 6.65 | 11.1 | 49 | 10 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-05-22 11:46 | 45.2 | 37.4 | 0.4 | 17 | -3.9 | 3.9 | 1012 | 10.26 | 7 | 33 | 10 | 20.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2018-05-22 11:44 | 49.3 | 40.1 | 0 | 10.6 | -47 | 47 | 1013 | 7.21 | 22 | 114 | 70 | 49.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2018-05-22 11:43 | 51 | 39 | 0.9 | 9.1 | -4.1 | 4.1 | 1013 | 0.17 | 7.8 | 42 | 15 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2018-05-22 11:41 | 50.3 | 39.2 | 0 | 10.5 | -19.1 | 19.1 | 1013 | 15.7 | 33.4 | 176 | 50 | 45.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-05-22 11:40 | 52.8 | 39.1 | 2 | 6.1 | -28.1 | 28.1 | 1013 | 4.94 | 4.8 | 26 | 15 | 24.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2018-05-22 11:39 | 1.6 | 1.5 | 19.9 | 77 | -1.5 | 1.5 | 1013 | 0.01 | 0 | 0 | 0 | 20.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2018-05-22 11:31 | 50.5 | 39.6 | 0 | 9.9 | -6.2 | 6.2 | 1014 | 5.01 | 9.8 | 52 | 15 | 16.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-05-22 11:30 | 45.6 | 37.7 | 0 | 16.7 | -3.4 | 3.4 | 1014 | 1.11 | 20.1 | 96 | 20 | 16.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-05-22 11:29 | 55.8 | 41.1 | 0 | 3.1 | -77.6 | 77.6 | 1014 | 0.83 | 16.9 | 99 | 25 | 16.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-05-22 11:27 | 46.4 | 37.8 | 0 | 15.8 | -3.7 | 3.7 | 1014 | 11.51 | 29.9 | 145 | 40 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-05-22 11:25 | 41.6 | 32.9 | 3.8 | 21.7 | -0.7 | 0.7 | 1013 | 0.03 | 3.1 | 13 | 10 | 25.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-05-22 11:22 | 45.8 | 36.9 | 0 | 17.3 | -3.8 | 3.8 | 1013 | 7.11 | 23 | 110 | 25 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-05-22 11:21 | 52.1 | 39.5 | 0.9 | 7.5 | -34.3 | 34.3 | 1013 | 0.86 | 27.7 | 151 | 40 | 38.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-05-22 11:19 | 48.5 | 38 | 0 | 13.5 | -1.3 | 1.3 | 1013 | 2.21 | 13.1 | 66 | 15 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2018-05-22 11:18 | 1 | 1.6 | 16.2 | 81.2 | 0 | 0 | 1013 | 0.11 | 2.9 | 0 | 0 | 21.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2018-05-22 11:17 | 55 | 40.1 | 0 | 4.9 | -65.1 | 65.1 | 1013 | 0.79 | 26.8 | 154 | 99 | 25.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-05-22 11:15 | 36 | 34.2 | 0 | 29.8 | -0.3 | 0.3 | 1013 | 7.05 | 22.2 | 84 | 25 | 44.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2018-05-22 11:07 | 3.9 | 3.2 | 19 | 73.9 | -11.6 | 11.6 | 1013 | -0.06 | 0 | 0 | 0 | 33.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2018-05-22 11:06 | 61.1 | 42.1 | 0 | 0 | -65.4 | 65.4 | 1013 | 1.59 | 37.3 | 238 | 99 | 42.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2018-05-22 11:05 | 7.5 | 5.2 | 18.4 | 68.9 | -66.5 | 66.5 | 1013 | -0.02 | 0 | 0 | 99 | 16.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2018-05-22 11:04 | 3.6 | 2.9 | 19.7 | 73.8 | -66.9 | 66.9 | 1013 | 0 | 0 | 0 | 99 | 16.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2018-05-22 11:03 | 8.9 | 6.9 | 16.9 | 67.3 | -1.4 | 1.4 | 1013 | -0.02 | 0 | 0 | 0 | 17.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2018-05-22 11:01 | 49 | 37.9 | 0.4 | 12.7 | -0.6 | 0.6 | 1013 | 9.66 | 6.8 | 35 | 15 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-05-22 11:00 | 56.8 | 41.1 | 0 | 2.1 | -9.6 | 9.6 | 1013 | 2.25 | 27.8 | 166 | 40 | 39.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2018-05-22 10:58 | 58.7 | 43.3 | 0.2 | 0 | -66.5 | 66.5 | 1013 | 0.03 | 3.1 | 19 | 99 | 35.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2018-05-22 10:57 | 5.5 | 4.3 | 18.9 | 71.3 | -66.9 | 66.9 | 1013 | -0.01 | 0 | 0 | 99 | 15.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2018-05-22 10:56 | 39.3 | 31.5 | 6.5 | 22.7 | -66.4 | 66.4 | 1013 | 0.01 | 1.9 | 7 | 40 | 15.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-05-22 09:07 | 11.1 | 20.8 | 1.7 | 66.4 | -0.3 | 0.3 | 1014 | 30.35 | 2.6 | 3 | 10 | 20.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2018-05-22 09:05 | 53 | 38.4 | 0 | 8.6 | -12.5 | 12.5 | 1014 | 5.64 | 44.4 | 247 | 40 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-05-22 09:02 | 51 | 38.2 | 0 | 10.8 | -0.9 | 0.9 | 1014 | 0.53 | 13.7 | 73 | 20 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2018-05-22 09:01 | 49.9 | 37.2 | 0 | 12.9 | -3.6 | 3.6 | 1014 | 1.33 | 21.6 | 113 | 25 | 33.4 | oK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-05-22 08:59 | 38.5 | 33.6 | 0 | 27.9 | -4.5 | 4.5 | 1014 | 0.32 | 10.5 | 42 | 17 | 25.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-05-22 08:57 | 27.2 | 20.2 | 9.8 | 42.8 | -0.5 | 0.5 | 1014 | 10.5 | 14.3 | 40 | 15 | 16.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-05-22 08:56 | 53.6 | 38.7 | 0.3 | 7.4 | -0.5 | 0.5 | 1014 | 14.88 | 8.5 | 48 | 15 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-05-22 08:54 | 16.4 | 13.2 | 13.3 | 57.1 | -0.3 | 0.3 | 1014 | 2.12 | 6.3 | 10 | 7 | 25 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-05-22 08:53 | 55.4 | 39 | 0 | 5.6 | -1.2 | 1.2 | 1014 | 11.77 | 7.6 | 44 | 20 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-05-21 15:41 | 62.6 | 45 | 0 | 0 | -77.8 | 77.8 | 1011 | 4.37 | 38.3 | 251 | 99 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-05-21 15:39 | 61.2 | 46.8 | 0 | 0 | -74.7 | 74.7 | 1011 | 10.65 | 59.7 | 383 | 99 | 24.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-05-21 15:38 | 59.9 | 47.9 | 0 | 0 | -68.7 | 68.7 | 1011 | 22.68 | 87.9 | 551 | 99 | 17.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2018-05-21 15:37 | 45.4 | 46 | 0 | 8.6 | -8.6 | 8.6 | 1011 | 10.17 | 59.3 | 282 | 50 | 16.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2018-05-21 15:36 | 48.6 | 41.5 | 3.5 | 6.4 | -83.5 | 83.5 | 1011 | 0.02 | 2.7 | 14 | 99 | 18.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-05-21 15:27 | 45.5 | 38.1 | 0 | 16.4 | -0.6 | 0.6 | 1011 | 2.33 | 13.2 | 63 | 25 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2018-05-21 15:25 | 44.3 | 36.6 | 0 | 19.1 | -3.8 | 3.8 | 1011 | 2.52 | 14 | 65 | 25 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-05-21 15:23 | 50.4 | 37.5 | 1.9 | 10.2 | -0.1 | 0.1 | 1011 | 1.87 | 12.1 | 64 | 20 | 19.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-05-21 15:22 | 37.9 | 33.3 | 1.4 | 27.4 | 0 | 0 | 1011 | 2.07 | 12.4 | 49 | 15 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-05-21 15:21 | 60.8 | 41.5 | 0 | 0 | -31.6 | 31.6 | 1011 | 0.44 | 5.8 | 37 | 28 | 20.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-05-21 15:18 | 48.5 | 36.8 | 0.2 | 14.5 | -1.2 | 1.2 | 1011 | 0.32 | 17.4 | 88 | 30 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2018-05-21 15:17 | 47.5 | 37 | 0.7 | 14.8 | -1.6 | 1.6 | 1011 | 3.33 | 7.9 | 39 | 20 | 24.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2018-05-21 15:15 | 51.4 | 37.6 | 0.2 | 10.8 | -4.8 | 4.8 | 1013 | 9.53 | 26.9 | 145 | 40 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2018-05-21 13:59 | 47.3 | 36.8 | 0.6 | 15.3 | -3.7 | 3.7 | 1011 | 2.84 | 30.9 | 153 | 40 | 43.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2018-05-21 13:58 | 8 | 4.8 | 16.7 | 70.5 | -61.2 | 61.2 | 1011 | 0 | 0 | 0 | 90 | 15.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2018-05-21 13:57 | 56.8 | 40.4 | 0 | 2.8 | -0.2 | 0.2 | 1011 | 0.04 | 0.4 | 2 | 25 | 15.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-05-21 13:55 | 49.6 | 38.2 | 0.1 | 12.1 | -1.7 | 1.7 | 1011 | 1.35 | 22 | 114 | 25 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-05-21 13:54 | 50.7 | 38.3 | 0 | 11 | -3.9 | 3.9 | 1011 | 1.34 | 22 | 116 | 25 | 25.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-05-21 13:52 | 54.7 | 38.7 | 0 | 6.6 | 0 | 0 | 1011 | 6.68 | 5.8 | 33 | 5 | 17.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2018-05-21 13:51 | 46.9 | 35.9 | 0 | 17.2 | -0.8 | 0.8 | 1011 | 4.59 | 4.8 | 23 | 10 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2018-05-21 13:50 | 60.9 | 40.9 | 0 | 0 | 0 | 0 | 1011 | 0.31 | 10.7 | 68 | 15 | 25.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2018-05-21 13:48 | 49.3 | 38.5 | 0.1 | 12.1 | -28.3 | 28.3 | 1011 | 22.74 | 87.2 | 450 | 80 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2018-05-21 13:47 | 49.7 | 38.9 | 0.3 | 11.1 | -0.2 | 0.2 | 1011 | 5.83 | 5.3 | 27 | 10 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-05-21 13:45 | 42.5 | 36.2 | 0 | 21.3 | -0.1 | 0.1 | 1011 | 6.14 | 5.4 | 24 | 5 | 19.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-05-21 13:32 | 59.8 | 41.5 | 0 | 0 | -57.4 | 57.4 | 1010 | 0.17 | 12.7 | 79 | 30 | 24.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2018-05-21 13:31 | 52.5 | 39.5 | 0.2 | 7.8 | -1.3 | 1.3 | 1010 | 6.22 | 21.8 | 120 | 25 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-05-21 13:29 | 60 | 42.2 | 0 | 0 | 0.1 | -0.1 | 1010 | 3.91 | 4.4 | 28 | 8 | 21.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2018-05-21 13:27 | 56.8 | 41.1 | 0 | 2.1 | -62.8 | 62.8 | 1010 | 3.37 | 54.1 | 322 | 99 | 40.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2018-05-21 13:26 | 53.9 | 39.7 | 0 | 6.4 | -14.9 | 14.9 | 1010 | 12.03 | 64.6 | 365 | 50 | 35 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2018-05-21 13:24 | 58.1 | 41.4 | 0 | 0.5 | -38.1 | 38.1 | 1010 | 19.13 | 38 | 232 | 99 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-05-21 13:23 | 47.4 | 38.8 | 0 | 13.8 | 0 | 0 | 1010 | 0.15 | 7.2 | 35 | 10 | 23.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-05-21 13:21 | 60.9 | 42.1 | 0 | 0 | -0.2 | 0.2 | 1010 | 1.22 | 21.3 | 136 | 30 | 22.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L101 | 2018-05-21 13:19 | 0.8 | 0.8 | 20.3 | 78.1 | 0 | 0 | 1010 | -0.06 | 0 | 0 | 0 | 17.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2018-05-21 13:17 | 50.6 | 38.7 | 0.1 | 10.6 | -26.4 | 26.4 | 1010 | 2.77 | 51.3 | 272 | 40 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-05-21 13:15 | 59 | 42.1 | 0 | 0 | 0 | 0 | 1010 | 4.68 | 4.8 | 30 | 10 | 18.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-05-21 13:13 | 31.7 | 24.5 | 7.3 | 36.5 | -0.3 | 0.3 | 1010 | 23.99 | 10.9 | 36 | 10 | 18.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2018-05-21 13:11 | 53.5 | 40.4 | 0 | 6.1 | -0.3 | 0.3 | 1010 | 1.54 | 10.8 | 60 | 20 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-05-21 13:10 | 59.1 | 43.8 | 0.1 | 0 | -38.6 | 38.6 | 1010 | 0.35 | 1.2 | 8 | 5 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-05-21 13:08 | 56.4 | 41.9 | 0 | 1.7 | -0.3 | 0.3 | 1010 | 3.24 | 15.3 | 90 | 15 | 47 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2018-05-21 13:07 | 55.9 | 39.8 | 0 | 4.3 | -43.4 | 43.4 | 1010 | 14.81 | 113.4 | 664 | 80 | 48.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-05-21 13:05 | 59.4 | 42.5 | 0 | 0 | -0.1 | 0.1 | 1010 | 3.92 | 8.5 | 53 | 18 | 37.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-05-21 13:03 | 50.8 | 38.5 | 0.1 | 10.6 | -0.6 | 0.6 | 1010 | 0.81 | 16.7 | 89 | 20 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2018-05-21 13:01 | 43.1 | 35.8 | 1.8 | 19.3 | 0 | 0 | 1010 | 6.61 | 1.2 | 5 | 5 | 16.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2018-05-21 11:23 | 14.5 | 10.2 | 14.6 | 60.7 | -0.1 | 0.1 | 1012 | -0.18 | 0 | 0 | 5 | 14 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2018-05-21 11:22 | 55.1 | 38.9 | 1.3 | 4.7 | -1.4 | 1.4 | 1012 | -0.12 | 0 | 0 | 5 | 16.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2018-05-21 11:21 | 5 | 4 | 19.3 | 71.7 | 0 | 0 | 1012 | -0.18 | 0 | 0 | 0 | 14.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2018-05-21 11:20 | 59.5 | 42.8 | 0 | 0 | -8.6 | 8.6 | 1012 | 0.43 | 5.9 | 36 | 20 | 15.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2018-05-21 11:18 | 48.6 | 38.6 | 0.7 | 12.1 | -0.5 | 0.5 | 1012 | 2.49 | 6.9 | 35 | 20 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-05-21 11:17 | 45.1 | 31.2 | 3.9 | 19.8 | -1.5 | 1.5 | 1012 | 0.37 | 11.7 | 55 | 10 | 19.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-05-21 11:15 | 44.2 | 36.3 | 0 | 19.5 | -1.1 | 1.1 | 1012 | 0.07 | 5.1 | 23 | 15 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2018-05-21 11:13 | 48.3 | 38.9 | 0 | 12.8 | -1.8 | 1.8 | 1012 | 1.13 | 20 | 101 | 20 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2018-05-21 11:11 | 49.9 | 38.6 | 0 | 11.5 | -3.8 | 3.8 | 1012 | 0.69 | 15.7 | 82 | 20 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-05-21 11:10 | 52.4 | 38 | 1.1 | 8.5 | -1.1 | 1.1 | 1012 | 1.19 | 20.9 | 114 | 20 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2018-05-21 11:09 | 53.2 | 39.5 | 0 | 7.3 | -2.2 | 2.2 | 1012 | 8.47 | 25.6 | 143 | 25 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-05-21 11:07 | 47.1 | 37.2 | 0.5 | 15.2 | -1.3 | 1.3 | 1012 | 0.55 | 14 | 69 | 20 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2018-05-21 11:06 | 50.3 | 39.1 | 0.4 | 10.2 | -2.5 | 2.5 | 1012 | 9.05 | 12.9 | 68 | 25 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2018-05-21 11:04 | 46.6 | 38.6 | 0 | 14.8 | 0 | 0 | 1012 | 1.11 | 9.2 | 45 | 15 | 22.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2018-05-21 11:02 | 49.5 | 38.5 | 0.3 | 11.7 | -0.2 | 0.2 | 1012 | 0.1 | 2.8 | 14 | 15 | 18.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-05-21 10:48 | 57.6 | 39.8 | 0 | 2.6 | -4.3 | 4.3 | 1012 | 2.51 | 30.3 | 183 | 40 | 26.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2018-05-21 10:47 | 49.9 | 38.5 | 0.1 | 11.5 | -4.8 | 4.8 | 1013 | 2.04 | 26.8 | 140 | 40 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-05-21 10:43 | 44.3 | 35.5 | 0.8 | 19.4 | -3.4 | 3.4 | 1013 | 2.48 | 13.6 | 63 | 15 | 30.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2018-05-21 10:41 | 49.2 | 39.1 | 0.3 | 11.4 | -69.4 | 69.4 | 1013 | 9.25 | 53.7 | 276 | 80 | 45.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2018-05-21 10:39 | 57.7 | 39.9 | 0.2 | 2.2 | 0 | 0 | 1013 | 0 | 0.2 | 1 | 20 | 13.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-05-21 10:36 | 46.2 | 37.5 | 0 | 16.3 | -0.4 | 0.4 | 1013 | 0.9 | 8.2 | 40 | 8 | 26.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-05-21 10:34 | 49.8 | 38.1 | 0.2 | 11.9 | -36.6 | 36.6 | 1013 | 4.84 | 65.6 | 342 | 50 | 38 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-05-21 10:32 | 59.5 | 39.1 | 0 | 1.4 | -1.7 | 1.7 | 1013 | 2.98 | 15.4 | 96 | 28 | 27.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-05-21 10:30 | 52.5 | 37.3 | 0.4 | 9.8 | -20.2 | 20.2 | 1014 | 15.8 | 34.6 | 190 | 40 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-05-21 10:29 | 53.6 | 36.7 | 1.1 | 8.6 | -0.2 | 0.2 | 1015 | 0.4 | 5.6 | 31 | 10 | 20.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2018-04-26 11:18 | 52.3 | 37.7 | 0 | 10 | -5.5 | 5.5 | 1010 | 29.99 | 48.3 | 264 | 50 | 26.3 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2018-04-26 11:16 | 62.7 | 38 | 0 | 0 | -50.9 | 50.9 | 1010 | 16.21 | 35.5 | 233 | 99 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2018-04-26 11:15 | 55.5 | 37.9 | 0 | 6.6 | -10.9 | 10.9 | 1010 | 31.61 | 49.6 | 288 | 99 | 28.8 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-04-26 11:14 | 60.3 | 41 | 0 | 0 | -8.1 | 8.1 | 1010 | >>>> | 0 | 0 | 99 | 34.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-04-26 11:11 | 58.9 | 42 | 0 | 0 | -0.1 | 0.1 | 1010 | 0.35 | 5.1 | 32 | 8 | 29.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-04-26 11:09 | 44.8 | 36.5 | 0.6 | 18.1 | -28.3 | 28.3 | 1010 | 2.89 | 50.4 | 236 | 45 | 40.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-04-26 11:04 | 38.6 | 30.8 | 4.6 | 26 | -1.7 | 1.7 | 1010 | 0.34 | 10.7 | 43 | 50 | 40 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2018-04-26 11:02 | 48.9 | 39.3 | 0 | 11.8 | -6 | 6 | 1010 | 4.78 | 9.4 | 48 | 10 | 24.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-04-26 11:01 | 43.9 | 37.1 | 0 | 19 | -4.3 | 4.3 | 1010 | 1.52 | 23.1 | 106 | 42 | 26.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-04-26 11:00 | 55.5 | 41 | 0 | 3.5 | -74 | 74 | 1010 | 0.25 | 9.2 | 53 | 25 | 25.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-04-26 10:59 | 46.6 | 37.9 | 0 | 15.5 | -4.6 | 4.6 | 1010 | 14.38 | 32.9 | 161 | 27 | 29.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-04-26 10:52 | 45.3 | 37.1 | 0 | 17.6 | -4.5 | 4.5 | 1009 | 9.07 | 25.8 | 122 | 23 | 35.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-04-26 10:51 | 47.6 | 35.8 | 3.1 | 13.5 | -39.4 | 39.4 | 1009 | 0.89 | 27.9 | 139 | 40 | 41.4 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-04-26 10:49 | 48.1 | 38 | 0.1 | 13.8 | -1.4 | 1.4 | 1009 | 1.62 | 11.1 | 56 | 15 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2018-04-26 10:48 | 0.9 | 1.5 | 17.4 | 80.2 | 0 | 0 | 1009 | -0.02 | 0 | 0 | 0 | 25.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2018-04-26 10:47 | 52.8 | 39.4 | 0 | 7.8 | -65.1 | 65.1 | 1010 | 0.73 | 25.4 | 140 | 99 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-04-26 10:46 | 32.5 | 33.3 | 0 | 34.2 | -0.3 | 0.3 | 1009 | 6.85 | 21.7 | 74 | 25 | 47.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2018-04-26 10:43 | 0.9 | 1.1 | 19.6 | 78.4 | -15.4 | 15.4 | 1009 | 0.12 | 2.8 | 0 | 0 | 37.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2018-04-26 10:42 | 60.3 | 41.8 | 0 | 0 | -65.1 | 65.1 | 1009 | 2.36 | 45.2 | 286 | 99 | 43.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2018-04-26 10:40 | 7.8 | 5.1 | 18.5 | 68.6 | -65.9 | 65.9 | 1009 | 0.02 | 1.2 | 1 | 99 | 21 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2018-04-26 10:39 | 3.8 | 2.9 | 19.6 | 73.7 | -65 | 65 | 1009 | 0.26 | 9.3 | 3 | 99 | 20.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2018-04-26 10:38 | 6.5 | 3.9 | 19 | 70.6 | -0.4 | 0.4 | 1009 | 0.01 | 0.6 | 0 | 0 | 21.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2018-04-26 10:37 | 43.1 | 36.2 | 0.6 | 20.1 | -1.1 | 1.1 | 1009 | 17.14 | 8.9 | 40 | 17 | 32.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-04-26 10:35 | 55.2 | 41.1 | 0 | 3.7 | -8.9 | 8.9 | 1009 | 2.27 | 28.4 | 164 | 30 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2018-04-26 10:34 | 58.5 | 43.5 | 0 | 0 | -65.2 | 65.2 | 1009 | 0.05 | 4.1 | 25 | 99 | 40 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2018-04-26 10:33 | 20.4 | 14.4 | 16.1 | 49.1 | -66.3 | 66.3 | 1009 | 0.02 | 1.3 | 2 | 99 | 18.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2018-04-26 10:32 | 43.9 | 34.7 | 4.5 | 16.9 | -66 | 66 | 1009 | -0.03 | 0 | 0 | 20 | 17.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-04-26 09:29 | 62.2 | 45.3 | 0 | 0 | -80.7 | 80.7 | 1010 | 3.74 | 35.2 | 230 | 99 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-04-26 09:27 | 60.7 | 47.8 | 0 | 0 | -68.9 | 68.9 | 1010 | 12.74 | 64.9 | 412 | 90 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-04-26 09:26 | 60 | 48.5 | 0 | 0 | -71 | 71 | 1010 | 20.83 | 83.6 | 526 | 99 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2018-04-26 09:25 | 47.1 | 48.9 | 0 | 4 | -4.7 | 4.7 | 1010 | 5.2 | 42.1 | 208 | 40 | 18.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2018-04-26 09:24 | 51.5 | 53.3 | 0 | 0 | -67.2 | 67.2 | 1009 | 0.3 | 9.8 | 53 | 40 | 18.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2018-04-26 09:19 | 51.1 | 39.2 | 0.8 | 8.9 | -42.2 | 42.2 | 1009 | 19.27 | 78.2 | 419 | 99 | 51.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2018-04-26 09:18 | 59.6 | 42.7 | 0 | 0 | -50 | 50 | 1009 | 8.01 | 51.3 | 320 | 99 | 43.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2018-04-26 09:16 | 57.5 | 41.9 | 0.2 | 0.4 | -48.6 | 48.6 | 1009 | 11.25 | 99 | 596 | 99 | 43.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2018-04-26 09:15 | 31 | 24.9 | 8.6 | 35.5 | -1.8 | 1.8 | 1009 | 0 | 0 | 0 | 0 | 32.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-04-26 09:14 | 37.9 | 29.9 | 6.4 | 25.8 | -26.6 | 26.6 | 1009 | 7.25 | 48.4 | 192 | 30 | 47.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-04-26 09:12 | 60 | 43 | 0.1 | 0 | -58.3 | 58.3 | 1009 | 0.52 | 13 | 82 | 99 | 40.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2018-04-26 09:10 | 0.4 | 0.3 | 19.1 | 80.2 | -56.3 | 56.3 | 1009 | -0.01 | 0 | 0 | 0 | 22.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-04-26 09:09 | 44.7 | 38.1 | 0.4 | 16.8 | -1.6 | 1.6 | 1009 | 1.86 | 11.8 | 55 | 22 | 26.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-04-26 09:07 | 49.3 | 38.9 | 0.9 | 10.9 | -23.5 | 23.5 | 1009 | 4.55 | 38.7 | 200 | 50 | 42.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-04-26 09:05 | 56.1 | 43.6 | 0 | 0.3 | -58.4 | 58.4 | 1009 | 2.67 | 29.2 | 172 | 99 | 41 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2018-04-26 09:04 | 0.2 | 0.2 | 20.7 | 78.9 | -18.5 | 18.5 | 1009 | 0.03 | 3.4 | 0 | 0 | 18.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2018-04-26 09:03 | 4.7 | 3.5 | 18.9 | 72.9 | 0 | 0 | 1009 | 0.02 | 1.2 | 0 | 0 | 18.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2018-04-26 09:02 | 59.1 | 44.4 | 0.2 | 0 | -53.6 | 53.6 | 1009 | 0.02 | 1.1 | 7 | 15 | 21.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2018-04-26 09:00 | 59.5 | 42.2 | 0.1 | 0 | -55 | 55 | 1009 | 2.22 | 44.2 | 275 | 99 | 40.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2018-04-26 08:58 | 52.5 | 39.5 | 0.4 | 7.6 | -5.4 | 5.4 | 1009 | 8.27 | 25.2 | 138 | 25 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-04-26 08:57 | 47.7 | 38 | 0.4 | 13.9 | -3.3 | 3.3 | 1009 | 4.78 | 18.9 | 94 | 22 | 31 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-04-26 08:55 | 49 | 39.1 | 0.3 | 11.6 | -6.1 | 6.1 | 1009 | 1.48 | 22.8 | 117 | 25 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-04-26 08:53 | 55.5 | 42.2 | 0 | 2.3 | -2.6 | 2.6 | 1009 | 1.37 | 21.9 | 127 | 40 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-04-25 11:41 | 46.1 | 34.9 | 2.1 | 16.9 | 0.2 | -0.2 | 1006 | 0.01 | 0 | 0 | 20 | 30 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2018-04-25 11:39 | 56 | 39.2 | 0 | 4.8 | -12.2 | 12.2 | 1006 | 5.82 | 45.2 | 265 | 40 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-04-25 11:38 | 54.9 | 39.4 | 0 | 5.7 | -0.4 | 0.4 | 1006 | 0 | 1 | 6 | 25 | 36.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2018-04-25 11:37 | 50.9 | 37.5 | 0 | 11.6 | -3.1 | 3.1 | 1006 | 1.36 | 21.8 | 116 | 25 | 35.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-04-25 11:36 | 50.9 | 37.3 | 0 | 11.8 | -3.9 | 3.9 | 1006 | 0.33 | 10.8 | 58 | 15 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-04-25 11:35 | 60.3 | 40.6 | 0 | 0 | 0 | 0 | 1006 | 1.09 | 9.4 | 59 | 17 | 22.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-04-25 11:32 | 56.6 | 39.9 | 0 | 3.5 | 0 | 0 | 1006 | 11.9 | 7.6 | 45 | 15 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-04-25 11:31 | 59.9 | 40.8 | 0 | 0 | 0.1 | -0.1 | 1006 | 0.66 | 3.6 | 22 |  | 23.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-04-25 11:28 | 57.9 | 39.7 | 0 | 2.4 | -0.7 | 0.7 | 1006 | 11.83 | 7.7 | 47 | 25 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2018-04-25 11:25 | 43.4 | 35.2 | 0.8 | 20.6 | -9 | 9 | 1006 | 7.1 | 48.4 | 220 | 40 | 46.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2018-04-25 11:23 | 59 | 41.8 | 0 | 0 | -58.1 | 58.1 | 1006 | 0.04 | 5.9 | 36 | 90 | 28.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2018-04-25 11:22 | 54.9 | 39.4 | 0.1 | 5.6 | -0.1 | 0.1 | 1006 | 0.1 | 0.6 | 4 | 15 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-04-25 11:20 | 48.9 | 38.1 | 0 | 13 | -1.4 | 1.4 | 1006 | 1.15 | 20.1 | 103 | 25 | 30.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-04-25 11:18 | 50.5 | 38.5 | 0 | 11 | -3.6 | 3.6 | 1006 | 1.27 | 21.2 | 112 | 25 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-04-25 11:17 | 31.8 | 30.8 | 0.5 | 36.9 | -0.3 | 0.3 | 1006 | 0.21 | 8.6 | 28 | 5 | 25.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2018-04-25 11:14 | 28.6 | 29.5 | 0.4 | 41.5 | -1.3 | 1.3 | 1006 | 0.08 | 5.2 | 15 | 2 | 26.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2018-04-25 11:12 | 47.5 | 36.7 | 0.5 | 15.3 | -0.7 | 0.7 | 1006 | 0.8 | 16.5 | 82 | 25 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2018-04-25 11:11 | 49 | 38.6 | 0.1 | 12.3 | -26.7 | 26.7 | 1006 | 21.44 | 84.4 | 433 | 80 | 40 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2018-04-25 11:09 | 40 | 35.1 | 0.5 | 24.4 | -1.1 | 1.1 | 1006 | 0.22 | 8.7 | 36 | 12 | 31.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-04-25 11:07 | 34.2 | 32.4 | 0.5 | 32.9 | -0.8 | 0.8 | 1006 | 1.8 | 11.6 | 41 | 12 | 26.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-04-25 10:45 | 47 | 39 | 0 | 14 | -0.4 | 0.4 | 1006 | 2.32 | 13.1 | 64 | 25 | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2018-04-25 10:44 | 44.1 | 36.9 | 0 | 19 | -3.5 | 3.5 | 1006 | 2.38 | 13.5 | 62 | 25 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-04-25 10:43 | 58.4 | 42.5 | 0 | 0 | 0.1 | -0.1 | 1006 | 2.02 | 12.6 | 77 | 27 | 23.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-04-25 10:40 | 31.7 | 31.4 | 1.6 | 35.3 | -0.1 | 0.1 | 1006 | 1.95 | 11.9 | 39 | 20 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-04-25 10:39 | 46.2 | 34.2 | 3.6 | 16 | -18.1 | 18.1 | 1006 | 0.9 | 8.2 | 40 | 12 | 23.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-04-25 10:37 | 44.4 | 36.3 | 0.3 | 19 | -1.8 | 1.8 | 1006 | 1.16 | 32.9 | 153 | 20 | 30.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2018-04-25 10:35 | 43.6 | 36.1 | 1.2 | 19.1 | -2.8 | 2.8 | 1006 | 5.27 | 9.8 | 45 | 17 | 28.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2018-04-25 10:32 | 48.8 | 37.5 | 0.4 | 13.3 | -4.7 | 4.7 | 1006 | 9.24 | 26.3 | 134 | 30 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-04-25 10:08 | 40.1 | 33.8 | 0 | 26.1 | -0.4 | 0.4 | 1008 | 5.58 | 10.3 | 43 | 10 | 21.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-04-25 10:05 | 54.3 | 36.8 | 0 | 8.9 | -2.8 | 2.8 | 1008 | 5.85 | 21.7 | 124 | 25 | 19.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2018-04-25 10:02 | 3.1 | 2.3 | 19.8 | 74.8 | -0.5 | 0.5 | 1008 | 0.18 | 3.7 | 1 | 2 | 16.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2018-04-25 09:58 | 41.5 | 34.4 | 0 | 24.1 | -7.2 | 7.2 | 1008 | 6.64 | 11 | 47 | 17 | 32.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2018-04-25 09:56 | 40.8 | 34.3 | 0 | 24.9 | -2.9 | 2.9 | 1009 | 3.46 | 16.4 | 70 | 22 | 19.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2018-04-25 09:53 | 48.4 | 37 | 0.1 | 14.5 | -4.8 | 4.8 | 1008 | 1.58 | 23.4 | 118 | 25 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-04-25 09:50 | 59.3 | 40.7 | 0 | 0 | -60.1 | 60.1 | 1008 | 0.42 | 12.2 | 75 | 99 | 21.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-04-25 09:49 | 56.1 | 37.6 | 0.5 | 5.8 | -1.6 | 1.6 | 1008 | 0.63 | 7.1 | 42 | 15 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2018-04-25 09:47 | 33.1 | 30.9 | 0.8 | 35.2 | -0.5 | 0.5 | 1008 | 8.69 | 6.4 | 22 | 10 | 24 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-04-25 09:46 | 24.9 | 24.2 | 4.8 | 46.1 | -32.6 | 32.6 | 1008 | 5.02 | 40.9 | 106 | 30 | 28.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-04-25 09:43 | 24.3 | 27.2 | 1.8 | 46.7 | -36.6 | 36.6 | 1008 | 0.05 | 1.9 | 4 | 5 | 21.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-04-25 09:41 | 49.9 | 37.1 | 1.4 | 11.6 | -1.7 | 1.7 | 1008 | 0.26 | 15.7 | 82 | 20 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-04-25 09:40 | 52.3 | 39 | 0.5 | 8.2 | -0.8 | 0.8 | 1008 | 5.63 | 20.7 | 113 | 25 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2018-04-25 09:38 | 59.3 | 41.9 | 0 | 0 | -47.4 | 47.4 | 1008 | 9.66 | 56.8 | 353 | 99 | 39.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-04-25 09:37 | 47.3 | 36.9 | 0 | 15.8 | -17 | 17 | 1008 | 0.83 | 16.9 | 83 | 40 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-04-25 09:35 | 31.3 | 28.9 | 3 | 36.8 | -22.2 | 22.2 | 1008 | 0.08 | 2.4 | 8 | 5 | 22.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-04-25 09:33 | 45.5 | 36.5 | 0.8 | 17.2 | -0.3 | 0.3 | 1008 | 0.36 | 5.2 | 24 | 15 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-04-25 09:31 | 51.6 | 38.8 | 0 | 9.6 | -5.2 | 5.2 | 1008 | 4.92 | 42.1 | 227 | 40 | 25.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-04-25 09:30 | 51.4 | 37 | 0 | 11.6 | -4.7 | 4.7 | 1008 | 0.38 | 2.7 | 14 | 10 | 18.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-04-25 09:29 | 20.4 | 25.4 | 1.1 | 53.1 | -0.1 | 0.1 | 1008 | 1.74 | 0.6 | 1 | 5 | 17.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-04-25 09:27 | 55.1 | 38.9 | 0 | 6 | -24 | 24 | 1008 | 0.15 | 3.4 | 19 | 10 | 22.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-04-25 09:26 | 41.1 | 33.6 | 0 | 25.3 | -19.7 | 19.7 | 1009 | 6.05 | 45.8 | 197 | 40 | 27.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-04-25 09:24 | 46 | 30.1 | 1.9 | 22 | -1.3 | 1.3 | 1009 | 0.79 | 3.9 | 19 | 5 | 22.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2018-04-25 09:22 | 51.5 | 35.2 | 0 | 13.3 | -3.8 | 3.8 | 1009 | >>>> | 0 | 0 | 99 | 23 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-04-25 09:20 | 44.6 | 35.1 | 0 | 20.3 | -48.4 | 48.4 | 1009 | 0.07 | 4.9 | 23 | 40 | 23.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2018-04-24 15:27 | 60.8 | 42.6 | 0 | 0 | -27.8 | 27.8 | 1007 | 11.67 | 104 | 662 | 99 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2018-04-24 15:26 | 60.5 | 42.3 | 0 | 0 | -37.6 | 37.6 | 1007 | 0.26 | 4.4 | 28 | 99 | 24.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2018-04-24 15:25 | 58.3 | 42.3 | 0 | 0 | -24.5 | 24.5 | 1007 | 19.2 | 134.3 | 820 | 99 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2018-04-24 15:24 | 59 | 43.1 | 0 | 0 | -28.2 | 28.2 | 1008 | 17.53 | 127.4 | 787 | 99 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2018-04-24 15:21 | 49.1 | 36.3 | 0.6 | 14 | -4.4 | 4.4 | 1008 | 4.54 | 18.8 | 97 | 22 | 23.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2018-04-24 15:19 | 50.6 | 37.1 | 0 | 12.3 | -0.3 | 0.3 | 1007 | 1.68 | 11.5 | 61 | 15 | 21 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2018-04-24 15:17 | 48.2 | 35.9 | 0.4 | 15.5 | -1.1 | 1.1 | 1007 | 3.41 | 16.4 | 82 | 22 | 21.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2018-04-24 15:14 | 50.1 | 37 | 0 | 12.9 | -1.6 | 1.6 | 1007 | 4.1 | 17.8 | 93 | 25 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2018-04-24 15:12 | 35.1 | 27.9 | 4 | 33 | -0.2 | 0.2 | 1008 | 0.54 | 6.4 | 23 | 25 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2018-04-24 15:10 | 43.5 | 32.8 | 2 | 21.7 | -0.1 | 0.1 | 1008 | 1.13 | 9.3 | 42 | 20 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-04-24 15:07 | 47.3 | 35.6 | 0.3 | 16.8 | -1 | 1 | 1007 | 5.45 | 20.5 | 101 | 22 | 27 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2018-04-24 14:17 | 56.7 | 40.2 | 0.8 | 2.3 | -3 | 3 | 1004 | 0.02 | 1.3 | 8 | 5 | 25.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2018-04-24 14:16 | 58 | 43 | 0 | 0 | -0.8 | 0.8 | 1004 | 0.02 | 4.1 | 25 | 5 | 27.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2018-04-24 14:15 | 52.2 | 39.6 | 0 | 8.2 | -1 | 1 | 1004 | 10.28 | 27.7 | 151 | 30 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-04-24 14:14 | 43.9 | 36.4 | 0 | 19.7 | 0 | 0 | 1004 | 6.36 | 10.8 | 49 | 15 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-04-24 14:13 | 44.5 | 37.9 | 0.5 | 17.1 | -4.7 | 4.7 | 1004 | 17.7 | 9.1 | 42 | 17 | 28.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2018-04-24 14:11 | 48.8 | 40.3 | 0 | 10.9 | -46.5 | 46.5 | 1004 | 7 | 21.6 | 110 | 70 | 51.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2018-04-24 14:10 | 50.3 | 39.7 | 0.5 | 9.5 | -5.6 | 5.6 | 1004 | 0.25 | 9.2 | 48 | 20 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2018-04-24 14:08 | 48.9 | 39.3 | 0 | 11.8 | -20 | 20 | 1004 | 17.08 | 34.6 | 177 | 50 | 47.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-04-24 14:07 | 46.8 | 36.1 | 3.5 | 13.6 | -43.2 | 43.2 | 1003 | 4.89 | 4.7 | 23 | 20 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2018-04-24 14:06 | 0.6 | 0.5 | 20.5 | 78.4 | -1.3 | 1.3 | 1004 | 0.04 | 0.1 | 0 | 0 | 24.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2018-04-24 14:03 | 7.1 | 5.3 | 17.2 | 70.4 | 0 | 0 | 1004 | -0.05 | 0 | 0 | 0 | 24.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2018-04-24 14:02 | 53.7 | 38.7 | 1.4 | 6.2 | -1 | 1 | 1005 | 0.06 | 1.1 | 6 | 2 | 22.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2018-04-24 14:00 | 38.6 | 27.4 | 6.2 | 27.8 | 0 | 0 | 1004 | -0.03 | 0 | 0 | 0 | 22.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2018-04-24 13:58 | 58.1 | 43 | 0 | 0 | -8.1 | 8.1 | 1005 | 0.3 | 4.8 | 29 | 15 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2018-04-24 13:57 | 50 | 39.7 | 0 | 10.3 | -0.6 | 0.6 | 1004 | 2.46 | 6.8 | 35 | 20 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-04-24 13:56 | 44.8 | 31.1 | 3.7 | 20.4 | -1.8 | 1.8 | 1004 | 0.51 | 13.6 | 63 | 22 | 24.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-04-24 13:54 | 48.6 | 37.7 | 0 | 13.7 | -1.2 | 1.2 | 1004 | 0.06 | 4.7 | 24 | 20 | 25.1
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-04-24 13:53 | 48.6 | 37.7 | 0 | 13.7 | -1.2 | 1.2 | 1004 | 0.06 | 4.7 | 24 | 20 | 25.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2018-04-24 13:52 | 48.6 | 39.2 | 0 | 12.2 | -1.5 | 1.5 | 1004 | 0.62 | 14.6 | 74 | 25 | 33.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2018-04-24 13:51 | 51 | 39 | 0 | 10 | -3.3 | 3.3 | 1004 | 0.66 | 15.3 | 82 | 20 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-04-24 13:50 | 54.2 | 39.1 | 0.7 | 6 | -0.9 | 0.9 | 1004 | 1.05 | 19.5 | 111 | 25 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2018-04-24 13:48 | 55 | 40.3 | 0 | 4.7 | -2.1 | 2.1 | 1004 | 8.32 | 25.3 | 146 | 30 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-04-24 13:47 | 49.4 | 38.6 | 0.4 | 11.6 | -1.2 | 1.2 | 1004 | 0.52 | 13.5 | 70 | 20 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2018-04-24 13:45 | 57.8 | 42.7 | 0 | 0 | -0.1 | 0.1 | 1004 | -0.01 | 0 | 0 | 30 | 32.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2018-04-24 13:43 | 51 | 40.9 | 0 | 8.1 | -0.3 | 0.3 | 1004 | 1.27 | 9.8 | 52 | 20 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2018-04-24 13:42 | 58.5 | 42.2 | 0 | 0 | 0 | 0 | 1004 | 0.39 | 5.5 | 33 | 20 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-04-24 13:31 | 57.1 | 40.3 | 0.1 | 2.5 | -3.3 | 3.3 | 1004 | 2.07 | 27.3 | 163 | 25 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2018-04-24 13:30 | 52.2 | 39.7 | 0.1 | 8 | -5.4 | 5.4 | 1004 | 1.53 | 23.2 | 127 | 30 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-04-24 13:26 | 48 | 37.7 | 0.2 | 14.1 | -2.8 | 2.8 | 1004 | 2.36 | 13.2 | 66 | 30 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2018-04-24 13:24 | 49.5 | 39.7 | 0.4 | 10.4 | -65 | 65 | 1004 | 9.98 | 55.7 | 289 | 80 | 46.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2018-04-24 13:22 | 58.9 | 41.3 | 0.1 | 0 | 0 | 0 | 1004 | -0.03 | 0 | 0 | 15 | 24.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-04-24 09:01 | 49.7 | 35.5 | 2.5 | 12.3 | -2 | 2 | 1006 | 3.85 | 17.2 | 89 | 17 | 30.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-04-24 08:59 | 52.4 | 38.9 | 0.3 | 8.4 | -19.4 | 19.4 | 1006 | 14.48 | 32.9 | 181 | 40 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-04-24 08:57 | 48.7 | 37.7 | 0.9 | 12.7 | -0.1 | 0.1 | 1004 | 0.25 | 4.4 | 22 | 5 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-04-24 08:54 | 58.7 | 43.6 | 0 | 0 | -2.8 | 2.8 | 1004 | 0.18 | 13.3 | 81 | 25 | 26.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2018-04-24 08:52 | 44.1 | 37.7 | 0.8 | 17.4 | -2.8 | 2.8 | 1004 | 9.14 | 25.8 | 119 | 27 | 36.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-04-24 08:50 | 42.5 | 38.1 | 0 | 19.4 | -0.3 | 0.3 | 1004 | 4.62 | 4.5 | 20 | 10 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2018-04-24 08:49 | 52.3 | 41.8 | 0 | 5.9 | -62.4 | 62.4 | 1004 | 3.72 | 56.1 | 307 | 99 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2018-04-24 08:48 | 51.1 | 41.1 | 0 | 7.8 | -15.2 | 15.2 | 1004 | 11.87 | 63.3 | 339 | 50 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2018-04-24 08:46 | 55.9 | 43.6 | 0 | 0.5 | -37.5 | 37.5 | 1004 | 17.75 | 36.1 | 211 | 99 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-04-24 08:45 | 36.1 | 35.4 | 0 | 28.5 | 0 | 0 | 1004 | -0.01 | 0 | 0 | 5 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-04-24 08:43 | 36.8 | 29.8 | 6.4 | 27 | -1.1 | 1.1 | 1004 | 2.01 | 26.5 | 102 | 20 | 28.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2018-04-24 08:41 | 47 | 39.9 | 0.2 | 12.9 | -28.8 | 28.8 | 1004 | 1.86 | 41.5 | 204 | 50 | 21.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-04-24 08:39 | 11.7 | 22.2 | 3.6 | 62.5 | -0.6 | 0.6 | 1004 | 4.56 | 4.5 | 5 | 5 | 23.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-04-24 08:37 | 25.5 | 22.7 | 7.8 | 44 | -1.1 | 1.1 | 1004 | 0.16 | 3.4 | 9 | 8 | 23.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2018-04-24 08:35 | 36.8 | 36.9 | 0.3 | 26 | -0.4 | 0.4 | 1004 | 2.53 | 13.3 | 51 | 22 | 38.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L101 | 2018-04-24 08:32 | 0.2 | 0.4 | 20.2 | 79.2 | -0.2 | 0.2 | 1004 | -0.18 | 0 | 0 | 0 | 21.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-04-24 08:31 | 53.1 | 44.8 | 0 | 2.1 | -7.2 | 7.2 | 1004 | 0.89 | 2 | 11 | 5 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-04-24 08:29 | 43 | 40.1 | 0 | 16.9 | -1.2 | 1.2 | 1004 | 4.19 | 17 | 76 | 20 | 49.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2018-04-24 08:28 | 52.2 | 41.4 | 0 | 6.4 | -40.3 | 40.3 | 1004 | 16.16 | 117.1 | 640 | 80 | 49.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-04-24 08:26 | 42.5 | 39.3 | 0 | 18.2 | -1.3 | 1.3 | 1004 | 8.08 | 11.8 | 52 | 20 | 43.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-04-24 08:24 | 37.5 | 35.8 | 0.7 | 26 | -1.4 | 1.4 | 1004 | 0.72 | 15.4 | 60 | 22 | 38.7 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2018-04-24 08:22 | 23.2 | 26.5 | 5.4 | 44.9 | -0.2 | 0.2 | 1004 | 10.79 | 1.5 | 3 | 2 | 21.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2018-04-23 15:44 | 50.2 | 37.6 | 0 | 12.2 | -1.6 | 1.6 | 1007 | 5.12 | 19.5 | 102 | 25 | 40 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2018-04-23 15:42 | 41.9 | 35.5 | 0 | 22.6 | -0.9 | 0.9 | 1006 | 0.93 | 17.6 | 77 | 20 | 41.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2018-04-23 15:40 | 47.6 | 36.7 | 0 | 15.7 | -2 | 2 | 1006 | 3.95 | 8.6 | 43 | 10 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-04-23 15:39 | 45 | 34.6 | 0 | 20.4 | -1.6 | 1.6 | 1006 | 0.59 | 14.4 | 68 | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-04-23 15:38 | 50.5 | 36.8 | 2.5 | 10.2 | -1.7 | 1.7 | 1006 | 0.2 | 3.9 | 20 | 5 | 31.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-04-23 15:37 | 4.7 | 3.4 | 18.3 | 73.6 | -61.7 | 61.7 | 1006 | -0.15 | 0 | 0 | 99 | 29.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-04-23 15:35 | 47.5 | 32.1 | 3.9 | 16.5 | -0.3 | 0.3 | 1006 | 0.11 | 2.8 | 14 | 15 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-04-23 15:34 | 47.4 | 37.1 | 0 | 15.5 | -5.5 | 5.5 | 1006 | 4 | 17.3 | 86 | 25 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-04-23 15:33 | 45.7 | 36.4 | 0.1 | 17.8 | -0.9 | 0.9 | 1006 | 4.46 | 9.1 | 43 | 25 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2018-04-23 15:32 | 0.3 | 0.2 | 20.4 | 79.1 | -0.7 | 0.7 | 1006 | -0.02 | 0 | 0 | 5 | 25.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2018-04-23 15:31 | 41.6 | 32.4 | 0 | 26 | -1.7 | 1.7 | 1006 | 5.28 | 20.1 | 88 | 20 | 26.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-04-23 15:29 | 2.7 | 1.6 | 19.5 | 76.2 | -0.1 | 0.1 | 1007 | -0.03 | 0 | 0 | 0 | 26.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-04-23 15:28 | 56.5 | 39 | 0.6 | 3.9 | -6.8 | 6.8 | 1007 | 3.27 | 15.9 | 94 | 25 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2018-04-23 15:27 | 55.2 | 41 | 0 | 3.8 | -0.5 | 0.5 | 1007 | 1.19 | 9.4 | 54 | 20 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2018-04-23 15:16 | 57.6 | 40.3 | 0 | 2.1 | -69.3 | 69.3 | 1006 | 1.23 | 20.3 | 122 | 99 | 30.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2018-04-23 15:15 | 48.5 | 37.4 | 0 | 14.1 | -34.1 | 34.1 | 1006 | 3.28 | 15.5 | 79 | 50 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-04-23 15:13 | 36.3 | 31.3 | 0 | 32.4 | -11.9 | 11.9 | 1006 | 1.7 | 11.2 | 42 | 10 | 29.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2018-04-23 15:13 | 0.5 | 0.3 | 20 | 79.2 | -3.2 | 3.2 | 1006 | -0.07 | 0 | 0 | 0 | 27.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2018-04-23 15:11 | 50.7 | 39 | 0 | 10.3 | -22.3 | 22.3 | 1006 | 4.84 | 18.7 | 99 | 30 | 40 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-04-23 15:09 | 51.3 | 39.1 | 0 | 9.6 | -21.6 | 21.6 | 1006 | 7.49 | 23.7 | 127 | 40 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-04-23 15:08 | 39.6 | 29.1 | 5.8 | 25.5 | -2.2 | 2.2 | 1006 | 0.08 | 2.4 | 10 | 5 | 30.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-04-23 15:07 | 52.4 | 38 | 0.4 | 9.2 | -34.7 | 34.7 | 1006 | 14.8 | 116 | 637 | 80 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-04-23 15:05 | 39.8 | 34.6 | 0 | 25.6 | -1 | 1 | 1006 | 4.28 | 17.7 | 74 | 25 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-04-23 15:04 | 48.4 | 37.5 | 0.1 | 14 | -11.2 | 11.2 | 1006 | 1.26 | 20.9 | 106 | 20 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-04-23 15:03 | 45.8 | 35.3 | 0.2 | 18.7 | -23.7 | 23.7 | 1006 | 1.22 | 20.2 | 97 | 25 | 39.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2018-04-23 15:01 | 49.3 | 36.2 | 0 | 14.5 | -5.9 | 5.9 | 1006 | 5.11 | 42.4 | 219 | 40 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-04-23 15:00 | 31.3 | 26.4 | 3.6 | 38.7 | -0.3 | 0.3 | 1006 | 10.88 | 7.2 | 23 | 10 | 28.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2018-04-23 14:58 | 42.2 | 34.9 | 0.2 | 22.7 | -58.8 | 58.8 | 1006 | 0.69 | 24.4 | 108 | 99 | 34.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-04-23 14:07 | 60.1 | 41 | 0 | 0 | 0.2 | -0.2 | 1007 | 1.55 | 5.4 | 34 | 30 | 31.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-04-23 14:05 | 49.7 | 35.4 | 1.3 | 13.6 | -2.8 | 2.8 | 1007 | 5.79 | 45.1 | 235 | 40 | 36.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-04-23 14:04 | 54.9 | 38.7 | 0 | 6.4 | -36.9 | 36.9 | 1007 | 11.88 | 29.6 | 170 | 50 | 34.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2018-04-23 14:03 | 60.5 | 40.3 | 0 | 0 | -56.3 | 56.3 | 1007 | 0.07 | 4.7 | 30 | 99 | 39.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-04-23 14:01 | 48 | 37 | 0.6 | 14.4 | -23.1 | 23.1 | 1007 | 7.64 | 50.7 | 255 | 50 | 39.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-04-23 14:00 | 0.8 | 1.9 | 18.7 | 78.6 | 0 | 0 | 1007 | 0.03 | 0.3 | 0 | 2 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2018-04-23 13:59 | 48.2 | 37.3 | 0 | 14.5 | -1.1 | 1.1 | 1007 | 1.47 | 5.2 | 26 | 20 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2018-04-23 13:58 | 55.4 | 38.3 | 0 | 6.3 | -46.6 | 46.6 | 1007 | 8.58 | 89.2 | 517 | 99 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2018-04-23 13:57 | 42.8 | 32.5 | 0.6 | 24.1 | -1.4 | 1.4 | 1007 | 19.17 | 2.1 | 9 | 5 | 25.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-04-23 13:55 | 47.2 | 35.4 | 0.1 | 17.3 | -2.9 | 2.9 | 1007 | 3.96 | 17.4 | 86 | 20 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-04-23 13:53 | 48.2 | 35 | 1.1 | 15.7 | -4.8 | 4.8 | 1007 | 3.86 | 36.8 | 186 | 40 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2018-04-23 13:52 | 54.3 | 39.7 | 0 | 6 | -0.4 | 0.4 | 1007 | 2.11 | 12.5 | 71 | 25 | 38.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2018-04-23 13:51 | 49.5 | 36.9 | 0 | 13.6 | -36.5 | 36.5 | 1007 | 26.6 | 95 | 492 | 99 | 34.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2018-04-23 13:41 | 4.6 | 7.5 | 10.1 | 77.8 | 0 | 0 | 1007 | -0.06 | 0 | 0 | 0 | 32.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-04-23 13:40 | 53.2 | 40.1 | 0 | 6.7 | -4.7 | 4.7 | 1007 | 3.66 | 16.4 | 91 | 25 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2018-04-23 13:39 | 51.9 | 40.7 | 0 | 7.4 | -38.1 | 38.1 | 1007 | 26.04 | 149.6 | 814 | 99 | 46.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-04-23 13:37 | 36 | 33.1 | 0.9 | 30 | -7 | 7 | 1007 | 6.17 | 21.2 | 80 | 20 | 31.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-04-23 13:35 | 57.4 | 41.4 | 0.4 | 0.8 | -0.6 | 0.6 | 1007 | 0.52 | 13.6 | 82 | 15 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2018-04-23 13:34 | 51.5 | 39.6 | 0.1 | 8.8 | -2 | 2 | 1007 | 1.54 | 22.8 | 123 | 20 | 42 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-04-23 13:32 | 44.7 | 36.4 | 0 | 18.9 | -5 | 5 | 1007 | 4.42 | 38.7 | 181 | 40 | 38.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-04-23 13:31 | 57 | 40.9 | 0.1 | 2 | -0.1 | 0.1 | 1007 | 7.5 | 11.9 | 71 | 25 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2018-04-23 13:29 | 52.5 | 38 | 0 | 9.5 | -7.2 | 7.2 | 1007 | 5.25 | 43.2 | 237 | 40 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2018-04-23 13:28 | 51 | 38.8 | 0 | 10.2 | -51.2 | 51.2 | 1007 | 1.29 | 20.6 | 110 | 50 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-04-23 13:27 | 52.7 | 37.6 | 0.3 | 9.4 | -2.1 | 2.1 | 1007 | 1.12 | 20 | 110 | 25 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-04-23 13:25 | 45.5 | 34.4 | 2.1 | 18 | -0.2 | 0.2 | 1007 | 12.26 | 7.7 | 36 | 12 | 29.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-04-23 13:24 | 58.2 | 42.7 | 0.1 | 0 | -0.2 | 0.2 | 1007 | 5.43 | 5.1 | 31 | 10 | 35.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2018-04-23 11:56 | 58.8 | 42.9 | 0 | 0 | -57.5 | 57.5 | 1008 | 0.62 | 23.3 | 143 | 99 | 38.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2018-04-23 11:55 | 17.8 | 21.9 | 6.2 | 54.1 | -0.1 | 0.1 | 1008 | -0.01 | 0 | 0 | 0 | 33.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2018-04-23 11:54 | 58.7 | 43.1 | 0 | 0 | -54.7 | 54.7 | 1008 | 1.36 | 9.8 | 60 | 99 | 37.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2018-04-23 11:53 | 55.9 | 40.7 | 0.9 | 2.5 | -57.8 | 57.8 | 1008 | 0.17 | 3.5 | 20 | 99 | 26.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2018-04-23 11:52 | 49.7 | 37.9 | 0.1 | 12.3 | -16.7 | 16.7 | 1008 | 11.2 | 62.2 | 324 | 50 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2018-04-23 11:50 | 11.3 | 7.3 | 16.9 | 64.5 | -57.6 | 57.6 | 1008 | 0.04 | 1.6 | 1 | 99 | 27.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2018-04-23 11:49 | 1.8 | 4.4 | 18 | 75.8 | -3.9 | 3.9 | 1008 | 0.01 | 1.8 | 0 | 0 | 35.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2018-04-23 11:48 | 51.7 | 38.7 | 0.4 | 9.2 | -25.1 | 25.1 | 1008 | 6.31 | 45.7 | 247 | 50 | 45.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2018-04-23 11:46 | 52 | 39 | 0 | 9 | -54.7 | 54.7 | 1009 | 3.4 | 54.4 | 296 | 99 | 40.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-04-23 11:45 | 57.3 | 42.5 | 0 | 0.2 | -0.4 | 0.4 | 1008 | 1.44 | 10.2 | 61 | 42 | 47.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2018-04-23 11:36 | 59.4 | 41.5 | 0 | 0 | -37.7 | 37.7 | 1009 | 23.88 | 145.4 | 905 | 99 | 46.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-04-23 11:35 | 54.4 | 38.5 | 0.5 | 6.6 | -6.2 | 6.2 | 1009 | 11.16 | 28.6 | 163 | 40 | 45.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2018-04-23 11:33 | 22.1 | 14.7 | 14 | 49.2 | -0.1 | 0.1 | 1009 | 0.04 | 6.4 | 14 | 0 | 21.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2018-04-23 11:32 | 0.8 | 0.7 | 20.3 | 78.2 | -5.1 | 5.1 | 1009 | 0.05 | 1.8 | 0 | 0 | 22.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2018-04-23 11:31 | 25.2 | 17.4 | 12.4 | 45 | -47.1 | 47.1 | 1009 | 0.04 | 3.5 | 9 | 10 | 21.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2018-04-23 11:30 | 54.3 | 40.8 | 0.2 | 4.7 | -19.1 | 19.1 | 1009 | 0.06 | 2.1 | 12 | 20 | 33.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2018-04-23 11:28 | 55.3 | 40.8 | 0.2 | 3.7 | -0.4 | 0.4 | 1009 | 0.25 | 4.3 | 25 | 10 | 34.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2018-04-23 11:26 | 58.1 | 42.5 | 0 | 0 | -35.9 | 35.9 | 1009 | 26.18 | 151.9 | 924 | 99 | 44.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2018-04-23 11:25 | 22.3 | 30.4 | 4 | 43.3 | -0.5 | 0.5 | 1010 | 0.01 | 1 | 2 | 5 | 28.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2018-04-23 11:21 | 55.6 | 38.3 | 0.2 | 5.9 | -28.9 | 28.9 | 1010 | 2.92 | 31.8 | 185 | 40 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2018-04-23 11:20 | 49.3 | 36.2 | 0 | 14.5 | -11.7 | 11.7 | 1010 | 17.72 | 36.4 | 188 | 40 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-04-23 11:19 | 51.7 | 36.6 | 0 | 11.7 | -8.9 | 8.9 | 1010 | 18.22 | 79.8 | 432 | 50 | 37.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-04-23 11:17 | 51.5 | 38.2 | 0 | 10.3 | -3.5 | 3.5 | 1011 | 20.99 | 39.2 | 211 | 40 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-04-23 11:16 | 56.9 | 40 | 0.6 | 2.5 | -27.7 | 27.7 | 1011 | 8.22 | 52.5 | 313 | 50 | 44.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2018-04-23 11:14 | 30.5 | 33.3 | 0 | 36.2 | -55.3 | 55.3 | 1011 | 0.14 | 6.6 | 21 | 99 | 37.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-04-23 11:13 | 10.8 | 27.4 | 0 | 61.8 | -1.7 | 1.7 | 1011 | 0.1 | 2.5 | 2 | 2 | 35.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2018-04-23 11:12 | 61.6 | 39.5 | 0 | 0 | -48.1 | 48.1 | 1010 | 7.58 | 23.8 | 154 | 99 | 33.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2018-04-23 11:10 | 53.4 | 37.3 | 0 | 9.3 | -19.2 | 19.2 | 1011 | 28.45 | 46.3 | 259 | 50 | 34.6 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2018-04-23 11:08 | 2.4 | 2.2 | 19.9 | 75.5 | -6.3 | 6.3 | 1011 | 0.02 | 0.5 | 0 | 0 | 31.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-04-23 11:07 | 55.4 | 38.9 | 1.4 | 4.3 | -18.4 | 18.4 | 1011 | 21.97 | 40.2 | 233 | 50 | 41.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-04-20 14:06 | 58 | 37.8 | 0.1 | 4.1 | 0.1 | -0.1 | 1012 | 0.01 | 0.4 | 2 | 5 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2018-04-20 14:03 | 0.4 | 0.2 | 20.5 | 78.9 | -60.2 | 60.2 | 1012 | 0.05 | 1.9 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2018-04-20 14:01 | 0.3 | 0.1 | 20.4 | 79.2 | -60.4 | 60.4 | 1012 | 0.05 | 1.8 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2018-04-20 14:00 | 45.9 | 36 | 0 | 18.1 | -4.1 | 4.1 | 1011 | 9.13 | 13.2 | 63 | 15 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2018-04-20 13:57 | 44.6 | 36.2 | 0 | 19.2 | -5.3 | 5.3 | 1011 | 8.99 | 26.4 | 123 | 40 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2018-04-20 13:54 | 34.5 | 33.1 | 0 | 32.4 | 0 | 0 | 1012 | 0 | 0 | 0 | 3 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2018-04-20 13:52 | 54 | 38.4 | 0 | 7.6 | -6.8 | 6.8 | 1012 | 17.4 | 37.2 | 211 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-04-20 13:49 | 57.6 | 39.6 | 0.4 | 2.4 | -63.8 | 63.8 | 1012 | 14.58 | 33.2 | 200 | 40 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2018-04-20 13:47 | 0.2 | 0.1 | 20.6 | 79.1 | -60.8 | 60.8 | 1012 | -0.02 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2018-04-20 13:44 | 0.7 | 0.5 | 20.4 | 78.4 | -60 | 60 | 1012 | 0.06 | 7.3 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-04-20 13:42 | 0.2 | 0.1 | 20.5 | 79.2 | -61.1 | 61.1 | 1012 | -0.08 | 0 | 0 | 3 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-04-20 13:40 | 52.2 | 36.3 | 0.6 | 10.9 | -7.1 | 7.1 | 1013 | 12.19 | 31.2 | 171 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2018-04-20 13:37 | 0.2 | 0.1 | 20.5 | 79.2 | -61.1 | 61.1 | 1013 | -0.01 | 0 | 0 | 5 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-04-20 13:34 | 59.1 | 40.2 | 0.2 | 0.5 | -64.6 | 64.6 | 1013 | 10.38 | 98.9 | 613 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-03-30 13:07 | 55.9 | 40.8 | 0 | 3.3 | 0 | 0 | 1008 | 0.47 | 6.4 | 37.3 | 15 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-03-30 13:03 | 32.7 | 31.1 | 0.4 | 35.8 | -0.54 | 0.5 | 1008 | 0.05 | 4.4 | 14.9 | 10 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-03-30 13:00 | 45.2 | 35.4 | 0.4 | 19 | -2.52 | 2.5 | 1007 | 0.79 | 28.8 | 136.4 | 25 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-03-30 12:57 | 54.3 | 39.9 | 1.2 | 4.6 | -29.39 | 29.4 | 1007 | 5.42 | 4.1 | 30.3 | 20 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-03-30 12:54 | 44.9 | 32.2 | 4.2 | 18.7 | -1.67 | 1.7 | 1007 | 2.04 | 28.5 | 133.9 | 40 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-03-30 12:51 | 42.8 | 32.8 | 1.9 | 22.5 | -1.08 | 1.1 | 1007 | 0.2 | 4.1 | 18.3 | 5 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-03-30 12:49 | 57.4 | 42.9 | 0 | 0 | -5.88 | 5.9 | 1007 | 0.07 | 0.6 | 3.7 | 7 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-03-30 12:46 | 54.4 | 40.5 | 0 | 5.1 | -0.24 | 0.2 | 1007 | 3.53 | 9.1 | 49.1 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L101 | 2018-03-30 12:44 | 0.6 | 0.6 | 20.6 | 78.2 | -0.24 | 0.2 | 1007 | -0.2 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-03-30 12:43 | 52.3 | 39.5 | 0 | 8.2 | -0.22 | 0.2 | 1007 | 1.05 | 2.4 | 13 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-03-30 12:41 | 53.4 | 39 | 1.2 | 6.4 | -1.97 | 2 | 1007 | -0.24 | 0 | 0 | 10 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-03-30 12:39 | 41.3 | 34.4 | 0 | 24.3 | -0.15 | 0.2 | 1007 | -0.04 | 0 | 0 | 10 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-03-30 12:35 | 58.4 | 39.9 | 0 | 1.7 | 0.29 | -0.3 | 1008 | -0.08 | 0 | 0 | 10 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-03-30 12:33 | 44.1 | 34 | 0.9 | 21 | -1.27 | 1.3 | 1008 | 1.17 | 21.5 | 99.3 | 22 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-03-30 12:31 | 35.6 | 31.9 | 0 | 32.5 | -23.83 | 23.8 | 1008 | 0.61 | 15.1 | 56.2 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-03-30 12:27 | 42 | 29.4 | 3.8 | 24.8 | -9.16 | 9.2 | 1008 | 4.7 | 43.1 | 189.5 | 40 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-03-30 12:25 | 57.1 | 39 | 0.2 | 3.7 | -0.14 | 0.1 | 1008 | 0.62 | 15.8 | 94.3 | 28 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-03-30 12:20 | 57.3 | 38.5 | 0.1 | 4.1 | -3.52 | 3.5 | 1008 | 1.88 | 27.6 | 165.6 | 42 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-03-30 12:16 | 42.9 | 30.1 | 3.8 | 23.2 | -3.22 | 3.2 | 1008 | 8.25 | 26.6 | 119.2 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-03-30 12:14 | 45.8 | 30.9 | 3.6 | 19.7 | -0.56 | 0.6 | 1008 | 0.87 | 8.7 | 41.7 | 5 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-03-30 11:18 | 34.9 | 30.7 | 0.1 | 34.3 | -1.28 | 1.3 | 1008 | 13.26 | 16.5 | 60.1 | 10 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-03-30 11:15 | 43.1 | 37.7 | 0 | 19.2 | -5.07 | 5.1 | 1008 | 1.78 | 26.1 | 117.8 | 25 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-03-30 11:13 | 57 | 41.7 | 0 | 1.3 | -63.57 | 63.6 | 1008 | 0.12 | 6.7 | 40.1 | 28 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-03-30 11:10 | 39.7 | 31.8 | 3.8 | 24.7 | -1.6 | 1.6 | 1008 | 0.14 | 7.4 | 30.9 | 50 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-03-30 11:06 | 35.7 | 33.4 | 0.1 | 30.8 | -2.28 | 2.3 | 1009 | 7.59 | 24.9 | 93.1 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-03-30 11:03 | 35.7 | 27.8 | 4.6 | 31.9 | -0.19 | 0.2 | 1008 | -0.13 | 0 | 0 | 10 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-03-30 10:59 | 29.6 | 29 | 0 | 41.4 | -14.28 | 14.3 | 1009 | 3.36 | 16.5 | 51.2 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-03-30 10:55 | 49.9 | 35.8 | 2.8 | 11.5 | -27.28 | 27.3 | 1009 | 4.16 | 18.6 | 0 | 20 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-03-30 10:53 | 56.6 | 39 | 0.7 | 3.7 | -7.39 | 7.4 | 1009 | 3.16 | 16.5 | 97.8 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-03-30 10:51 | 0.6 | 0.5 | 20.8 | 78.1 | -0.87 | 0.9 | 1009 | -0.13 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-03-30 10:48 | 42.3 | 32.3 | 0 | 25.4 | -22.31 | 22.3 | 1009 | 7.99 | 55.7 | 246.7 | 45 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-03-30 10:46 | 44.8 | 32.8 | 1.3 | 21.1 | -4.85 | 4.9 | 1009 | 2.12 | 13.4 | 63 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-03-30 10:44 | 24 | 26.5 | 1.5 | 48 | -41.16 | 41.2 | 1009 | 0.01 | 1 | 2.6 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-03-30 10:42 | 53.4 | 37.9 | 0.5 | 8.2 | -1.06 | 1.1 | 1009 | 6.01 | 22.8 | 127.4 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-03-30 10:40 | 46.1 | 33.7 | 2.3 | 17.9 | -3.44 | 3.4 | 1009 | 0.28 | 17.3 | 83.4 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-03-30 10:04 | 40.5 | 31.5 | 3.3 | 24.7 | -0.24 | 0.2 | 1008 | 1.38 | 5.4 | 22.7 | 5 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-03-30 10:02 | 47.9 | 33.8 | 2.4 | 15.9 | -5.02 | 5 | 1008 | 8.8 | 59.2 | 297 | 40 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-03-30 09:59 | 48.5 | 36.7 | 0.9 | 13.9 | -42.04 | 42 | 1006 | 5.05 | 44 | 223.3 | 60 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-03-30 09:56 | 4.3 | 4.1 | 17.8 | 73.8 | -0.27 | 0.3 | 1008 | -0.15 | 0 | 0 | 1 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-03-30 09:52 | 38.1 | 34.6 | 0.9 | 26.4 | -8.37 | 8.4 | 1008 | 13.82 | 33.6 | 134 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-03-30 09:49 | 48.2 | 40 | 0 | 11.8 | -0.29 | 0.3 | 1007 | 5.35 | 5.3 | 26.8 | 9 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-03-30 09:46 | 54.4 | 41.7 | 0 | 3.9 | -1.03 | 1 | 1007 | 1.35 | 10.7 | 60.9 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-03-30 09:42 | 57 | 41.4 | 0.1 | 1.5 | -47.61 | 47.6 | 1006 | 2.16 | 28.7 | 170.9 | 48 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-03-30 09:39 | 46.7 | 36.6 | 0.4 | 16.3 | -4.81 | 4.8 | 1006 | 8.95 | 27.5 | 134.3 | 22 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-03-30 09:36 | 48.2 | 37.4 | 0.7 | 13.7 | -7.26 | 7.3 | 1006 | 1.97 | 27.7 | 139.7 | 25 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-03-30 09:32 | 46.7 | 37.6 | 0 | 15.7 | -5.24 | 5.2 | 1006 | 11.23 | 30.7 | 149.9 | 40 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-03-30 09:30 | 50 | 37 | 1.9 | 11.1 | -33.81 | 33.8 | 1006 | 2.52 | 51 | 266.9 | 42 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-03-30 09:27 | 35.3 | 34 | 0 | 30.7 | -0.69 | 0.7 | 1006 | 9.38 | 27.7 | 102.2 | 25 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-03-30 09:21 | 56.9 | 41 | 0 | 2.1 | -7.68 | 7.7 | 1007 | 1.92 | 27.6 | 164.5 | 28 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-03-30 09:15 | 57.8 | 47.3 | 0 | 0 | -44.41 | 44.4 | 1008 | 19.72 | 84.8 | 512.8 | 90 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2018-03-28 15:28 | 60.6 | 40.9 | 0 | 0 | -23.59 | 23.6 | 1006 | 12.94 | 116.7 | 740.6 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2018-03-28 15:26 | 60.2 | 41.4 | 0 | 0 | -32.32 | 32.3 | 1006 | 0.09 | 2.7 | 17.1 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2018-03-28 15:23 | 59.1 | 41.5 | 0 | 0 | -20.12 | 20.1 | 1006 | 18.93 | 141.1 | 872.9 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2018-03-28 15:20 | 50.6 | 35.6 | 0.2 | 13.6 | -6.05 | 6.1 | 1006 | 3.31 | 16.9 | 89.3 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2018-03-28 15:18 | 49.6 | 34.8 | 0.2 | 15.4 | -0.51 | 0.5 | 1006 | 0.33 | 5.4 | 27.8 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2018-03-28 15:16 | 49.9 | 34.6 | 0.4 | 15.1 | -1.32 | 1.3 | 1006 | 2 | 13.2 | 68.8 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2018-03-28 15:14 | 51.7 | 36.1 | 0 | 12.2 | -1.73 | 1.7 | 1006 | 6.85 | 24.3 | 131.7 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2018-03-28 15:12 | 38.3 | 28.6 | 2.6 | 30.5 | -0.04 | 0 | 1006 | 0.29 | 5 | 20 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2018-03-28 15:09 | 47.4 | 32.9 | 1.2 | 18.5 | 0.01 | 0 | 1006 | 2.04 | 13.3 | 66 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-03-28 15:07 | 51.4 | 35.7 | 0.2 | 12.7 | -1.06 | 1.1 | 1004 | 5.36 | 21.6 | 116 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2018-03-28 14:57 | 58.5 | 40.3 | 0 | 1.2 | -32.32 | 32.3 | 1003 | 9.49 | 99.4 | 608.2 | 99 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-03-28 14:55 | 52.3 | 36.3 | 0.6 | 10.8 | -19.96 | 20 | 1004 | 2.37 | 14.2 | 77.5 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2018-03-28 14:54 | 5.4 | 4.2 | 18.2 | 72.2 | -0.27 | 0.3 | 1004 | -0.09 | 0 | 0 | 0 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2018-03-28 14:53 | 0.5 | 0.3 | 19.8 | 79.4 | -7.94 | 7.9 | 1004 | 0.3 | 5 | 0.3 | 0 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2018-03-28 14:51 | 4.4 | 2.5 | 18.4 | 74.7 | -38.22 | 38.2 | 1004 | -0.03 | 0 | 0 | 15 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2018-03-28 14:50 | 7.7 | 18.7 | 3 | 70.6 | -27.53 | 27.5 | 1004 | 0.01 | 0.8 | 0.6 | 10 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2018-03-28 14:49 | 51.4 | 38.4 | 0.6 | 9.6 | -0.84 | 0.8 | 1004 | 0.07 | 2.4 | 13.2 | 5 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2018-03-28 14:47 | 57.4 | 41.4 | 0 | 1.2 | -31.97 | 32 | 1004 | >>>> |  | 0 | 99 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2018-03-28 14:45 | 19.9 | 27.7 | 4.3 | 48.1 | -0.79 | 0.8 | 1004 | -0.11 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2018-03-28 14:33 | 55.1 | 37.5 | 0 | 7.4 | -2.9 | 2.9 | 1005 | 5.57 | 47.4 | 273.7 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2018-03-28 14:32 | 50.4 | 35.5 | 0 | 14.1 | -11.23 | 11.2 | 1005 | 15.5 | 36.4 | 192.3 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-03-28 14:30 | 51.2 | 35.7 | 0 | 13.1 | -8.39 | 8.4 | 1005 | 16.72 | 81.7 | 438.2 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-03-28 14:29 | 53.3 | 37.5 | 0 | 9.2 | -3.32 | 3.3 | 1005 | 18.47 | 39.9 | 222.5 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-03-28 14:27 | 59.8 | 39.3 | 0.4 | 0.5 | -25.42 | 25.4 | 1005 | 3.44 | 37.2 | 232.6 | 60 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2018-03-28 14:26 | 57.3 | 37.5 | 0.1 | 5.1 | -49.4 | 49.4 | 1005 | -0.19 | 0 | 0 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-03-28 14:24 | 38.2 | 34.1 | 0 | 27.7 | -1.01 | 1 | 1005 | 0.02 | 1.4 | 5.6 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2018-03-28 14:22 | 61 | 38.3 | 0 | 0.7 | -43.69 | 43.7 | 1005 | 6.71 | 23.9 | 152.7 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2018-03-28 14:20 | 54 | 36.2 | 0.1 | 9.7 | -18.76 | 18.8 | 1005 | >>>> |  | 0 | 60 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2018-03-28 14:18 | 0.5 | 0.2 | 20 | 79.3 | -6.72 | 6.7 | 1005 | -0.04 | 0 | 0 | 0 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-03-28 14:17 | 56.1 | 38.2 | 1.2 | 4.5 | -10.76 | 10.8 | 1004 | 19.91 | 41.4 | 243.4 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-03-28 13:37 | 46 | 33.6 | 1.9 | 18.5 | -0.14 | 0.1 | 1005 | 1.3 | 5.2 | 25.2 | 7 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-03-28 13:35 | 49.2 | 33.6 | 1.9 | 15.3 | -4.91 | 4.9 | 1005 | 8.97 | 60 | 309.1 | 57 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-03-28 13:33 | 36.2 | 24.4 | 5.7 | 33.7 | -50.03 | 50 | 1005 | 0.19 | 3.9 | 14.9 | 50 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2018-03-28 13:31 | 59.4 | 39.3 | 0 | 1.3 | -50.41 | 50.4 | 1005 | 0.07 | 5.1 | 31.5 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-03-28 13:30 | 49.5 | 36.2 | 0.7 | 13.6 | -26.3 | 26.3 | 1005 | 9.52 | 60.9 | 315.4 | 70 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-03-28 13:28 | 21.9 | 17.2 | 8.9 | 52 | -0.07 | 0.1 | 1005 | 0.39 | 1.4 | 3.3 | 2 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2018-03-28 13:26 | 48.8 | 36.3 | 0 | 14.9 | -1.22 | 1.2 | 1005 | 1.45 | 5.5 | 28.2 | 15 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2018-03-28 13:25 | 57.3 | 38 | 0 | 4.7 | -41.07 | 41.1 | 1005 | 11.37 | 108.9 | 652.9 | 99 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2018-03-28 13:23 | 45.9 | 32.6 | 0.8 | 20.7 | -1.33 | 1.3 | 1005 | 17.59 | 2.1 | 10.3 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-03-28 13:20 | 51.2 | 36 | 0.1 | 12.7 | -2.77 | 2.8 | 1005 | 3.59 | 17.6 | 94.3 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-03-28 13:18 | 51.6 | 36 | 0.6 | 11.8 | -4.55 | 4.6 | 1005 | 3.46 | 37.2 | 201.1 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2018-03-28 13:16 | 53 | 38.8 | 0 | 8.2 | -0.46 | 0.5 | 1005 | 2.09 | 13.4 | 74.1 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2018-03-28 13:14 | 50.2 | 36.4 | 0 | 13.4 | -33.02 | 33 | 1005 | 22.93 | 94.1 | 494.8 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2018-03-28 13:00 | 3.9 | 6.2 | 8.9 | 81 | -0.1 | 0.1 | 1004 | -0.1 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-03-28 12:59 | 53.6 | 38.9 | 0 | 7.5 | -4.63 | 4.6 | 1004 | 2.8 | 15.5 | 86.8 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2018-03-28 12:58 | 54.2 | 40.1 | 0 | 5.7 | -34.85 | 34.9 | 1004 | 23.71 | 155.9 | 883.5 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-03-28 12:56 | 41.6 | 35 | 0.6 | 22.8 | -8.7 | 8.7 | 1004 | 23.25 | 43.9 | 191.2 | 45 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-03-28 12:54 | 49.3 | 35.6 | 2.3 | 12.8 | -1.01 | 1 | 1004 | 0.35 | 11.8 | 61.1 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2018-03-28 12:53 | 52.5 | 38.4 | 0.1 | 9 | -2.24 | 2.2 | 1004 | 1.52 | 24.6 | 134.9 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-03-28 12:51 | 47.9 | 36.6 | 0 | 15.5 | -4.76 | 4.8 | 1004 | 4.15 | 40.4 | 202.3 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-03-28 12:49 | 48 | 35.3 | 1.5 | 15.2 | -0.43 | 0.4 | 1004 | 7.08 | 12.2 | 61.3 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2018-03-28 12:48 | 55.3 | 37.9 | 0 | 6.8 | -7.18 | 7.2 | 1004 | 22.92 | 44.5 | 257.9 | 50 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2018-03-28 12:46 | 49.4 | 34.2 | 1.9 | 14.5 | -52.88 | 52.9 | 1004 | -0.02 | 0 | 0 | 25 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-03-28 12:43 | 53.7 | 37.1 | 0.3 | 8.9 | -2.05 | 2.1 | 1004 | 0.89 | 18.9 | 106.5 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-03-28 12:41 | 49.9 | 32.7 | 2.7 | 14.7 | -0.17 | 0.2 | 1004 | 11.03 | 7.8 | 40.7 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-03-28 12:39 | 55.6 | 41 | 0 | 3.4 | 0.07 | -0.1 | 1003 | 4.17 | 4.8 | 27.7 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-03-28 12:35 | 46.8 | 36.9 | 0 | 16.3 | -4.81 | 4.8 | 1003 | 10.34 | 29.5 | 144.6 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-03-28 12:33 | 41.1 | 31 | 4.2 | 23.7 | -41.46 | 41.5 | 1003 | 3.37 | 58.5 | 251.2 | 40 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-03-28 12:31 | 51 | 37.9 | 0.1 | 11 | -1.4 | 1.4 | 1003 | 1.95 | 12.9 | 69 | 15 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2018-03-28 12:29 | 1.3 | 1.8 | 18.3 | 78.6 | 0.14 | -0.1 | 1003 | -0.08 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2018-03-28 12:28 | 54.6 | 38.2 | 0.8 | 6.4 | -56.96 | 57 | 1003 | 0.88 | 29.8 | 170.5 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-03-28 12:26 | 37.9 | 33.9 | 0.1 | 28.1 | -0.51 | 0.5 | 1003 | 8.64 | 26.7 | 106.2 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-03-27 15:46 | 55.5 | 35.8 | 0.1 | 8.6 | 0.23 | -0.2 | 1006 | 0 | 0 | 0 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2018-03-27 15:44 | 0.4 | 0.3 | 20.4 | 78.9 | -54.67 | 54.7 | 1006 | 0.04 | 1.8 | 0.1 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2018-03-27 15:42 | 0.4 | 0.4 | 20.3 | 78.9 | -54.61 | 54.6 | 1006 | -0.01 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2018-03-27 15:40 | 47.6 | 35.8 | 0 | 16.6 | -3.51 | 3.5 | 1006 | 8.49 | 13.3 | 66.4 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2018-03-27 15:38 | 47.8 | 36.6 | 0 | 15.6 | -4.67 | 4.7 | 1006 | 8.24 | 26.4 | 132.1 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-03-27 15:35 | 58.8 | 39.6 | 0.3 | 1.3 | -55.51 | 55.5 | 1006 | 12.95 | 32.7 | 201.6 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2018-03-27 15:33 | 0.4 | 0.3 | 20.2 | 79.1 | -54.48 | 54.5 | 1006 | -0.01 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2018-03-27 15:31 | 45.5 | 36.5 | 0 | 18 | 0.01 | 0 | 1005 | 0.03 | 1.5 | 7.1 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2018-03-27 15:29 | 56.8 | 38.3 | 0.1 | 4.8 | -5.82 | 5.8 | 1006 | 15.83 | 37.1 | 220.4 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2018-03-27 15:27 | 0.9 | 0.6 | 20.2 | 78.3 | -53.8 | 53.8 | 1006 | -0.01 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-03-27 15:25 | 0.3 | 0.2 | 20.3 | 79.2 | -53.77 | 53.8 | 1006 | -0.04 | 0 | 0 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-03-27 15:23 | 53.8 | 36.1 | 0.4 | 9.7 | -6.15 | 6.2 | 1006 | 11.05 | 31 | 174.7 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2018-03-27 15:20 | 1 | 0.7 | 19.9 | 78.4 | -54.23 | 54.2 | 1007 | -0.05 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-03-27 15:18 | 59.9 | 39.7 | 0.1 | 0.3 | -57.99 | 58 | 1005 | 12.65 | 114 | 714.9 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-03-27 15:15 | 39.5 | 32.2 | 0.1 | 28.2 | -1.08 | 1.1 | 1006 | 18.2 | 19.4 | 80.1 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-03-27 15:11 | 49.7 | 34.6 | 0 | 15.7 | -4.25 | 4.3 | 1006 | >>>> |  | 0 | 50 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2018-03-27 14:52 | 45 | 35.1 | 0.6 | 19.3 | -8.19 | 8.2 | 1005 | 7.07 | 52.5 | 247.4 | 38 |  | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2018-03-27 14:49 | 3.7 | 2.9 | 17.9 | 75.5 | -49.53 | 49.5 | 1005 | -0.47 | 0 | 0 | 80 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2018-03-27 14:48 | 52.1 | 37.8 | 0 | 10.1 | -0.13 | 0.1 | 1005 | 2.09 | 3.4 | 18.3 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-03-27 14:46 | 54 | 38.6 | 0 | 7.4 | -0.86 | 0.9 | 1005 | 1.18 | 21.7 | 122.8 | 25 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-03-27 14:44 | 53.9 | 38.4 | 0 | 7.7 | -2.44 | 2.4 | 1005 | 0.92 | 19.2 | 108.4 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-03-27 14:43 | 44.2 | 34.8 | 0 | 21 | -0.17 | 0.2 | 1005 | 0.16 | 7.9 | 36.5 | 15 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2018-03-27 14:41 | 37.2 | 31.6 | 0 | 31.2 | -0.92 | 0.9 | 1005 | 0.01 | 1.9 | 6.2 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2018-03-27 14:40 | 53.1 | 37.6 | 0.1 | 9.2 | -0.42 | 0.4 | 1005 | 0.76 | 17.4 | 96.8 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2018-03-27 14:38 | 50.1 | 37.9 | 0.1 | 11.9 | -23.11 | 23.1 | 1005 | 18.78 | 85.2 | 447.1 | 80 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2018-03-27 14:36 | 47.7 | 36.7 | 0.3 | 15.3 | -0.84 | 0.8 | 1005 | 0.14 | 7.5 | 37.5 | 15 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-03-27 14:34 | 46.1 | 36.2 | 0 | 17.7 | -0.43 | 0.4 | 1005 | 1.6 | 11.6 | 56.1 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-03-27 14:21 | 51.9 | 39.8 | 0 | 8.3 | -0.33 | 0.3 | 1011 | 2.22 | 13.7 | 74.5 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2018-03-27 14:20 | 48 | 36.6 | 0 | 15.4 | -2.46 | 2.5 | 1005 | 2.1 | 13.3 | 66.9 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-03-27 14:18 | 50.3 | 37.1 | 1.5 | 11.1 | -0.31 | 0.3 | 1005 | 2.34 | 14.1 | 74.4 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-03-27 14:17 | 50.4 | 38.3 | 0 | 11.3 | -0.05 | 0.1 | 1005 | 2.17 | 13.6 | 71.7 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-03-27 14:15 | 53.3 | 37 | 1.7 | 8 | -38.72 | 38.7 | 1005 | 0.24 | 4.5 | 25 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-03-27 14:13 | 46.2 | 35.6 | 0.2 | 18 | -3.01 | 3 | 1005 | 1.38 | 38 | 183.8 | 37 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2018-03-27 14:11 | 45.3 | 35.6 | 0.8 | 18.3 | -3.79 | 3.8 | 1005 | 9.58 | 14.1 | 66.7 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2018-03-27 14:09 | 50 | 36.3 | 0.4 | 13.3 | -4.08 | 4.1 | 1005 | 8.27 | 26.6 | 139.1 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2018-03-27 14:06 | 57.1 | 38.4 | 0.8 | 3.7 | -4.31 | 4.3 | 1004 | -0.07 | 0 | 0 | 5 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2018-03-27 14:04 | 0.3 | 0.3 | 19.7 | 79.7 | -19.23 | 19.2 | 1004 | -0.1 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2018-03-27 14:02 | 56.9 | 39.1 | 0 | 4 | -0.79 | 0.8 | 1004 | 9.29 | 28.4 | 169.4 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-03-27 14:01 | 51.8 | 37.7 | 0 | 10.5 | -0.11 | 0.1 | 1004 | 5.61 | 10.9 | 59.1 | 15 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-03-27 13:59 | 48.5 | 37.6 | 0.2 | 13.7 | -3.25 | 3.3 | 1004 | 15.84 | 9.2 | 46.7 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2018-03-27 13:58 | 50.1 | 38.8 | 0 | 11.1 | -41.55 | 41.6 | 1004 | 6.33 | 22.7 | 119 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2018-03-27 13:56 | 51.3 | 38.4 | 0.5 | 9.8 | -5.66 | 5.7 | 1004 | 0.21 | 9 | 48.4 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2018-03-27 13:54 | 49.2 | 37.9 | 0 | 12.9 | -17.61 | 17.6 | 1004 | 15.39 | 35.8 | 184.6 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-03-27 13:53 | 57.6 | 41.1 | 0.4 | 0.9 | -23.23 | 23.2 | 1004 | 3.21 | 4.1 | 24.9 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2018-03-27 13:51 | 1.8 | 1.6 | 18.4 | 78.2 | -0.88 | 0.9 | 1005 | -0.07 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-03-27 13:12 | 54.8 | 39.8 | 1.1 | 4.3 | -1.51 | 1.5 | 1005 | 0.4 | 20.6 | 118 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2018-03-27 13:10 | 53.2 | 39.2 | 0 | 7.6 | -1.41 | 1.4 | 1005 | 8.3 | 26.7 | 148.4 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-03-27 13:08 | 59.4 | 41.8 | 0 | 0 | 0.57 | -0.6 | 1005 | 3.3 | 4.2 | 0 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2018-03-27 13:07 | 55.3 | 40 | 0 | 4.7 | -52.95 | 53 | 1029 | 3.74 | 61.6 | 356.6 | 99 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2018-03-27 13:05 | 54.4 | 38.8 | 0 | 6.8 | -12.15 | 12.2 | 1005 | 10.35 | 64.1 | 365 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2018-03-27 13:04 | 59.2 | 41.3 | 0 | 0 | -28.4 | 28.4 | 1005 | 14.1 | 34.5 | 213.6 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-03-27 13:02 | 54.7 | 40.3 | 0 | 5 | 0.37 | -0.4 | 1005 | 0.13 | 7.1 | 40.7 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-03-27 13:01 | 60.4 | 41.3 | 0 | 0 | -0.5 | 0.5 | 1005 | 1.81 | 27 | 170.8 | 35 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2018-03-27 12:59 | 50.8 | 38.3 | 0.2 | 10.7 | -17.7 | 17.7 | 1005 | 2.07 | 46.2 | 246 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-03-27 12:57 | 57.8 | 41.3 | 0 | 0.9 | 0.17 | -0.2 | 1005 | >>>> |  | 0 | 99 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-03-27 12:53 | 56.9 | 39.9 | 0 | 3.2 | 0.08 | -0.1 | 1005 | -0.26 | 0 | 0 | 8 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2018-03-27 12:50 | 52 | 39.2 | 0 | 8.8 | -0.65 | 0.7 | 1005 | 2.32 | 14 | 76.5 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L101 | 2018-03-27 12:49 | 0.3 | 0.3 | 19.8 | 79.6 | -2.18 | 2.2 | 1005 | -0.1 | 0 | 0 | 0 |  | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-03-27 12:47 | 58.9 | 40.8 | 0.1 | 0.2 | 1.28 | -1.3 | 1005 | -0.08 | 0 | 0 | 5 |  | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-03-27 12:44 | 56 | 40.9 | 0 | 3.1 | -0.32 | 0.3 | 1005 | 3.65 | 17.6 | 103.4 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2018-03-27 12:42 | 56.2 | 38.9 | 0 | 4.9 | -34.3 | 34.3 | 1005 | 12.8 | 115.8 | 680.9 | 80 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-03-27 12:41 | 59.4 | 41.7 | 0 | 0 | 0.24 | -0.2 | 1005 | 3.55 | 8.7 | 54 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-03-27 12:39 | 52.8 | 37.8 | 0.1 | 9.3 | -0.67 | 0.7 | 1005 | 0.61 | 15.6 | 86.3 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2018-03-27 12:37 | 43.8 | 35.6 | 1.8 | 18.8 | 0.12 | -0.1 | 1006 | 9.1 | 1.5 | 7 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2018-03-27 12:31 | 52.6 | 38.7 | 1.8 | 6.9 | -47.67 | 47.7 | 1006 | 0.73 | 27.2 | 149.9 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2018-03-27 12:30 | 41.8 | 31.7 | 3.8 | 22.7 | -0.11 | 0.1 | 1006 | -0.11 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2018-03-27 12:28 | 59 | 42.8 | 0 | 0 | -44.82 | 44.8 | 1006 | 1.25 | 10.1 | 62.4 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2018-03-27 12:26 | 7.5 | 5.2 | 16.7 | 70.6 | -47.93 | 47.9 | 1006 | -0.09 | 0 | 0 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2018-03-27 12:25 | 55.9 | 39.2 | 0 | 4.9 | -15.29 | 15.3 | 1006 | 9.36 | 60.9 | 356.2 | 50 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2018-03-27 12:23 | 60 | 42.3 | 0 | 0 | -47.07 | 47.1 | 1006 | 0.14 | 3.3 | 21 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2018-03-27 12:21 | 11 | 14.6 | 5.5 | 68.9 | -3.86 | 3.9 | 1006 | -0.11 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2018-03-27 12:19 | 54.8 | 38.7 | 0.4 | 6.1 | -21.43 | 21.4 | 1006 | 5.2 | 45.2 | 259.6 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2018-03-27 12:17 | 56 | 38.9 | 0 | 5.1 | -45.99 | 46 | 1006 | 0.66 | 26.1 | 152.9 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-03-27 12:16 | 58.5 | 41.9 | 0 | 0 | 0 | 0 | 1006 | 1.08 | 9.6 | 59.1 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2018-03-27 08:17 | 55.3 | 39.8 | 0.4 | 4.5 | -33.75 | 33.8 | 1007 | 16.75 | 80.5 | 465.6 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2018-03-27 08:14 | 61.1 | 42 | 0 | 0 | -40.67 | 40.7 | 1007 | 7.02 | 52 | 332.2 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2018-03-27 08:13 | 60.2 | 42 | 0 | 0 | -39.83 | 39.8 | 1007 | 9.75 | 100 | 629.8 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2018-03-27 08:11 | 21.4 | 17.5 | 14.3 | 46.8 | -1.41 | 1.4 | 1007 | -0.01 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-03-27 08:10 | 48.8 | 36.2 | 3.1 | 11.9 | -29.11 | 29.1 | 1007 | 6.69 | 50.8 | 259.2 | 50 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-03-27 08:08 | 62.3 | 42.8 | 0 | 0 | -47.88 | 47.9 | 1007 | 0.29 | 10.5 | 68.7 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2018-03-27 08:06 | 28.6 | 21.4 | 14.4 | 35.6 | -47.27 | 47.3 | 1007 | -0.01 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-03-27 08:05 | 53 | 41 | 0.1 | 5.9 | -0.93 | 0.9 | 1007 | 1.72 | 12.1 | 67 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-03-27 08:03 | 59.2 | 42.1 | 0.1 | 0 | -37.55 | 37.6 | 1007 | 0.92 | 18.7 | 115.8 | 50 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-03-27 08:01 | 59.4 | 43.6 | 0 | 0 | -48.4 | 48.4 | 1007 | 1.18 | 21.1 | 131.3 | 99 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2018-03-27 07:59 | 0.2 | 0.3 | 21 | 78.5 | -20.46 | 20.5 | 1007 | 0.01 | 2 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2018-03-27 07:57 | 9.1 | 6.5 | 18.3 | 66.1 | -0.19 | 0.2 | 1007 | 0.01 | 1 | 1 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2018-03-27 07:56 | 31 | 23 | 9.3 | 36.7 | -48.09 | 48.1 | 1007 | -0.03 | 0 | 0 | 15 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2018-03-27 07:54 | 60.7 | 41.8 | 0.1 | 0 | -48.97 | 49 | 1007 | 1.34 | 36.9 | 234.7 | 99 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2018-03-27 07:52 | 56 | 39.4 | 0.5 | 4.1 | -4.54 | 4.5 | 1007 | 7.03 | 24.6 | 144.2 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-03-27 07:50 | 47.3 | 36.7 | 0.7 | 15.3 | -5.21 | 5.2 | 1007 | 11.11 | 30.6 | 151.4 | 35 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-03-27 07:47 | 48.8 | 37.6 | 0.9 | 12.7 | -8.19 | 8.2 | 1007 | 2.28 | 29.8 | 152.4 | 25 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-03-27 07:45 | 58 | 42 | 0 | 0 | -2.08 | 2.1 | 1007 | 1.13 | 21.2 | 128.9 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2018-03-27 07:41 | 0.5 | 0.6 | 20.6 | 78.3 | -12.95 | 13 | 1007 | -0.03 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2018-03-27 07:40 | 61.7 | 41.9 | 0.1 | 0 | -52.85 | 52.9 | 1007 | 1.76 | 42.3 | 273.3 | 99 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2018-03-27 07:38 | 7.1 | 5 | 18.4 | 69.5 | -54.42 | 54.4 | 1007 | 0.05 | 2.1 | 1.5 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2018-03-27 07:37 | 0.2 | 0.3 | 20.7 | 78.8 | -54.25 | 54.3 | 1007 | 0.01 | 1.9 | 0 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2018-03-27 07:35 | 1.7 | 2.4 | 18.9 | 77 | -0.96 | 1 | 1007 | 0.01 | 0.7 | 0.1 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2018-03-27 07:34 | 46 | 36.7 | 0.3 | 17 | -1.2 | 1.2 | 1007 | 14.32 | 8.7 | 42 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-03-27 07:32 | 57.5 | 41 | 0 | 1.5 | -6.71 | 6.7 | 1007 | 1.65 | 25.7 | 154.5 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2018-03-27 07:30 | 59.4 | 42.8 | 0.1 | 0 | -54.04 | 54 | 1007 | -0.01 | 0 | 0 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2018-03-27 07:28 | 8.4 | 6.5 | 17.8 | 67.3 | -53.93 | 53.9 | 1007 | 0.16 | 3.6 | 3.1 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2018-03-27 07:27 | 37.5 | 29.2 | 6.3 | 27 | -57.81 | 57.8 | 1007 | -0.01 | 0 | 0 | 30 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2018-03-26 15:46 | 53.5 | 37.7 | 0 | 8.8 | -4.63 | 4.6 | 1001 | >>>> |  | 0 | 50 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2018-03-26 15:44 | 63.6 | 37.5 | 0 | 0 | -35.97 | 36 | 1002 | 23 | 44.7 | 297.8 | 99 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2018-03-26 15:41 | 57.7 | 37.9 | 0 | 4.4 | -9.79 | 9.8 | 1002 |  |  | 0 | 70 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-03-26 15:39 | 61.2 | 40.8 | 0 | 0 | -6.8 | 6.8 | 1002 |  |  | 0 | 99 |  | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-03-26 15:36 | 58.4 | 41.4 | 0 | 0.2 | -0.03 | 0 | 1002 | 0.36 | 5.6 | 34.2 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-03-26 15:35 | 50.1 | 37.5 | 0.2 | 12.2 | -15.05 | 15.1 | 1001 | 1.33 | 36.8 | 193.1 | 50 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-03-26 15:31 | 61.1 | 44.7 | 0 | 0 | -65.03 | 65 | 1001 | 3.05 | 33.4 | 213.3 | 99 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-03-26 15:30 | 59.4 | 47.1 | 0 | 0 | -32.16 | 32.2 | 1001 | 12.47 | 67.9 | 422 | 80 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-03-26 15:28 | 58.3 | 48.1 | 0 | 0 | -53.26 | 53.3 | 1001 | 19.39 | 83.3 | 508.1 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2018-03-26 15:26 | 47.7 | 48.9 | 0 | 3.4 | -3.81 | 3.8 | 1001 | 4.33 | 39.9 | 199 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2018-03-26 15:25 | 54.9 | 46.3 | 0.1 | 0 | -70.28 | 70.3 | 1001 | 0.05 | 4.3 | 24.6 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2018-03-26 15:16 | 47.8 | 37.5 | 1.5 | 13.2 | -4.73 | 4.7 | 1001 | 4.72 | 9.9 | 49.5 | 15 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-03-26 15:14 | 45.9 | 38.6 | 0 | 15.5 | -4.15 | 4.2 | 1001 | 1.72 | 25.7 | 123.6 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-03-26 15:12 | 57.8 | 42.2 | 0 | 0 | -57.41 | 57.4 | 1001 | 0.21 | 8.9 | 53.8 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-03-26 15:11 | 51.2 | 39.8 | 0 | 9 | -3.63 | 3.6 | 1001 | 12.01 | 31.8 | 170.7 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-03-26 15:08 | 45.6 | 35.3 | 2.3 | 16.8 | -1.02 | 1 | 1001 | 0.06 | 4.9 | 23.6 | 40 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2018-03-26 14:59 | 59 | 40.1 | 0 | 0.9 | -64.1 | 64.1 | 1001 | 0.04 | 4 | 24.6 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2018-03-26 14:57 | 48.5 | 37 | 0 | 14.5 | -30.69 | 30.7 | 1001 | 3.63 | 17.3 | 87.9 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2018-03-26 14:55 | 0.2 | 0.2 | 20.6 | 79 | 0.12 | -0.1 | 1001 | -0.05 | 0 | 0 | 0 |  | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-03-26 14:53 | 28.3 | 28.7 | 0 | 43 | -17.57 | 17.6 | 1001 | 6.53 | 22.9 | 68 | 20 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2018-03-26 14:51 | 51.2 | 38.9 | 0 | 9.9 | -12.47 | 12.5 | 1001 | 7.52 | 24.8 | 132.7 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-03-26 14:49 | 53 | 39.6 | 0 | 7.4 | -20.45 | 20.5 | 1001 | 5.93 | 22.3 | 123.5 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-03-26 14:45 | 47.6 | 36.4 | 1.1 | 14.9 | -2.75 | 2.8 | 1001 | 0.16 | 3.7 | 18.4 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-03-26 14:43 | 52.2 | 37.6 | 0.4 | 9.8 | -33.9 | 33.9 | 1001 | 13.81 | 119.6 | 653.4 | 90 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-03-26 14:41 | 36.8 | 34.1 | 0 | 29.1 | -2.27 | 2.3 | 1001 | 10.16 | 28.9 | 111.2 | 25 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-03-26 14:39 | 48.1 | 37.1 | 0.2 | 14.6 | -3.13 | 3.1 | 1001 | 1.47 | 24 | 120.8 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-03-26 14:37 | 46.5 | 35.4 | 0.2 | 17.9 | -22.08 | 22.1 | 1001 | 1.83 | 26.6 | 129.4 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2018-03-26 14:35 | 50.9 | 36.7 | 0 | 12.4 | -5.64 | 5.6 | 1002 | 4.65 | 43 | 229.1 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-03-26 14:34 | 43.9 | 32.2 | 2.8 | 21.1 | -0.17 | 0.2 | 1001 | 0.04 | 3.8 | 17.4 | 15 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2018-03-26 14:32 | 45.7 | 36.8 | 0 | 17.5 | -51.11 | 51.1 | 1003 | 0.06 | 7.6 | 36.5 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2018-03-26 14:27 | 46.1 | 36.9 | 0 | 17 | -0.79 | 0.8 | 1002 | 0.88 | 18.5 | 89.3 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2018-03-26 14:20 | 52.3 | 38 | 0 | 9.7 | -1.34 | 1.3 | 1002 | 2.98 | 7.9 | 43.4 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-03-26 14:18 | 51 | 37.1 | 0 | 11.9 | -1.13 | 1.1 | 1002 | 0.42 | 13 | 69.3 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-03-26 14:16 | 58.4 | 42 | 0 | 0 | 7.14 | -7.1 | 1002 | 0 | 0 | 0 | 25 |  | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-03-26 14:14 | 15.1 | 10.7 | 14.7 | 59.5 | -52.44 | 52.4 | 1002 | 0.04 | 6.6 | 10.5 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-03-26 14:12 | 44.9 | 30.5 | 4.5 | 20.1 | -0.27 | 0.3 | 1000 | 0.07 | 2.4 | 11.2 | 20 |  | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-03-26 14:10 | 51.5 | 38.2 | 0 | 10.3 | -4.63 | 4.6 | 1002 | 3.32 | 16.8 | 90.7 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-03-26 14:09 | 48.1 | 37.3 | 0.2 | 14.4 | -0.79 | 0.8 | 1002 | 3.95 | 9.1 | 45.7 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2018-03-26 13:34 | 0.2 | 0.2 | 21.4 | 78.2 | -3.54 | 3.5 | 1002 | 0.04 | 1.8 | 0 | 2 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2018-03-26 13:32 | 46.6 | 36.6 | 0 | 16.8 | -1.42 | 1.4 | 1002 | 4.47 | 19.4 | 94.7 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-03-26 13:31 | 1.1 | 0.8 | 21 | 77.1 | -38.78 | 38.8 | 1002 | 0.06 | 1.1 | 0.1 | 0 |  | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-03-26 13:28 | 57.1 | 39.2 | 0.7 | 3 | -6.07 | 6.1 | 1002 | 2.95 | 16 | 95.6 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2018-03-26 13:26 | 56 | 41.3 | 0 | 2.7 | -1.78 | 1.8 | 1002 | 0.76 | 8 | 47.1 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2018-03-26 13:23 | 52.9 | 38.4 | 0 | 8.7 | -1.49 | 1.5 | 1003 | 4.26 | 19.1 | 106 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2018-03-26 13:21 | 23.2 | 15.9 | 12.8 | 48.1 | -1.07 | 1.1 | 1002 | 0.7 | 7.7 | 18.6 | 10 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2018-03-26 13:18 | 45 | 34.1 | 0 | 20.9 | -6.6 | 6.6 | 1003 | 5.38 | 10.6 | 49.8 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2018-03-26 13:15 | 43.6 | 34 | 0 | 22.4 | -2.94 | 2.9 | 1003 | 3 | 15.9 | 72.6 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2018-03-26 13:13 | 51.2 | 36.3 | 0.1 | 12.4 | -4.14 | 4.1 | 1003 | 1.55 | 24.9 | 133.3 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-03-26 13:11 | 61.1 | 39.7 | 0 | 0 | -39.09 | 39.1 | 1002 | 0.04 | 3.9 | 25 | 99 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-03-26 13:09 | 47.4 | 33.5 | 1.4 | 17.7 | -3.56 | 3.6 | 1003 | 1.71 | 12.1 | 60.1 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2018-03-26 13:07 | 43 | 34.3 | 0 | 22.7 | -0.3 | 0.3 | 1003 | 7.21 | 6.2 | 27.9 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-03-26 13:05 | 34.3 | 29.8 | 1.8 | 34.1 | -37.52 | 37.5 | 1003 | 11 | 64 | 229.7 | 70 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-03-26 13:03 | 28.4 | 28.2 | 1.3 | 42.1 | -43.16 | 43.2 | 1002 | 0.27 | 4.6 | 13.8 | 22 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-03-26 13:00 | 47.3 | 34.6 | 2 | 16.1 | -3.29 | 3.3 | 1003 | 0.67 | 26.7 | 132 | 22 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-03-26 12:57 | 57 | 39.8 | 0 | 3.2 | -0.35 | 0.4 | 1003 | 5.34 | 21.5 | 128.5 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2018-03-26 12:41 | 59.9 | 40.7 | 0 | 0 | -46.78 | 46.8 | 1003 | 2.87 | 33.3 | 208.6 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-03-26 12:39 | 50.9 | 36.5 | 0 | 12.6 | -7 | 7 | 1003 | 0.33 | 11.5 | 61.2 | 40 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-03-26 12:38 | 32.7 | 28.4 | 2.6 | 36.3 | -27.07 | 27.1 | 1003 | 0.1 | 2.9 | 9.8 | 15 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-03-26 12:35 | 52.2 | 37.8 | 0.1 | 9.9 | -0.25 | 0.3 | 1003 | 0.31 | 5.2 | 28.3 | 15 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-03-26 12:33 | 54.3 | 37.9 | 0 | 7.8 | -4.28 | 4.3 | 1003 | 4.2 | 41 | 233.4 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-03-26 12:32 | 53.6 | 36.5 | 0 | 9.9 | -4.82 | 4.8 | 1003 | 0.38 | 2.8 | 16 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-03-26 12:30 | 25.5 | 26.1 | 0.5 | 47.9 | -0.46 | 0.5 | 1002 | 1.07 | 0.5 | 1.4 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-03-26 12:28 | 50.9 | 31.3 | 3.3 | 14.5 | -40.33 | 40.3 | 1003 | 0.01 | 1.1 | 5.8 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-03-26 12:26 | 44.4 | 32.7 | 0 | 22.9 | -18.82 | 18.8 | 1003 | 6.65 | 50.9 | 237 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-03-26 12:24 | 47 | 30.6 | 1.4 | 21 | -2.18 | 2.2 | 1003 | 0.63 | 3.7 | 18.1 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2018-03-26 12:22 | 64.7 | 35.9 | 0 | 0 | -33.58 | 33.6 | 1003 | 16.02 | 2.1 | 14.1 | 99 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-03-26 12:20 | 50.7 | 34.7 | 0 | 14.6 | -51.29 | 51.3 | 1003 | 0.11 | 6.5 | 34.3 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-03-26 10:55 | 12 | 22.2 | 2.1 | 63.7 | 0.07 | -0.1 | 1001 | 14.56 | 1.9 | 2.4 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2018-03-26 10:52 | 53.7 | 37.9 | 0 | 8.4 | -11.35 | 11.4 | 1001 | 4.67 | 43.1 | 242 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-03-26 10:50 | 42.1 | 33.7 | 1.2 | 23 | -1.72 | 1.7 | 1001 | 0.71 | 16.7 | 73.6 | 25 |  | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2018-03-26 10:48 | 48.9 | 36.2 | 0 | 14.9 | -3.31 | 3.3 | 1001 | 1.34 | 23 | 118 |  |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-03-26 10:47 | 32.6 | 32.6 | 0 | 34.8 | -11.62 | 11.6 | 1001 | 0.44 | 12.8 | 43.8 | 25 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-03-26 10:45 | 21.5 | 16.8 | 11.6 | 50.1 | -0.18 | 0.2 | 1001 | 0.35 | 5.4 | 12.2 | 10 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-03-26 10:43 | 51.7 | 37.9 | 0 | 10.4 | -0.43 | 0.4 | 1001 | 10.29 | 7.5 | 40.4 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-03-26 10:41 | 48.2 | 38.5 | 1.8 | 11.5 | 0.19 | -0.2 | 1001 | -0.03 | 0 | 0 |  |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-03-26 10:39 | 56.4 | 38.7 | 0 | 4.9 | -1.08 | 1.1 | 1000 | 8.55 | 6.9 | 40.5 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2018-03-26 10:35 | 42.8 | 37 | 1.2 | 19 | -0.59 | 0.6 | 1000 | -0.05 | 0 | 0 | 5 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2018-03-26 10:33 | 55.4 | 38.8 | 0.9 | 4.9 | -1.11 | 1.1 | 1000 | 0.07 | 1.2 | 6.8 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2018-03-26 10:31 | 19.9 | 12.6 | 14.1 | 53.4 | 0.08 | -0.1 | 1000 | -0.03 | 0 | 0 | 0 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2018-03-26 10:30 | 58.5 | 42.1 | 0 | 0 | -6.86 | 6.9 | 1000 | 0.01 | 1 | 6.3 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2018-03-26 10:28 | 48.4 | 38.7 | 0 | 12.9 | -0.52 | 0.5 | 1000 | 2.9 | 7.7 | 39.3 | 20 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-03-26 10:26 | 41.4 | 29.8 | 4.1 | 24.7 | -13.24 | 13.2 | 1000 | 7.23 | 53.2 | 230.4 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-03-26 10:23 | 45.9 | 35.6 | 0 | 18.5 | -1.13 | 1.1 | 1000 | 0.07 | 5.4 | 25.8 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2018-03-26 10:21 | 47.5 | 37.1 | 0 | 15.4 | -1.52 | 1.5 | 1000 | 0.5 | 14 | 69.5 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2018-03-26 10:19 | 50.7 | 38.1 | 0 | 11.2 | -3.12 | 3.1 | 1000 | 0.52 | 14.4 | 76.3 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-03-26 10:18 | 51.7 | 37.2 | 1.3 | 9.8 | -0.78 | 0.8 | 1000 | 0.37 | 12.1 | 65.5 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2018-03-26 10:16 | 56 | 39.2 | 0 | 4.8 | -2.2 | 2.2 | 1000 | 6.65 | 24 | 140.8 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-03-26 10:14 | 47.9 | 36.2 | 1 | 14.9 | -1.39 | 1.4 | 1000 | -0.01 | 0 | 0 | 25 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2018-03-26 10:12 | 54.8 | 40.5 | 0 | 4.7 | -1.05 | 1.1 | 1000 | 0.12 | 7 | 40.2 | 25 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2018-03-26 10:09 | 48.3 | 38.9 | 0 | 12.8 | -0.46 | 0.5 | 1000 | 0.61 | 7.2 | 36.2 | 15 |  | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2018-03-26 10:07 | 51.6 | 39.5 | 0 | 8.9 | -0.43 | 0.4 | 1000 | 0.13 | 2.1 | 11.3 | 10 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-03-26 08:40 | 58.5 | 40.5 | 0 | 1 | -4.27 | 4.3 | 1000 | 2.05 | 28.7 | 175.6 | 50 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2018-03-26 08:37 | 53.6 | 40 | 0 | 6.4 | -20.74 | 20.7 | 999 | -16.87 | 0 | 0 | 40 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-03-26 08:34 | 47.1 | 37.1 | 0.6 | 15.2 | -3.07 | 3.1 | 999 | 2.38 | 14.2 | 69.8 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2018-03-26 08:32 | 51.7 | 40.5 | 0 | 7.8 | -59 | 59 | 999 | -8.33 | 0 | 0 | 70 |  | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2018-03-26 08:29 | 55.6 | 40.1 | 0 | 4.3 | 0.11 | -0.1 | 1000 | 0.03 | 0.8 | 4.5 | 5 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-03-26 08:25 | 55.9 | 38.7 | 0.2 | 5.2 | -3.44 | 3.4 | 1000 | 7.28 | 25.1 | 147 | 30 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-03-26 08:23 | 53.3 | 37.9 | 0.3 | 8.5 | -18.08 | 18.1 | 1000 | 11.51 | 31.2 | 174.4 | 40 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-03-26 08:20 | 41.1 | 28.8 | 5.2 | 24.9 | -1.27 | 1.3 | 1000 | 1.15 | 9.9 | 42.7 | 5 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-03-23 10:46 | 50.8 | 36.2 | 0.6 | 12.4 | -3.38 | 3.4 | 1016 | 9.32 | 28.3 | 150.6 | 27 |  | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-03-23 10:36 | 42.6 | 29.5 | 4.4 | 23.5 | -1.18 | 1.2 | 1015 | 1.11 | 9.7 | 43.2 | 15 |  | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-02-21 10:10 | 36.8 | 32.5 | 0 | 30.7 | 0.1 | -0.1 | 1007 | 0.06 | 1 | 4 | 3 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2018-02-21 10:08 | 0.2 | 0.1 | 20.7 | 79 | -55.4 | 55.4 | 1007 | -0.01 | 0 | 0 | 0 | 28.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2018-02-21 10:07 | 0.7 | 0.4 | 18.9 | 80 | -55.5 | 55.5 | 1007 | -0.05 | 0 | 0 | 0 | 27.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2018-02-21 10:05 | 46.4 | 36.2 | 0 | 17.4 | -4 | 4 | 1007 | 8.95 | 12.8 | 62 | 20 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2018-02-21 10:03 | 56.8 | 39.1 | 0 | 4.1 | -6.5 | 6.5 | 1007 | 15.95 | 34.9 | 207 | 40 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2018-02-21 10:00 | 23.4 | 28.3 | 0 | 48.3 | -0.5 | 0.5 | 1006 | 0.36 | 5.1 | 12 | 5 | 26.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2018-02-21 09:57 | 46.3 | 36.9 | 0 | 16.8 | -5.2 | 5.2 | 1007 | 8.52 | 25.3 | 123 | 25 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-02-21 09:55 | 58.6 | 39.8 | 0 | 1.6 | -57.8 | 57.8 | 1007 | 10.03 | 27.3 | 167 | 45 | 28.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2018-02-21 09:53 | 0.4 | 0.2 | 21.1 | 78.3 | -55.9 | 55.9 | 1007 | 0.01 | 0.7 | 0 | 5 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2018-02-21 09:51 | 1.4 | 1 | 20.7 | 76.9 | -56 | 56 | 1007 | 0.06 | 7.4 | 1 | 5 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-02-21 09:49 | 0.2 | 0.1 | 20.9 | 78.8 | -56.2 | 56.2 | 1007 | 0.05 | 6.9 | 0 | 5 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-02-21 09:47 | 52.8 | 36.3 | 0 | 10.9 | -6.6 | 6.6 | 1007 | 11.32 | 29.2 | 162 | 40 | 38.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2018-02-21 09:45 | 0.2 | 0.1 | 21 | 78.7 | -55.8 | 55.8 | 1007 | 0.05 | 6.6 | 0 | 10 | 27.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-02-21 09:42 | 60.7 | 40.3 | 0 | 0 | -61.6 | 61.6 | 1007 | 12.3 | 107.2 | 681 | 99 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2018-02-20 15:51 | 64.1 | 40.8 | 0 | 0 | -24.1 | 24.1 | 1011 | 10.61 | 98.9 | 664 | 99 | 45.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2018-02-20 15:50 | 63.4 | 41.6 | 0 | 0 | -30.6 | 30.6 | 1011 | 0.34 | 5 | 33 | 99 | 39.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2018-02-20 15:49 | 62.1 | 42 | 0 | 0 | -20.8 | 20.8 | 1011 | 16.16 | 121.9 | 793 | 99 | 42.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2018-02-20 15:48 | 61.1 | 41.2 | 0 | 0 | -20.2 | 20.2 | 1011 | 16.67 | 123.9 | 793 | 99 | 42.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2018-02-20 15:45 | 57.2 | 37.6 | 0 | 5.2 | -3.5 | 3.5 | 1012 | 2.82 | 14.7 | 88 | 25 | 36.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2018-02-20 15:43 | 51.3 | 35.1 | 0 | 13.6 | -0.3 | 0.3 | 1011 | 1.95 | 12.2 | 65 | 20 | 35.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2018-02-20 15:41 | 55.2 | 35.8 | 0 | 9 | -0.9 | 0.9 | 1011 | 2.93 | 15.1 | 87 | 25 | 35.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2018-02-20 15:40 | 57.3 | 37.1 | 0 | 5.6 | -0.9 | 0.9 | 1012 | 4.27 | 18.2 | 109 | 40 | 34.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2018-02-20 15:37 | 46.5 | 33.4 | 0 | 20.1 | -0.1 | 0.1 | 1012 | 0.6 | 6.7 | 33 | 20 | 33 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2018-02-20 15:35 | 49.5 | 34.1 | 0 | 16.4 | -0.5 | 0.5 | 1012 | 2 | 12.4 | 64 | 20 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-02-20 15:33 | 52.7 | 35.7 | 0 | 11.6 | -1.1 | 1.1 | 1010 | 4.96 | 19.6 | 108 | 25 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-02-20 15:26 | 55.9 | 38.4 | 0 | 5.7 | -7.9 | 7.9 | 1010 | 11.04 | 28.6 | 167 | 40 | 45.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2018-02-20 15:26 | 61.3 | 41.1 | 0 | 0 | -34 | 34 | 1010 | 22.5 | 143.9 | 925 | 99 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2018-02-20 15:24 | 61.3 | 40.5 | 0 | 0 | -47.4 | 47.4 | 1010 | 2.26 | 44.9 | 288 | 99 | 45 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2018-02-20 15:23 | 0.7 | 0.3 | 20.2 | 78.8 | -4.4 | 4.4 | 1010 | -0.03 | 0 | 0 | 0 | 36.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2018-02-20 15:22 | 20.5 | 12.3 | 13.1 | 54.1 | -50.4 | 50.4 | 1010 | 0.04 | 3.4 | 7 | 99 | 37.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2018-02-20 15:21 | 60.6 | 42.2 | 0 | 0 | -25.6 | 25.6 | 1010 | 0.01 | 0.7 | 5 | 5 | 36.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2018-02-20 15:19 | 57.3 | 41.5 | 0 | 1.2 | -0.1 | 0.1 | 1009 | 0.2 | 3.9 | 23 | 5 | 35.1 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2018-02-20 15:15 | 61.3 | 42.2 | 0 | 0 | -18.9 | 18.9 | 1009 | 12.41 | 106.2 | 682 | 99 | 45.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2018-02-20 15:13 | 6.1 | 12.1 | 12 | 69.8 | -26.5 | 26.5 | 1010 | 5.17 | 18.8 | 12 | 0 | 37.8 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2018-02-20 15:10 | 4.9 | 2.6 | 18.9 | 73.6 | -1 | 1 | 1010 | -0.04 | 0 | 0 | 0 | 31.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2018-02-20 15:09 | 54 | 37 | 0 | 9 | -11.8 | 11.8 | 1010 | 15.8 | 34.6 | 196 | 40 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-02-20 15:08 | 57.1 | 38.1 | 0 | 4.8 | -7.9 | 7.9 | 1010 | 14.83 | 72.5 | 433 | 70 | 38.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-02-20 15:06 | 55.7 | 39.8 | 0 | 4.5 | -3.7 | 3.7 | 1010 | 22.71 | 40.9 | 239 | 40 | 44.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-02-20 15:05 | 60.4 | 40.4 | 0 | 0 | -16.3 | 16.3 | 1010 | 30.49 | 47.5 | 301 | 70 | 44.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2018-02-20 15:03 | 54.3 | 38.5 | 0 | 7.2 | -50.3 | 50.3 | 1010 | -0.08 | 0 | 0 | 20 | 31.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-02-20 15:02 | 37.4 | 39.8 | 0 | 22.8 | -3.6 | 3.6 | 1010 | 0.63 | 6.6 | 25 | 5 | 39.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2018-02-20 15:01 | 63.6 | 38.7 | 0 | 0 | -20.6 | 20.6 | 1010 | 2.12 | 12.9 | 86 | 25 | 32.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2018-02-20 14:59 | 58.7 | 37.5 | 0 | 3.8 | -15.6 | 15.6 | 1010 | 21.35 | 40.6 | 250 | 45 | 33.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2018-02-20 14:57 | 0.7 | 0.2 | 19.4 | 79.7 | -9.4 | 9.4 | 1010 | -0.02 | 0 | 0 | 0 | 37.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-02-20 14:56 | 60 | 40.1 | 0 | 0 | -3.6 | 3.6 | 1010 | 17.1 | 36 | 226 | 45 | 40.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-02-20 13:39 | 50.3 | 34.8 | 0 | 14.9 | 0 | 0 | 1011 | 2.13 | 6.3 | 33 | 20 | 35.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-02-20 13:38 | 49.9 | 33.9 | 0 | 16.2 | -4.6 | 4.6 | 1011 | 9.13 | 56.6 | 296 | 50 | 39.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-02-20 13:37 | 59.2 | 38.1 | 0 | 2.7 | -36.8 | 36.8 | 1011 | 6.97 | 22.9 | 142 | 60 | 34.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2018-02-20 13:35 | 61.4 | 38.7 | 0 | 0 | -52.6 | 52.6 | 1011 | 0.21 | 8.5 | 55 | 99 | 35.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-02-20 13:34 | 50.1 | 36.8 | 0 | 13.1 | -26.4 | 26.4 | 1011 | 8.02 | 52 | 273 | 70 | 40.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-02-20 13:32 | 26.1 | 19.6 | 5.5 | 48.8 | -0.1 | 0.1 | 1011 | 0.62 | 1.7 | 4 | 5 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2018-02-20 13:31 | 50 | 36.6 | 0 | 13.4 | -1.2 | 1.2 | 1011 | 1.41 | 5.1 | 26 |  | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2018-02-20 13:30 | 58.1 | 37.5 | 0 | 4.4 | -41.5 | 41.5 | 1011 | 8.33 | 88.4 | 538 |  | 32 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2018-02-20 13:28 | 44.5 | 31.8 | 0 | 23.7 | -1.3 | 1.3 | 1011 | 16.63 | 1.9 | 9 | 5 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-02-20 13:27 | 52.5 | 36.4 | 0 | 11.1 | -2.6 | 2.6 | 1011 | 3.98 | 17.5 | 96 | 20 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-02-20 13:26 | 51.6 | 35.4 | 0 | 13 | -4.6 | 4.6 | 1011 | 3.61 | 35.7 | 193 | 50 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2018-02-20 13:25 | 52.2 | 37.3 | 0 | 10.5 | -0.5 | 0.5 | 1011 | 2.51 | 13.7 | 74 | 25 | 40.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2018-02-20 13:24 | 50.7 | 35.3 | 0 | 14 | -33.9 | 33.9 | 1011 | 24.18 | 91 | 484 | 99 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2018-02-20 13:19 | 5.6 | 5.7 | 7.7 | 81 | 0 | 0 | 1011 | -0.11 | 0 | 0 | 0 | 32.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-02-20 13:18 | 52.8 | 38.5 | 0 | 8.7 | -5.5 | 5.5 | 1011 | 3.26 | 15.5 | 85 | 20 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2018-02-20 13:17 | 54.9 | 40.1 | 0 | 5 | -37.6 | 37.6 | 1011 | 22.05 | 138.5 | 797 | 99 | 48.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-02-20 13:16 | 42.9 | 36.3 | 0 | 20.8 | -9.2 | 9.2 | 1011 | >>>> | 0 | 0 | 50 | 37 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-02-20 13:13 | 51.6 | 36.1 | 0.1 | 12.2 | -1.2 | 1.2 | 1011 | 0.67 | 15.4 | 83 | 20 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2018-02-20 13:11 | 51 | 37.2 | 0 | 11.8 | -2.1 | 2.1 | 1011 | 1.49 | 23 | 123 | 20 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-02-20 13:10 | 51 | 36.4 | 0 | 12.6 | -0.2 | 0.2 | 1011 | 7.23 | 11.6 | 62 | 20 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-02-20 13:10 | 45.4 | 34.6 | 0 | 20 | -5.3 | 5.3 | 1011 | 4.86 | 40.7 | 194 | 25 | 40.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2018-02-20 13:08 | 55.4 | 37.4 | 0 | 7.2 | -6.9 | 6.9 | 1011 | 24.44 | 43.4 | 252 | 50 | 34.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2018-02-20 13:07 | 56.6 | 38.3 | 0 | 5.1 | -47 | 47 | 1011 | 0.16 | 7.4 | 43 | 20 | 36.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-02-20 13:06 | 54.9 | 36.2 | 0 | 8.9 | -1.8 | 1.8 | 1011 | 1.19 | 20.7 | 119 | 25 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-02-20 13:05 | 44.6 | 31.5 | 1.4 | 22.5 | -0.2 | 0.2 | 1011 | 11.33 | 7.4 | 34 | 10 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-02-20 13:03 | 52.5 | 39.1 | 0 | 8.4 | 0 | 0 | 1011 | 5 | 4.8 | 26 | 10 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2018-02-20 12:57 | 55.6 | 39 | 0 | 5.4 | -52.7 | 52.7 | 1010 | 0.92 | 28.4 | 165 | 99 | 42 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2018-02-20 12:56 | 38 | 26.5 | 5.2 | 30.3 | -0.2 | 0.2 | 1010 | -0.15 | 0 | 0 | 0 | 32.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2018-02-20 12:55 | 58.2 | 41 | 0 | 0.8 | -50.8 | 50.8 | 1010 | 1.19 | 9.2 | 56 | 99 | 38.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2018-02-20 12:54 | 49.1 | 33.3 | 1.7 | 15.9 | -53.3 | 53.3 | 1010 | -0.18 | 0 | 0 | 99 | 31.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2018-02-20 12:50 | 50.7 | 37.3 | 0 | 12 | -13.5 | 13.5 | 1010 | 11.69 | 63.4 | 336 | 50 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2018-02-20 12:49 | 59.3 | 41.5 | 0 | 0 | -50.7 | 50.7 | 1010 | 0.26 | 4.4 | 27 | 99 | 29.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2018-02-20 12:46 | 4.1 | 7.5 | 12.9 | 75.5 | -5.2 | 5.2 | 1010 | -0.07 | 0 | 0 | 0 | 34.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2018-02-20 12:45 | 52.2 | 37.3 | 0 | 10.5 | -23.8 | 23.8 | 1010 | 6.44 | 46.4 | 253 | 50 | 46.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2018-02-20 12:44 | 53 | 38 | 0 | 9 | -52.4 | 52.4 | 1010 | 2.39 | 45.7 | 253 | 99 | 42.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-02-20 12:43 | 54.7 | 40.2 | 0 | 5.1 | -0.4 | 0.4 | 1010 | 1.17 | 9.2 | 52 | 40 | 49.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2018-02-20 11:30 | 56 | 36.3 | 0 | 7.7 | -44.3 | 44.3 | 1011 | 0.15 | 3.4 | 20 | 99 | 29.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2018-02-20 11:27 | 60.3 | 35.9 | 0 | 3.8 | -31.1 | 31.1 | 1011 | 0.7 | 6.7 | 42 | 25 | 26.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2018-02-20 11:25 | 60.8 | 37.5 | 0 | 1.7 | -1.3 | 1.3 | 1011 | -0.51 | 0 | 0 | 15 | 28.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2018-02-20 10:59 | 46.4 | 34.3 | 0 | 19.3 | -4.7 | 4.7 | 1012 | 1.69 | 23.8 | 116 | 25 | 46.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2018-02-20 10:57 | 35.6 | 32.4 | 0 | 32 | -4.3 | 4.3 | 1012 | 5.71 | 20.3 | 75 | 25 | 36.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2018-02-20 10:55 | 37.4 | 32 | 0 | 30.6 | -8.3 | 8.3 | 1012 | 8.98 | 12.6 | 49 | 22 | 36.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2018-02-20 10:51 | 30.9 | 21.1 | 8.1 | 39.9 | -1.4 | 1.4 | 1012 | 2.27 | 13.3 | 43 | 15 | 23.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2018-02-20 10:48 | 39.1 | 33.5 | 0 | 27.4 | -1.3 | 1.3 | 1012 | 1.09 | 19.1 | 78 | 22 | 41.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2018-02-20 10:46 | 53.4 | 37.2 | 0 | 9.4 | -1.4 | 1.4 | 1012 | 4.74 | 19.1 | 106 | 25 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2018-02-20 10:44 | 48.4 | 35.9 | 0 | 15.7 | -2 | 2 | 1012 | 3.24 | 7.8 | 39 | 10 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-02-20 10:43 | 51.6 | 36.3 | 0 | 12.1 | -1.4 | 1.4 | 1012 | 0.56 | 14.2 | 77 | 20 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-02-20 10:42 | 57.7 | 38.9 | 0 | 3.4 | -55.7 | 55.7 | 1012 | 0.62 | 6.7 | 40 | 99 | 32.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-02-20 10:40 | 5.2 | 2.9 | 17.5 | 74.4 | -57.5 | 57.5 | 1012 | 0.1 | 9.4 | 5 | 99 | 20.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-02-20 10:39 | 55.6 | 35.5 | 0 | 8.9 | 0 | 0 | 1012 | 0.08 | 2.5 | 15 | 10 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-02-20 10:38 | 52.8 | 37.5 | 0 | 9.7 | -5.4 | 5.4 | 1012 | 3.76 | 16.9 | 93 | 25 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-02-20 10:37 | 46.1 | 35.4 | 0 | 18.5 | -1.2 | 1.2 | 1011 | 4.15 | 8.8 | 42 | 25 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2018-02-20 10:35 | 0.2 | 0.1 | 20.3 | 79.4 | -4.4 | 4.4 | 1011 | -0.06 | 0 | 0 | 5 | 23.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2018-02-20 10:34 | 9.7 | 5.2 | 17.3 | 67.8 | -9.1 | 9.1 | 1011 | -0.04 | 0 | 0 | 0 | 29.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-02-20 10:33 | 0.5 | 0.3 | 19 | 80.2 | -3 | 3 | 1011 | -0.02 | 0 | 0 | 0 | 26.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-02-20 10:32 | 58.6 | 38.3 | 0 | 3.1 | -5.2 | 5.2 | 1011 | 2.61 | 14.3 | 87 | 28 | 31.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2018-02-20 10:31 | 53.8 | 39 | 0 | 7.2 | -0.7 | 0.7 | 1011 | 0.87 | 8.1 | 45 | 20 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2018-02-20 10:14 | 56.7 | 38 | 0 | 5.3 | -74.8 | 74.8 | 1010 | -0.13 | 0 | 0 | 99 | 28.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2018-02-20 10:13 | 50.3 | 36.5 | 0 | 13.2 | -27.8 | 27.8 | 1010 | 3.91 | 17.1 | 90 | 50 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2018-02-20 10:12 | 55.8 | 37.8 | 0 | 6.4 | -74.7 | 74.7 | 1010 | 0.02 | 1.1 | 7 | 99 | 27.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-02-20 10:10 | 47.9 | 34.3 | 0 | 17.8 | -12.5 | 12.5 | 1010 | 7.31 | 23.7 | 119 | 30 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2018-02-20 10:09 | 47.5 | 36.9 | 0 | 15.6 | -13.4 | 13.4 | 1010 | 6.75 | 22.1 | 110 | 40 | 40.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-02-20 10:08 | 59.7 | 39.9 | 0 | 0.4 | -15 | 15 | 1010 | 3.39 | 16.2 | 101 | 35 | 28.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-02-20 10:06 | 39.1 | 30.3 | 1.8 | 28.8 | -2.5 | 2.5 | 1010 | 0.07 | 2.3 | 9 | 5 | 29.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-02-20 10:05 | 54.9 | 37.8 | 0 | 7.3 | -27.4 | 27.4 | 1010 | >>>> | 0 | 0 | 99 | 32.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-02-20 10:03 | 42.8 | 35.3 | 0 | 21.9 | -2.7 | 2.7 | 1010 | 16.84 | 35 | 157 | 42 | 38.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-02-20 10:02 | 49.8 | 37.7 | 0 | 12.5 | -6.9 | 6.9 | 1010 | 1.47 | 22.6 | 118 | 25 | 33.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-02-20 09:59 | 50 | 35.5 | 0 | 14.5 | -18.3 | 18.3 | 1009 | 0.08 | 5.3 | 28 | 25 | 40.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2018-02-20 09:58 | 48.8 | 35.3 | 0 | 15.9 | -6 | 6 | 1009 | 4.47 | 39.7 | 203 | 40 | 33.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-02-20 09:57 | 37.3 | 30 | 0.8 | 31.9 | -55.3 | 55.3 | 1009 | -0.29 | 0 | 0 | 50 | 30.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-02-20 09:55 | 23.5 | 21.8 | 3.9 | 50.8 | -1.3 | 1.3 | 1009 | 0.6 | 14.5 | 35 | 15 | 28.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2018-02-20 09:53 | 48.3 | 36.6 | 0 | 15.1 | -52.7 | 52.7 | 1009 | 0.45 | 20 | 101 | 99 | 32.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-02-20 09:07 | 58.4 | 38.9 | 0 | 2.7 | -52.5 | 52.5 | 1010 | 0.19 | 8.1 | 49 | 99 | 28.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-02-20 09:06 | 43 | 33 | 0 | 24 | -4.2 | 4.2 | 1010 | 1.62 | 11.1 | 50 | 15 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2018-02-20 09:04 | 32.1 | 30.6 | 0 | 37.3 | -23 | 23 | 1010 | 10.7 | 7 | 23 | 17 | 28.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-02-20 09:03 | 54.5 | 38.9 | 0 | 6.6 | -46.6 | 46.6 | 1010 | 7.34 | 49.9 | 285 | 99 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-02-20 09:01 | 29.5 | 29 | 0 | 41.5 | -17.2 | 17.2 | 1010 | 2.66 | 13.8 | 42 | 22 | 34 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-02-20 09:00 | 45.3 | 33.7 | 0 | 21 | -5.3 | 5.3 | 1010 | 0.88 | 28.5 | 135 | 42 | 37.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-02-20 08:58 | 53.1 | 38.1 | 0 | 8.8 | -0.9 | 0.9 | 1010 | 5.29 | 20 | 111 | 25 | 35 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2018-02-20 08:57 | 60.4 | 40.5 | 0 | 0 | -44.1 | 44.1 | 1010 | 7.46 | 50.2 | 318 | 99 | 40.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-02-20 08:56 | 45.7 | 36.1 | 0 | 18.2 | -15.3 | 15.3 | 1010 | 0.42 | 11.9 | 57 | 40 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-02-20 08:54 | 27.7 | 26.9 | 1.3 | 44.1 | -27.3 | 27.3 | 1010 | -0.05 | 0 | 0 | 10 | 28 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-02-20 08:52 | 41.5 | 34.9 | 0 | 23.6 | -0.5 | 0.5 | 1010 | 0.23 | 4.1 | 18 | 10 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-02-20 08:51 | 51.7 | 37.2 | 0 | 11.1 | -4.2 | 4.2 | 1010 | 3.94 | 37.6 | 204 | 40 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-02-20 08:50 | 40.9 | 30.3 | 0.9 | 27.9 | -6.1 | 6.1 | 1010 | 0.29 | 2.3 | 10 | 5 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-02-20 08:49 | 21.4 | 25.1 | 0 | 53.5 | -0.2 | 0.2 | 1010 | 0.42 | 0.3 | 0 | 5 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-02-20 08:47 | 0.4 | 0.5 | 17.1 | 82 | -35.3 | 35.3 | 1010 | -0.14 | 0 | 0 | 5 | 28 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-02-20 08:46 | 43.2 | 32.6 | 0 | 24.2 | -21 | 21 | 1010 | 7.52 | 51.1 | 231 | 50 | 31 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-02-20 08:44 | 38.1 | 26.8 | 1.3 | 33.8 | -7.2 | 7.2 | 1009 | 1.86 | 5.9 | 23 | 10 | 25.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2018-02-20 08:43 | 65.5 | 36.4 | 0 | 0 | -34.1 | 34.1 | 1009 | 15.86 | 1.9 | 13 | 99 | 26.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-02-20 08:41 | 45.2 | 33.3 | 0 | 21.5 | -46.2 | 46.2 | 1009 | -0.04 | 0 | 0 | 40 | 28.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2018-02-20 08:03 | 0.4 | 0.3 | 16.1 | 83.2 | 0 | 0 | 1007 | -0.07 | 0 | 0 | 0 | 31.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-02-20 08:01 | 54.5 | 40.2 | 0 | 5.3 | -36.6 | 36.6 | 1007 | 4.03 | 36.7 | 209 | 40 | 40.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-02-20 08:00 | 0.2 | 0.1 | 19.4 | 80.3 | 0.1 | -0.1 | 1007 | -0.02 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-02-20 07:59 | 0.5 | 1.4 | 18.5 | 79.6 | 0 | 0 | 1007 | -0.02 | 0 | 0 | 0 | 19.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-02-20 07:57 | 55 | 39.9 | 0 | 5.1 | -0.6 | 0.6 | 1007 | 0.58 | 14.1 | 81 | 50 | 46.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-02-20 07:54 | 44.1 | 36.8 | 0 | 19.1 | -5.5 | 5.5 | 1007 | 12.81 | 30.5 | 141 | 37 | 38.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-02-20 07:52 | 39.4 | 30.3 | 4.2 | 26.1 | -40.3 | 40.3 | 1006 | 6.69 | 75.9 | 313 | 50 | 45.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-02-20 07:48 | 49.2 | 38.5 | 0 | 12.3 | -1.1 | 1.1 | 1006 | 1.51 | 10.6 | 54 | 15 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2018-02-20 07:47 | 1.7 | 2.4 | 9.9 | 86 | 0.1 | -0.1 | 1006 | -0.11 | 0 | 0 | 0 | 29.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2018-02-20 07:46 | 56.1 | 40.2 | 0 | 3.7 | -58.5 | 58.5 | 1006 | 1.34 | 34.6 | 203 | 99 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-02-20 07:44 | 38.9 | 35.4 | 0 | 25.7 | -0.6 | 0.6 | 1006 | 11.25 | 28 | 114 | 27 | 48.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2018-02-19 15:04 | 54.9 | 39.1 | 0 | 6 | -34.7 | 34.7 | 1005 | 18.39 | 77.4 | 445 | 99 | 50.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2018-02-19 15:03 | 59.1 | 40.3 | 0 | 0.6 | -42.6 | 42.6 | 1005 | 8.14 | 52.1 | 323 | 99 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2018-02-19 15:02 | 58.6 | 39.8 | 0 | 1.6 | -41.1 | 41.1 | 1005 | 11.43 | 101.1 | 621 | 99 | 43.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2018-02-19 15:01 | 3.5 | 1.8 | 12.7 | 82 | -0.5 | 0.5 | 1005 | -0.04 | 0 | 0 | 0 | 44.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-02-19 15:00 | 49.2 | 35.9 | 0.9 | 14 | -34.8 | 34.8 | 1005 | 6.46 | 45.7 | 236 | 50 | 50.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-02-19 14:59 | 59 | 40.6 | 0 | 0.4 | -51.2 | 51.2 | 1005 | 0.38 | 11.2 | 69 | 99 | 40.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2018-02-19 14:58 | 36.2 | 25.9 | 7.3 | 30.6 | -24.1 | 24.1 | 1005 | -0.2 | 0 | 0 | 0 | 26.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-02-19 14:56 | 52.5 | 38.9 | 0 | 8.6 | -1.1 | 1.1 | 1005 | 1.78 | 11.6 | 64 | 20 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-02-19 14:55 | 58.6 | 40.5 | 0 | 0.9 | -22.4 | 22.4 | 1005 | 2.15 | 27 | 166 | 40 | 43.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-02-19 14:53 | 57.2 | 41.9 | 0 | 0.9 | -49.8 | 49.8 | 1005 | 5.32 | 41.7 | 249 | 99 | 43 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2018-02-19 14:52 | 0.4 | 0.1 | 21 | 78.5 | -6.7 | 6.7 | 1005 | -0.01 | 0 | 0 | 0 | 26 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2018-02-19 14:51 | 17.4 | 11.1 | 15.8 | 55.7 | -0.2 | 0.2 | 1005 | -0.03 | 0 | 0 | 0 | 28 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2018-02-19 14:50 | 2.5 | 1.7 | 20.8 | 75 | -44.1 | 44.1 | 1005 | -0.01 | 0 | 0 | 5 | 28.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2018-02-19 14:49 | 59 | 40 | 0 | 1 | -49.6 | 49.6 | 1005 | 3.84 | 58.3 | 361 | 99 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2018-02-19 14:48 | 52.8 | 38 | 0 | 9.2 | -5.4 | 5.4 | 1005 | 10.76 | 28.6 | 158 | 25 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-02-19 14:47 | 49.4 | 36.4 | 0 | 14.2 | -5 | 5 | 1005 | 11.91 | 30.1 | 156 | 20 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-02-19 14:46 | 51.6 | 38 | 0 | 10.4 | -7.8 | 7.8 | 1005 | 2.46 | 29.6 | 160 | 25 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-02-19 14:45 | 39.9 | 29 | 5.2 | 25.9 | -52.5 | 52.5 | 1005 | -0.15 | 0 | 0 | 50 | 26.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2018-02-19 14:36 | 0.4 | 0.2 | 19.9 | 79.5 | -28.7 | 28.7 | 1005 | -0.17 | 0 | 0 | 0 | 26.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2018-02-19 14:35 | 60.1 | 40 | 0 | 0 | -55.8 | 55.8 | 1005 | 2.32 | 46.5 | 293 | 99 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2018-02-19 14:34 | 3.4 | 2.3 | 19.3 | 75 | -58 | 58 | 1005 | -0.14 | 0 | 0 | 99 | 26.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2018-02-19 14:33 | 11.4 | 7.3 | 17.4 | 63.9 | -57.9 | 57.9 | 1005 | -0.13 | 0 | 0 | 99 | 26.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2018-02-19 14:32 | 9 | 11.9 | 13.8 | 65.3 | 0 | 0 | 1005 | -0.2 | 0 | 0 | 0 | 25.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2018-02-19 14:30 | 46.6 | 36.1 | 0 | 17.3 | -1.1 | 1.1 | 1005 | 17.53 | 9.1 | 44 | 25 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-02-19 14:29 | 56.6 | 39.9 | 0 | 3.5 | -6.3 | 6.3 | 1005 | 1.64 | 24.3 | 144 | 25 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2018-02-19 14:28 | 58.2 | 41.4 | 0 | 0.4 | -58.2 | 58.2 | 1005 | -0.06 | 0 | 0 | 99 | 32.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2018-02-19 14:24 | 18.4 | 12.2 | 15.4 | 54 | -58.2 | 58.2 | 1005 | -0.17 | 0 | 0 | 99 | 24.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2018-02-19 14:21 | 45.9 | 34.9 | 1.9 | 17.3 | -57.7 | 57.7 | 1005 | -0.1 | 0 | 0 | 30 | 24 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-02-19 13:52 | 0.4 | 0.2 | 20.2 | 79.2 | 0.1 | -0.1 | 1007 | 8.08 | 24.6 | 1 | 0 | 28 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2018-02-19 13:49 | 44.1 | 34.6 | 0 | 21.3 | -15.5 | 15.5 | 1007 | 7.83 | 51.7 | 239 | 42 | 35.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-02-19 13:47 | 41.2 | 32.5 | 0 | 26.3 | -1.5 | 1.5 | 1007 | 1.61 | 23.4 | 101 | 18 | 41.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2018-02-19 13:45 | 46.4 | 34.8 | 0 | 18.8 | -4.2 | 4.2 | 1007 | 1.8 | 25 | 121 | 20 | 37.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-02-19 13:44 | 31.6 | 29.6 | 0 | 38.8 | -54.6 | 54.6 | 1007 | 1.55 | 22.5 | 74 | 20 | 29.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-02-19 13:41 | 59.2 | 39 | 0 | 1.8 | 0.2 | -0.2 | 1007 | -0.02 | 0 | 0 | 10 | 27.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-02-19 13:40 | 48.6 | 36.3 | 0 | 15.1 | -0.4 | 0.4 | 1007 | 13.69 | 8.1 | 41 | 20 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-02-19 13:38 | 40 | 29.8 | 2.2 | 28 | -0.2 | 0.2 | 1007 | 2.98 | 7.5 | 31 | 10 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-02-19 13:37 | 53.7 | 37.3 | 0 | 9 | -0.8 | 0.8 | 1006 | 11.19 | 7.4 | 42 | 20 | 26.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2018-02-19 13:27 | 42.8 | 34.1 | 0 | 23.1 | -10.7 | 10.7 | 1006 | 8.08 | 51.7 | 232 | 48 | 46.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2018-02-19 13:25 | 8.5 | 5.8 | 15.8 | 69.9 | -48 | 48 | 1006 | -0.15 | 0 | 0 | 90 | 28 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2018-02-19 13:24 | 41.7 | 34.3 | 0 | 24 | -1.5 | 1.5 | 1006 | 2.92 | 3.6 | 16 | 17 | 37.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-02-19 13:22 | 50.4 | 37.6 | 0 | 12 | -1.2 | 1.2 | 1006 | 0.97 | 18.5 | 98 | 25 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-02-19 13:21 | 51.4 | 37.8 | 0 | 10.8 | -3 | 3 | 1006 | 0.9 | 18 | 96 | 25 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-02-19 13:20 | 29.9 | 29.3 | 0 | 40.8 | -0.7 | 0.7 | 1006 | 0.7 | 15.5 | 48 | 10 | 29.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-02-19 13:18 | 0.6 | 0.4 | 19.9 | 79.1 | 0 | 0 | 1006 | -0.06 | 0 | 0 | 0 | 21 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2018-02-19 13:17 | 28.2 | 28.6 | 0 | 43.2 | -1.8 | 1.8 | 1006 | 0.04 | 3.7 | 11 | 7 | 29.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2018-02-19 13:15 | 41.3 | 32.6 | 0 | 26.1 | -1.9 | 1.9 | 1006 | 1.71 | 24 | 104 | 45 | 43.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2018-02-19 13:14 | 49.6 | 37.8 | 0 | 12.6 | -21.6 | 21.6 | 1006 | 17.18 | 76 | 395 | 80 | 40.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2018-02-19 13:12 | 44.1 | 35.7 | 0 | 20.2 | -0.8 | 0.8 | 1006 | 0.17 | 7.6 | 35 | 15 | 31.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-02-19 13:09 | 41.9 | 32.8 | 0 | 25.3 | -1.2 | 1.2 | 1005 | 2.98 | 15 | 66 | 20 | 29.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-02-19 13:06 | 47.2 | 36.2 | 0.1 | 16.5 | 0.2 | -0.2 | 1005 | 1.87 | 11.8 | 58 | 25 | 34.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2018-02-19 13:04 | 46.5 | 36.4 | 0 | 17.1 | -2.4 | 2.4 | 1005 | 1.88 | 12 | 58 | 25 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-02-19 13:03 | 59.6 | 41.2 | 0 | 0 | 0.3 | -0.3 | 1005 | 1.33 | 10.2 | 64 | 22 | 27 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-02-19 13:01 | 60.1 | 40.9 | 0 | 0 | 0.3 | -0.3 | 1005 | 0.17 | 3.6 | 22 | 15 | 27.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-02-19 12:59 | 53.4 | 37.4 | 0 | 9.2 | -20.5 | 20.5 | 1005 | 0.96 | 8.5 | 48 | 20 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-02-19 12:58 | 45.6 | 36.5 | 0 | 17.9 | -4 | 4 | 1005 | 1.82 | 40.9 | 195 | 38 | 33.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2018-02-19 12:56 | 51.8 | 38.3 | 0 | 9.9 | -3 | 3 | 1005 | 8.71 | 12.8 | 69 | 20 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2018-02-19 12:54 | 51 | 36.9 | 0 | 12.1 | -4.2 | 4.2 | 1005 | 7.3 | 23.5 | 125 | 25 | 34 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-02-19 12:02 | 62.1 | 44.9 | 0 | 0 | -68.6 | 68.6 | 1006 | 4.57 | 39.2 | 255 | 99 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-02-19 12:01 | 59.8 | 49 | 0 | 0 | -14.4 | 14.4 | 1006 | 4.49 | 39.4 | 247 | 50 | 27.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-02-19 11:59 | 60.3 | 48.7 | 0 | 0 | -54.7 | 54.7 | 1006 | 18.97 | 79.7 | 503 | 99 | 26.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2018-02-19 11:57 | 50.3 | 51.6 | 0 | 0 | -4.1 | 4.1 | 1006 | 4.62 | 39.3 | 207 | 40 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2018-02-19 11:56 | 47.1 | 55.4 | 0 | 0 | -17.6 | 17.6 | 1005 | 1.16 | 19.2 | 95 | 25 | 24.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2018-02-19 11:53 | 57.2 | 38.9 | 0 | 3.9 | -5.8 | 5.8 | 1005 | 0 | 0.3 | 1 | 5 | 26.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2018-02-19 11:51 | 57.6 | 41 | 0 | 1.4 | -58.1 | 58.1 | 1005 | 0.29 | 16 | 97 | 99 | 37 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2018-02-19 11:50 | 53.1 | 38.7 | 0 | 8.2 | -1.1 | 1.1 | 1005 | 9.63 | 26.9 | 149 | 25 | 37.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-02-19 11:49 | 44.3 | 35.9 | 0 | 19.8 | -0.2 | 0.2 | 1005 | 6.78 | 11.2 | 52 | 12 | 31.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-02-19 11:48 | 48.1 | 38.3 | 0 | 13.6 | -3.9 | 3.9 | 1005 | 15.35 | 8.5 | 43 | 20 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2018-02-19 11:46 | 49 | 39.6 | 0 | 11.4 | -42.9 | 42.9 | 1005 | 6.6 | 21.1 | 108 | 50 | 51 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2018-02-19 11:45 | 49.1 | 38.1 | 0 | 12.8 | -8.3 | 8.3 | 1005 | 0.59 | 14.4 | 74 | 25 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2018-02-19 11:44 | 52.3 | 39.9 | 0 | 7.8 | -18.5 | 18.5 | 1005 | 15.56 | 33.2 | 182 | 50 | 47.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-02-19 11:43 | 50.6 | 37.4 | 0.7 | 11.3 | -39.8 | 39.8 | 1005 | 4.92 | 4.8 | 25 | 25 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2018-02-19 11:41 | 0.6 | 0.5 | 19.7 | 79.2 | -1.5 | 1.5 | 1005 | -0.01 | 0 | 0 | 5 | 24.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-02-19 11:32 | 53.8 | 38.5 | 0 | 7.7 | -2.4 | 2.4 | 1005 | 0.04 | 6.4 | 36 | 5 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2018-02-19 11:31 | 48.2 | 37.2 | 0 | 14.6 | -2.4 | 2.4 | 1005 | 7.29 | 23.2 | 117 | 40 | 37.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-02-19 11:30 | 49.9 | 38.9 | 0 | 11.2 | -0.1 | 0.1 | 1005 | 2.36 | 3.3 | 17 | 5 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2018-02-19 11:29 | 53.2 | 39.1 | 0 | 7.7 | -54.5 | 54.5 | 1005 | 3.92 | 58.3 | 324 | 99 | 43.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2018-02-19 11:28 | 51.7 | 38.4 | 0 | 9.9 | -13.3 | 13.3 | 1005 | 10.68 | 60.6 | 328 | 50 | 38 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2018-02-19 11:25 | 56.4 | 40.6 | 0 | 3 | -31.4 | 31.4 | 1005 | 12.81 | 31 | 183 | 99 | 30.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-02-19 11:24 | 38.1 | 34.2 | 0 | 27.7 | -0.1 | 0.1 | 1005 | 0.1 | 6 | 24 | 5 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-02-19 11:23 | 48 | 34.1 | 1.9 | 16 | -1.1 | 1.1 | 1005 | 2.22 | 28.2 | 141 | 25 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2018-02-19 11:21 | 48.8 | 37.5 | 0 | 13.7 | -27.3 | 27.3 | 1005 | 2.82 | 51.5 | 263 | 50 | 23.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-02-19 11:20 | 28.4 | 28.3 | 0 | 43.3 | -0.2 | 0.2 | 1005 | 1.88 | 0.6 | 1 | 2 | 22.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-02-19 11:18 | 40.7 | 33.1 | 0 | 26.2 | -0.8 | 0.8 | 1005 | -0.34 | 0 | 0 | 5 | 25.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2018-02-19 11:17 | 41.7 | 35.6 | 0 | 22.7 | -0.3 | 0.3 | 1005 | 2.14 | 12.4 | 54 | 17 | 39.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-02-19 11:14 | 58.5 | 42.9 | 0 | 0 | -57.8 | 57.8 | 1005 | 0.92 | 2 | 12 | 99 | 26.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-02-19 11:13 | 47 | 38.1 | 0 | 14.9 | -1.3 | 1.3 | 1005 | 5.87 | 20.3 | 100 | 25 | 51.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2018-02-19 11:12 | 55.1 | 38.9 | 0 | 6 | -33.2 | 33.2 | 1005 | 14.33 | 111.9 | 646 | 80 | 50.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-02-19 11:11 | 52.9 | 39.8 | 0 | 7.3 | -0.1 | 0.1 | 1005 | 3.86 | 8.4 | 46 | 20 | 39.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-02-19 11:10 | 44 | 35.4 | 0 | 20.6 | -1.6 | 1.6 | 1005 | 1.3 | 21 | 97 | 22 | 39.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2018-02-19 11:08 | 32.2 | 29.8 | 2.4 | 35.6 | -0.3 | 0.3 | 1007 | 11.49 | 1.6 | 5 | 5 | 24.2 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2018-02-19 10:46 | 56.8 | 38.2 | 0 | 5 | -4.9 | 4.9 | 1006 | 31.81 | 50 | 297 | 50 | 28.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2018-02-19 10:45 | 64.2 | 37.4 | 0 | 0 | -53.5 | 53.5 | 1006 | 11.67 | 30.3 | 204 | 99 | 25.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2018-02-19 10:43 | 58.3 | 38 | 0 | 3.7 | -8.8 | 8.8 | 1006 | 29.38 | 48 | 293 | 60 | 30.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-02-19 10:42 | 60.8 | 40.7 | 0 | 0 | -7.6 | 7.6 | 1006 | >>>> | 0 | 0 | 99 | 34.8 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-02-19 10:40 | 52 | 38.9 | 0 | 9.1 | 0 | 0 | 1006 | 0.32 | 4.9 | 26 | 5 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-02-19 10:39 | 52 | 38.5 | 0 | 9.5 | -29.6 | 29.6 | 1006 | 4.95 | 66.4 | 362 | 50 | 41.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-02-19 10:37 | 42.6 | 32.7 | 0.5 | 24.2 | -5.6 | 5.6 | 1007 | 15.28 | 33.8 | 151 | 35 | 34.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-02-19 10:34 | 48.9 | 36.7 | 0 | 14.4 | -19 | 19 | 1007 | 12.78 | 30.8 | 158 | 40 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-02-19 10:32 | 39.3 | 28.5 | 3.9 | 28.3 | -3.6 | 3.6 | 1006 | 5.41 | 20.3 | 83 | 15 | 29.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2018-02-19 10:28 | 0.8 | 1.2 | 20 | 78 | -0.1 | 0.1 | 1006 | -0.01 | 0 | 0 | 0 | 19.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2018-02-19 10:27 | 56.6 | 39.1 | 0 | 4.3 | -0.8 | 0.8 | 1006 | 0.03 | 0.7 | 4 | 10 | 22.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2018-02-19 10:25 | 8.5 | 4.6 | 18.5 | 68.4 | 0 | 0 | 1006 | -0.02 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2018-02-19 10:22 | 43 | 35.8 | 0 | 21.2 | -0.9 | 0.9 | 1005 | 4.48 | 9.1 | 41 | 20 | 29.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-02-19 10:20 | 42.2 | 32.2 | 0.2 | 25.4 | -24.7 | 24.7 | 1006 | 15.03 | 72.1 | 318 | 65 | 30.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2018-02-19 10:16 | 47.4 | 37.7 | 0 | 14.9 | -1.2 | 1.2 | 1006 | 0.76 | 16.2 | 80 | 25 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2018-02-19 10:15 | 51.5 | 38.3 | 0 | 10.2 | -2.9 | 2.9 | 1006 | 1.25 | 21.2 | 114 | 25 | 26.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-02-19 10:14 | 47.3 | 35.3 | 0 | 17.4 | -1.1 | 1.1 | 1006 | 0.79 | 16.8 | 83 | 25 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-02-19 10:10 | 47 | 36.2 | 0 | 16.8 | -1.5 | 1.5 | 1006 | 0.21 | 8.7 | 42 | 25 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2018-02-19 10:09 | 58.1 | 41.1 | 0 | 0.8 | -0.2 | 0.2 | 1005 | 0.09 | 5.8 | 35 | 22 | 30 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2018-02-19 10:06 | 46 | 35.7 | 0 | 18.3 | -0.1 | 0.1 | 1006 | 0.62 | 6.9 | 33 | 15 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-02-19 10:03 | 54.8 | 38.5 | 0 | 6.7 | -4.3 | 4.3 | 1006 | 2.17 | 27.9 | 160 | 40 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-02-19 09:59 | 44.1 | 35.6 | 0 | 20.3 | -2.7 | 2.7 | 1006 | 1.98 | 12.1 | 56 | 18 | 35.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2018-02-19 09:56 | 49.3 | 38.7 | 0 | 12 | -60.5 | 60.5 | 1005 | 9.79 | 55.5 | 286 | 80 | 46.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2018-02-19 09:54 | 54.6 | 38.3 | 0 | 7.1 | 0 | 0 | 1005 | -0.04 | 0 | 0 | 15 | 22.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-01-25 08:51 | 18.7 | 25.2 | 0 | 56.1 | -0.6 | 0.6 | 1001 | 1.33 | 9.8 | 19 | 5 | 29.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-01-25 08:49 | 18.6 | 13.3 | 12.5 | 55.6 | -1.2 | 1.2 | 1001 | 2.6 | 14 | 27 | 10 | 28.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-01-25 08:47 | 53 | 38.1 | 0 | 8.9 | -1.4 | 1.4 | 1000 | 12.93 | 7.9 | 43 | 20 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-01-25 08:44 | 42.6 | 33.3 | 2.2 | 21.9 | -0.5 | 0.5 | 1000 | 3.06 | 15.2 | 67 | 17 | 30.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-01-25 08:41 | 25.3 | 29.4 | 0 | 45.3 | -0.4 | 0.4 | 999 | 2.99 | 14.6 | 38 | 7 | 33.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-01-25 08:38 | 42.1 | 35.6 | 0 | 22.3 | -0.5 | 0.5 | 999 | 13.25 | 15.5 | 68 | 15 | 32.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-01-25 08:35 | 41.2 | 30 | 4.1 | 24.7 | -3.5 | 3.5 | 999 | 5.3 | 42.9 | 185 | 35 | 36.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-01-25 08:33 | 44.2 | 37.5 | 0 | 18.3 | -2.2 | 2.2 | 999 | 11.77 | 28.5 | 132 | 27 | 53.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-01-25 08:30 | 44 | 36.3 | 0 | 19.7 | -2.2 | 2.2 | 1000 | 1.58 | 23.1 | 106 | 25 | 40.4 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-01-25 08:25 | 30.3 | 30.2 | 0.8 | 38.7 | -0.7 | 0.7 | 1000 | 1.25 | 9.4 | 30 | 10 | 35.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-01-25 08:23 | 35.6 | 29.8 | 3.2 | 31.4 | -32.9 | 32.9 | 1000 | 16.28 | 118 | 440 | 60 | 46.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-01-25 08:02 | 61 | 40.6 | 0 | 0 | -50.9 | 50.9 | 1001 | 21.01 | 141.1 | 902 | 90 | 24.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-01-24 11:45 | 62.1 | 46 | 0 | 0 | -71 | 71 | 1002 | 5.43 | 42.3 | 275 | 99 | 32.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-01-24 11:44 | 57.7 | 50.1 | 0 | 0 | -15.8 | 15.8 | 1003 | 9.56 | 56 | 338 | 60 | 38.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-01-24 11:37 | 41.6 | 32.1 | 1.1 | 25.2 | -0.7 | 0.7 | 1003 | 7.64 | 11.7 | 51 | 17 | 40.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-01-24 11:35 | 54.4 | 40.2 | 0 | 5.4 | -19.5 | 19.5 | 1003 | 12.92 | 30.9 | 176 | 42 | 35.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2018-01-24 11:33 | 59 | 40.9 | 0 | 0.1 | -50.7 | 50.7 | 1003 | 0.42 | 12 | 74 | 80 | 35.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-01-24 11:31 | 59.3 | 38.1 | 0 | 2.6 | -0.7 | 0.7 | 1003 | 1.89 | 12.2 | 75 | 25 | 33 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-01-24 11:27 | 59.6 | 39.9 | 0 | 0.5 | -50.8 | 50.8 | 1003 | 0.38 | 11.5 | 72 | 70 | 30.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-01-24 11:25 | 59 | 39.6 | 0 | 1.4 | -38.5 | 38.5 | 1003 | 0.58 | 14.3 | 88 | 25 | 29.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-01-24 11:24 | 57 | 37.8 | 0 | 5.2 | -12.4 | 12.4 | 1003 | 1.2 | 20.6 | 122 | 45 | 36.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-01-24 11:20 | 40.3 | 32.5 | 0 | 27.2 | -15.3 | 15.3 | 1004 | 0.61 | 6.7 | 28 | 15 | 34.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-01-24 11:18 | 31.2 | 22.2 | 6.5 | 40.1 | -24.2 | 24.2 | 1004 | 0.59 | 6.6 | 21 | 15 | 30.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-01-24 11:16 | 42 | 32.6 | 0 | 25.4 | -51.2 | 51.2 | 1004 | 0.23 | 8.7 | 38 | 38 | 34.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-01-24 11:11 | 0.3 | 0.1 | 20.6 | 79 | -54 | 54 | 532 | 0.09 | 8.8 | 0 | 40 | 25.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-01-24 11:07 | 60.8 | 39.5 | 0 | 0 | -54.5 | 54.5 | 1002 | 0.47 | 5.9 | 37 | 20 | 26.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-01-24 11:01 | 52.1 | 38.1 | 0 | 9.8 | -7.5 | 7.5 | 1002 | 1.9 | 25.9 | 141 | 20 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-01-24 11:00 | 45 | 35.4 | 0 | 19.6 | -2.7 | 2.7 | 1002 | 1.11 | 9.2 | 43 | 12 | 27.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-01-24 10:58 | 60.9 | 39.7 | 0 | 0 | -11.9 | 11.9 | 1002 | 16.82 | 78.1 | 498 | 80 | 31.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-01-24 10:57 | 45 | 35.8 | 0 | 19.2 | -3.3 | 3.3 | 1002 | 22.77 | 40.8 | 192 | 50 | 39.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-01-24 10:55 | 52.4 | 36.1 | 0 | 11.5 | -20.9 | 20.9 | 1002 | 0.92 | 17.8 | 97 | 25 | 39 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-01-24 10:54 | 43.4 | 31.1 | 3.3 | 22.2 | -53.1 | 53.1 | 1000 | -0.1 | 0 | 0 | 80 | 28 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-01-24 10:47 | 59.6 | 41.4 | 0 | 0 | -48.9 | 48.9 | 1000 | 0.49 | 12.9 | 80 | 15 | 35.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2018-01-24 10:07 | 55.4 | 41.7 | 0 | 2.9 | -18.1 | 18.1 | 1002 | 0.02 | 1.3 | 7 | 10 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-01-24 10:03 | 57.9 | 39.2 | 0 | 2.9 | -5.5 | 5.5 | 1002 | 9.38 | 57.7 | 350 | 55 | 37.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-01-24 10:01 | 60.3 | 40.8 | 0 | 0 | -2.2 | 2.2 | 1002 | 10.57 | 28.2 | 178 | 45 | 42.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-01-24 09:59 | 61.2 | 41 | 0 | 0 | -41.6 | 41.6 | 1002 | 5.41 | 19.8 | 127 | 60 | 43 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-01-24 09:57 | 18.4 | 39.6 | 0 | 42 | -34.1 | 34.1 | 999 | 3.46 | 14.6 | 28 | 10 | 41.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-01-24 09:11 | 56 | 40.4 | 0 | 3.6 | -2.8 | 2.8 | 1001 | 1.34 | 21.7 | 127 | 27 | 35.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-01-24 09:09 | 47.7 | 36.7 | 0.2 | 15.4 | -0.8 | 0.8 | 1001 | 10.01 | 13.6 | 68 | 18 | 34.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-01-24 09:02 | 53.4 | 38.9 | 0 | 7.7 | -2.3 | 2.3 | 1000 | 0.86 | 17.7 | 99 | 25 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-01-24 08:55 | 42.6 | 33 | 3.3 | 21.1 | -26.3 | 26.3 | 1000 | 13.1 | 65 | 290 | 40 | 49.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-01-24 08:53 | 60.4 | 42.3 | 0 | 0 | -47 | 47 | 1000 | 0.04 | 3.7 | 23 | 60 | 40.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-01-24 08:51 | 45.9 | 38.3 | 0 | 15.8 | -2.4 | 2.4 | 1000 | 4.21 | 17.5 | 84 | 22 | 36.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-01-24 08:49 | 59.7 | 44 | 0 | 0 | -50.3 | 50.3 | 1000 | 2.98 | 31.2 | 195 | 99 | 42.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-01-24 08:47 | 46.4 | 36.6 | 0 | 17 | -6.4 | 6.4 | 999 | 13.54 | 31.5 | 153 | 38 | 38.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-01-24 08:44 | 36.4 | 28 | 5.7 | 29.9 | -53.6 | 53.6 | 999 | 0 | 0.2 | 0 | 50 | 23 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2018-01-12 13:12 | 40.6 | 31.8 | 0 | 27.6 | -39.1 | 39.1 | 997 | 0.26 | 4.3 | 18 | 40 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2018-01-12 13:10 | 32.7 | 25.1 | 3.8 | 38.4 | -39.4 | 39.4 | 997 | -0.01 | 0 | 0 | 40 | 25.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2018-01-12 13:10 | 0.5 | 1.4 | 16.9 | 81.2 | -0.4 | 0.4 | 997 | 0 | 0 | 0 | 0 | 25 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2018-01-12 13:08 | 40.8 | 31.6 | 0 | 27.6 | -35.5 | 35.5 | 997 | 4.12 | 4.4 | 18 | 50 | 24.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2018-01-12 13:07 | 35.8 | 29.3 | 0 | 34.9 | -38.2 | 38.2 | 997 | 0.95 | 2.1 | 7 | 50 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2018-01-12 13:06 | 33.1 | 29.5 | 0 | 37.4 | -15 | 15 | 997 | 0.03 | 1.4 | 5 | 10 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2018-01-12 13:05 | 0.8 | 0.8 | 18 | 80.4 | -0.1 | 0.1 | 997 | -0.26 | 0 | 0 | 0 | 24.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2018-01-12 13:03 | 56.8 | 39.2 | 0 | 4 | -39.4 | 39.4 | 997 | -0.07 | 0 | 0 | 99 | 26 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2018-01-12 13:02 | 25.9 | 24 | 3.3 | 46.8 | 0 | 0 | 997 | 0.08 | 2.4 | 6 | 5 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2018-01-12 13:01 | 54.2 | 38 | 0 | 5.8 | -8.9 | 8.9 | 997 | 0.94 | 2.1 | 12 | 10 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2018-01-12 13:00 | 50.7 | 34.7 | 0 | 14.6 | -15.4 | 15.4 | 996 | 0.26 | 4.5 | 23 | 10 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2018-01-12 12:15 | 53.9 | 36.4 | 0 | 5.7 | -7.3 | 7.3 | 993 | 1.16 | 2.4 | 14 | 5 | 27.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2018-01-12 12:14 | 53.1 | 33.6 | 0 | 13.3 | -13.7 | 13.7 | 993 | 0.36 | 5.2 | 29 | 10 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2018-01-12 12:12 | 50.6 | 35 | 0 | 14.4 | -26.8 | 26.8 | 993 | -0.09 | 0 | 0 | 5 | 32 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2018-01-12 12:11 | 0 | 0.2 | 20.7 | 79.1 | 0 | 0 | 993 | 0 | 0 | 0 | 0 | 31.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2018-01-12 12:09 | 41.8 | 31.7 | 0 | 26.5 | -16.3 | 16.3 | 993 | 3.43 | 16 | 70 | 25 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2018-01-12 12:08 | 23.7 | 17.3 | 9.7 | 49.3 | -37.6 | 37.6 | 993 | 0.05 | 0.5 | 1 | 20 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2018-01-12 12:06 | 1.9 | 1.5 | 20.6 | 76 | -4.7 | 4.7 | 993 | 0 | 0 | 0 | 0 | 31.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2018-01-12 12:05 | 47.1 | 45.9 | 0 | 7 | 0 | 0 | 993 | -0.02 | 0 | 0 | 5 | 29.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2018-01-12 12:04 | 2.6 | 2.1 | 20 | 75.3 | 0 | 0 | 993 | -0.02 | 0 | 0 | 0 | 31.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2018-01-12 12:03 | 53.5 | 35.1 | 0 | 11.4 | -37.1 | 37.1 | 993 | 0.32 | 4.4 | 25 | 99 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2018-01-12 12:02 | 48.4 | 32.3 | 2.5 | 16.8 | -37.9 | 37.9 | 993 | -0.1 | 0 | 0 | 40 | 31.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2018-01-12 12:00 | 50.5 | 49.9 | 0 | 0 | -37.9 | 37.9 | 993 | -0.16 | 0 | 0 | 25 | 28.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2018-01-12 11:59 | 54.6 | 35.4 | 0 | 10 | -22.9 | 22.9 | 993 | 0.63 | 6.3 | 36 | 20 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2018-01-12 11:58 | 56.2 | 36.8 | 0 | 7 | -0.5 | 0.5 | 993 | 0.28 | 4.7 | 27 | 10 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2018-01-12 11:30 | 58.5 | 41.3 | 0 | 0.2 | 0 | 0 | 992 | 0.63 | 6.9 | 42 | 17 | 35.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2018-01-12 11:28 | 40.3 | 31 | 2.6 | 26.1 | -33.5 | 33.5 | 992 | 14.83 | 113.5 | 480 | 70 | 45.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2018-01-12 11:26 | 60.4 | 47.9 | 0 | 0 | -43.4 | 43.4 | 992 | 9.35 | 55.9 | 354 | 80 | 32 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2018-01-12 11:24 | 56.1 | 54 | 0 | >>>> | -5.3 | 5.3 | 992 | 1.46 | 22 | 129 | 30 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2018-01-12 11:23 | 62.6 | 51.1 | 0 | >>>> | -7 | 7 | 992 | 4.43 | 39.1 | 256 | 50 | 30.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2018-01-12 11:21 | 54.9 | 53.2 | 0 | 0 | -3.3 | 3.3 | 992 | 4.08 | 36.8 | 212 | 40 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2018-01-12 11:20 | 51.8 | 54.9 | 0 | 0 | -13.6 | 13.6 | 992 | 0.32 | 10.1 | 55 | 10 | 29.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2018-01-12 11:17 | 60.9 | 39.2 | 0 | 0 | -4.7 | 4.7 | 992 | 31.66 | 50.1 | 320 | 50 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2018-01-12 11:16 | 64 | 37.3 | 0 | 0 | -60.5 | 60.5 | 992 | 17.94 | 37.1 | 249 | 99 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2018-01-12 11:14 | 60.1 | 38.1 | 0 | 1.8 | -7.8 | 7.8 | 992 | 28.84 | 47.5 | 299 | 50 | 33.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2018-01-12 11:13 | 60.9 | 40.5 | 0 | 0 | -6.1 | 6.1 | 993 | >>>> | 0 | 0 | 99 | 35.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2018-01-12 11:05 | 60.1 | 40.3 | 0 | 0 | 0.1 | -0.1 | 993 | 0.06 | 2.1 | 13 | 18 | 31.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2018-01-12 11:04 | 55.6 | 38.2 | 0 | 6.2 | -15.1 | 15.1 | 993 | 7.97 | 52.9 | 308 | 50 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2018-01-12 11:03 | 49.2 | 36.4 | 0.1 | 14.3 | -1.3 | 1.3 | 993 | 1.34 | 21.4 | 110 | 40 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2018-01-12 11:01 | 50.4 | 36.4 | 0 | 13.2 | -3.7 | 3.7 | 993 | 1.91 | 25.9 | 136 |  | 36.5
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2018-01-12 11:00 | 55.7 | 37.6 | 0 | 6.7 | -44.8 | 44.8 | 993 | 2.1 | 26.9 | 157 | 40 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2018-01-12 10:59 | 60.2 | 40.3 | 0 | 0 | 0.2 | -0.2 | 993 | 0.34 | 5.1 | 32 | 20 | 28.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2018-01-12 10:57 | 53.6 | 38.4 | 0 | 8 | -0.1 | 0.1 | 993 | 12.22 | 7.7 | 43 | 25 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2018-01-12 10:56 | 56 | 38.6 | 0 | 5.4 | 0 | 0 | 993 | 1.7 | 5.7 | 33 |  | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2018-01-12 10:55 | 59 | 39.5 | 0 | 1.5 | 0 | 0 | 993 | 6.73 | 5.7 | 35 | 25 | 32 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2018-01-12 10:50 | 47.2 | 36.5 | 0.1 | 16.2 | -9.5 | 9.5 | 993 | 7.92 | 51.4 | 254 | 50 | 45.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2018-01-12 10:48 | 60.2 | 41.1 | 0 | 0 | -45.3 | 45.3 | 993 | -0.01 | 0 | 0 | 90 | 33.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2018-01-12 10:46 | 46.9 | 36.3 | 0 | 16.8 | -1.7 | 1.7 | 993 | 7.58 | 5.9 | 29 | 25 | 41.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2018-01-12 10:37 | 58.3 | 42.3 | 0 | 0 | -47.5 | 47.5 | 993 | 1.94 | 41.3 | 252 | 99 | 42.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2018-01-12 10:36 | 16.7 | 22.6 | 8.8 | 51.9 | -0.1 | 0.1 | 993 | 0 | 0 | 0 | 0 | 34.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2018-01-12 10:35 | 58.8 | 43.6 | 0 | 0 | -47.5 | 47.5 | 993 | 1.05 | 8.6 | 53 | 99 | 37.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2018-01-12 10:34 | 59.1 | 42.3 | 0 | 0 | -48.6 | 48.6 | 993 | 0.27 | 4.4 | 27 | 99 | 29.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2018-01-12 10:33 | 56 | 40 | 0 | 4 | -9.8 | 9.8 | 993 | 10.52 | 60.8 | 356 | 60 | 35.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2018-01-12 10:31 | 52.5 | 40 | 0 | 7.5 | -24.7 | 24.7 | 993 | 3.53 | 15.9 | 87 | 25 | 42.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2018-01-12 10:30 | 9.8 | 16 | 9.8 | 64.4 | -4.9 | 4.9 | 993 | 0.01 | 2.1 | 2 | 0 | 38 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2018-01-12 10:29 | 51 | 38.4 | 0 | 10.6 | -22.3 | 22.3 | 994 | 5.81 | 43.9 | 234 | 50 | 45.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2018-01-12 10:28 | 54.6 | 39.4 | 0 | 6 | -48.1 | 48.1 | 994 | 2.1 | 43 | 246 | 99 | 41.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2018-01-12 10:27 | 58.2 | 43.8 | 0 | 0 | 0.1 | -0.1 | 994 | 0.14 | 3.1 | 19 | 45 | 42.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2018-01-12 10:23 | 56.9 | 39.5 | 0 | 3.6 | -61.8 | 61.8 | 994 | 1.33 | 21.2 | 127 | 99 | 31.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2018-01-12 10:21 | 56.7 | 39.2 | 0 | 4.1 | -22.8 | 22.8 | 994 | 3.95 | 17.4 | 103 | 60 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2018-01-12 10:20 | 55.3 | 37.8 | 0.6 | 6.3 | -61 | 61 | 994 | 1.9 | 11.8 | 68 | 99 | 26.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2018-01-12 10:18 | 57.5 | 37.6 | 0 | 4.9 | -10.5 | 10.5 | 994 | 7.18 | 23.7 | 143 | 40 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2018-01-12 10:17 | 48.5 | 38 | 0 | 13.5 | -5.5 | 5.5 | 994 | 5.67 | 20.4 | 103 | 40 | 39.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-01-12 10:16 | 60.3 | 41.2 | 0 | 0 | -13.5 | 13.5 | 994 | 3.11 | 15.6 | 98 | 28 | 26.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-01-12 10:14 | 50.3 | 37.6 | 0.4 | 11.7 | -2.8 | 2.8 | 994 | 1.16 | 9.4 | 49 | 20 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-01-12 10:13 | 60.9 | 40.4 | 0 | 0 | -15.4 | 15.4 | 994 | 9.95 | 59.9 | 382 | 70 | 31.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-01-12 10:11 | 40 | 34 | 0 | 26 | -3.8 | 3.8 | 995 | 25.22 | 42.8 | 179 | 47 | 39.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-01-12 08:56 | 48.9 | 32.2 | 0 | 18.9 | -4.1 | 4.1 | 995 | 26.16 | 44.6 | 229 | 50 | 39 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-01-12 08:55 | 61.1 | 36.3 | 0 | 2.6 | -11.6 | 11.6 | 995 | 1.24 | 21.4 | 137 | 25 | 31.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2018-01-12 08:27 | 44.3 | 31.1 | 0 | 24.6 | -13.5 | 13.5 | 995 | 3.22 | 15.8 | 73 | 30 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2018-01-12 08:26 | 35.8 | 28.5 | 0.8 | 34.9 | -2.7 | 2.7 | 995 | 1.17 | 9.4 | 35 | 15 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2018-01-12 08:25 | 44.8 | 32.7 | 0 | 22.5 | -12.5 | 12.5 | 995 | 9.3 | 57.2 | 268 | 50 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2018-01-12 08:24 | 27.7 | 27.9 | 0 | 44.4 | -6.6 | 6.6 | 996 | 31.64 | 47.4 | 137 | 50 | 39.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2018-01-12 08:22 | 36.2 | 33.2 | 0 | 30.6 | -9 | 9 | 996 | 1.71 | 24.1 | 91 | 25 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2018-01-12 08:20 | 37.9 | 32.3 | 0 | 29.8 | -24.4 | 24.4 | 996 | 1.39 | 21.3 | 84 | 25 | 39.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2018-01-12 08:19 | 41.3 | 35.6 | 0 | 23.1 | -5.9 | 5.9 | 996 | 4.3 | 38.3 | 166 | 40 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2018-01-12 08:18 | 30.3 | 27 | 7.4 | 35.3 | -50.9 | 50.9 | 996 | 0.04 | 3.6 | 11 | 80 | 27.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2018-01-12 08:16 | 49 | 40.6 | 0.1 | 10.3 | -0.5 | 0.5 | 996 | 0.49 | 13.1 | 67 | 20 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2018-01-12 08:15 | 52.9 | 43.7 | 0 | 3.4 | -50.1 | 50.1 | 996 | 1.18 | 32.2 | 178 | 99 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2018-01-11 12:18 | 56 | 38.2 | 0 | 5.8 | -0.4 | 0.4 | 1002 | 0.57 | 14.3 | 84 | 30 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2018-01-11 12:17 | 54.3 | 37.2 | 0 | 8.5 | -1.9 | 1.9 | 1002 | 0.7 | 15.9 | 90 | 30 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2018-01-11 12:16 | 42.4 | 33.8 | 0 | 23.8 | -0.4 | 0.4 | 1002 | 0.55 | 13.8 | 61 | 20 | 34.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2018-01-11 12:15 | 5.9 | 4.3 | 16.3 | 73.5 | -0.8 | 0.8 | 1002 | -4.77 | 0 | 0 | 0 | 36.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2018-01-11 12:14 | 37.9 | 31.6 | 0 | 30.5 | -1 | 1 | 1002 | 0.12 | 6.4 | 25 | 8 | 37.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2018-01-11 12:13 | 50.8 | 36.3 | 0.3 | 12.6 | -0.8 | 0.8 | 1002 | 1.15 | 19.8 | 105 | 40 | 46.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2018-01-11 12:12 | 50.7 | 37.2 | 0 | 12.1 | -14.5 | 14.5 | 1002 | 9.44 | 56.7 | 301 | 80 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2018-01-11 12:11 | 52.1 | 38.1 | 0 | 9.8 | -0.1 | 0.1 | 1002 | 0.12 | 6.5 | 35 | 15 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2018-01-11 12:10 | 53.8 | 38.2 | 0 | 8 | -0.6 | 0.6 | 1002 | 2.43 | 13.7 | 77 | 25 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2018-01-11 12:06 | 42.6 | 35.1 | 0.5 | 21.8 | -0.9 | 0.9 | 1002 | 2.75 | 14.1 | 63 | 22 | 38.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2018-01-11 12:04 | 50 | 36.9 | 0 | 13.1 | -1.9 | 1.9 | 1002 | 1.88 | 12 | 63 | 25 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2018-01-11 12:03 | 45.4 | 33.7 | 2.8 | 18.1 | -0.4 | 0.4 | 1002 | 3.27 | 15.8 | 75 | 18 | 31.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2018-01-11 12:01 | 59.6 | 41.2 | 0 | 0 | 0.1 | -0.1 | 1002 | 0.62 | 6.9 | 43 | 25 | 31.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2018-01-11 11:59 | 59.7 | 40.1 | 0 | 0.2 | -8.3 | 8.3 | 1002 | 0.43 | 5.7 | 36 | 22 | 30.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2018-01-11 11:58 | 57 | 38.7 | 0 | 4.3 | -3.4 | 3.4 | 1002 | 1.57 | 38.8 | 232 | 40 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2018-01-11 11:57 | 54.3 | 38.6 | 0 | 7.1 | -2.7 | 2.7 | 1002 | 9.71 | 13.5 | 77 | 25 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2018-01-11 11:55 | 55.3 | 38.5 | 0 | 6.2 | -4 | 4 | 1002 | 6.38 | 22 | 128 | 40 | 35.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2018-01-11 11:48 | 44.4 | 27.1 | 9.5 | 19 | -4.9 | 4.9 | 1002 | -0.03 | 0 | 0 | 0 | 38.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2018-01-11 11:47 | 57.3 | 41.1 | 0 | 1.6 | -53.1 | 53.1 | 1001 | 1.28 | 33.7 | 202 | 99 | 39.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2018-01-11 11:46 | 50.3 | 37.7 | 0 | 12 | -0.7 | 0.7 | 1001 | 8.94 | 25.8 | 135 | 25 | 39.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2018-01-11 11:45 | 44.1 | 35.6 | 0 | 20.3 | -0.4 | 0.4 | 1001 | 11.98 | 14.8 | 68 | 20 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2018-01-11 11:44 | 53.5 | 40.3 | 0 | 6.2 | -2.1 | 2.1 | 1001 | 14.91 | 8.3 | 47 | 15 | 38.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2018-01-11 11:42 | 51.4 | 40.1 | 0 | 8.5 | -39.9 | 39.9 | 1001 | 6.6 | 21.2 | 114 | 60 | 51.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2018-01-11 11:41 | 52.2 | 39.4 | 0 | 8.4 | -8.8 | 8.8 | 1002 | 0.55 | 13.7 | 75 | 20 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2018-01-11 11:40 | 55.4 | 40 | 0 | 4.6 | -16.9 | 16.9 | 1002 | 14.97 | 32.8 | 190 | 50 | 48.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2018-01-11 11:39 | 53.4 | 39.2 | 1.6 | 5.8 | -32.8 | 32.8 | 1002 | 6.64 | 5.5 | 31 | 25 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2018-01-11 11:38 | 2.5 | 2.7 | 19.2 | 75.6 | -0.7 | 0.7 | 1001 | -0.02 | 0 | 0 | 0 | 34.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2018-01-11 10:57 | 46.8 | 33.2 | 1.7 | 18.3 | -4.6 | 4.6 | 1004 | 14.56 | 33.2 | 162 | 40 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2018-01-11 10:56 | 52.6 | 37.1 | 0 | 10.3 | -17.3 | 17.3 | 1004 | 11.97 | 30 | 165 | 40 | 34.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2018-01-11 10:54 | 48.3 | 32.7 | 2.5 | 16.5 | -3.5 | 3.5 | 1002 | 4.73 | 19.1 | 96 | 20 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2018-01-11 10:51 | 56.6 | 39.8 | 0.3 | 3.3 | -1.1 | 1.1 | 1002 | 0.03 | 5.3 | 31 | 5 | 32.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2018-01-11 10:50 | 45.8 | 35.5 | 0.7 | 18 | -2.7 | 2.7 | 1002 | 6.34 | 21.6 | 104 | 40 | 38.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2018-01-11 10:49 | 22.5 | 27.5 | 0 | 50 | -0.8 | 0.8 | 1002 | 1.17 | 2.2 | 5 | 5 | 39.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2018-01-11 10:48 | 49.2 | 37.8 | 0 | 13 | -39.6 | 39.6 | 1002 | 18.03 | 124.9 | 644 | 99 | 45.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2018-01-11 10:47 | 53.1 | 38.7 | 0 | 8.2 | -12.7 | 12.7 | 1002 | 9.21 | 56.3 | 313 | 50 | 38.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2018-01-11 10:45 | 56.9 | 40.6 | 0 | 2.5 | -32.8 | 32.8 | 1002 | 17.01 | 35.6 | 212 | 99 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2018-01-11 10:44 | 44.7 | 36.6 | 0 | 18.7 | 0 | 0 | 1002 | 0.14 | 7 | 33 | 5 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2018-01-11 10:43 | 40.7 | 28.5 | 5.6 | 25.2 | -4.2 | 4.2 | 1002 | 7.05 | 49.5 | 211 | 45 | 36.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2018-01-11 10:41 | 49.9 | 38 | 0 | 12.1 | -19.4 | 19.4 | 1002 | 1.62 | 38 | 198 | 50 | 43.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-01-11 10:40 | 24.8 | 24.6 | 4.2 | 46.4 | -0.4 | 0.4 | 1002 | 1.48 | 0.5 | 1 | 2 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2018-01-11 10:39 | 24.8 | 24.6 | 4.2 | 46.4 | -0.4 | 0.4 | 1002 | 1.48 | 0.5 | 1 | 2 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2018-01-11 10:38 | 44.7 | 35.3 | 1.2 | 18.8 | -1.2 | 1.2 | 1002 | 0.37 | 5.2 | 24 | 5 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2018-01-11 10:37 | 44.8 | 37.3 | 0 | 17.9 | -0.5 | 0.5 | 1002 | 1.92 | 11.7 | 55 | 20 | 41.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2018-01-11 10:36 | 52.6 | 41.2 | 0 | 6.2 | -39.1 | 39.1 | 1002 | 14.05 | 7.8 | 43 | 99 | 42.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2018-01-11 10:34 | 43.1 | 37 | 0 | 19.9 | -2 | 2 | 1002 | 10.67 | 27.2 | 122 | 25 | 53.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2018-01-11 10:33 | 53.6 | 39.5 | 0 | 6.9 | -25.5 | 25.5 | 1002 | 16.67 | 120.5 | 677 | 70 | 50.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2018-01-11 10:32 | 50.1 | 40.1 | 0 | 9.8 | -0.4 | 0.4 | 1002 | 3.65 | 8.1 | 42 | 10 | 40.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2018-01-11 10:31 | 42.8 | 37 | 0 | 20.2 | -2 | 2 | 1002 | 1.35 | 21.3 | 95 | 25 | 39.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2018-01-11 10:30 | 39.4 | 36.2 | 1.2 | 23.2 | -0.2 | 0.2 | 1002 | 10.78 | 1.5 | 6 | 5 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2018-01-11 10:17 | 52.4 | 40.5 | 0 | 7.1 | -1.5 | 1.5 | 1003 | 7.47 | 23.7 | 130 | 40 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2018-01-11 10:15 | 0.7 | 1.6 | 18.8 | 78.9 | -0.4 | 0.4 | 1003 | -0.01 | 0 | 0 | 0 | 31 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2018-01-11 10:14 | 54.7 | 41.3 | 0.4 | 3.6 | -0.4 | 0.4 | 1003 | 0.05 | 0.9 | 5 | 5 | 29 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2018-01-11 10:12 | 0.8 | 0.5 | 19.6 | 79.1 | 0 | 0 | 1003 | 0.03 | 1.5 | 0 | 0 | 31.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2018-01-11 10:11 | 55.5 | 43.4 | 0 | 1.1 | -7.5 | 7.5 | 1003 | 0.47 | 5.9 | 34 | 15 | 32.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2018-01-11 10:09 | 47 | 39.3 | 0 | 13.7 | -0.4 | 0.4 | 1003 | 4.33 | 8.9 | 43 | 25 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2018-01-11 10:08 | 48.4 | 37.6 | 0.2 | 13.8 | -24.9 | 24.9 | 1003 | 14.26 | 70 | 355 | 70 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2018-01-11 10:07 | 43.2 | 36.9 | 0 | 19.9 | -2.9 | 2.9 | 1003 | 0.5 | 13.2 | 60 | 30 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2018-01-11 10:05 | 48.6 | 40.1 | 0 | 11.3 | -0.7 | 0.7 | 1003 | 0.57 | 13.9 | 71 | 25 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2018-01-11 10:03 | 49 | 38.2 | 0 | 12.8 | -1.9 | 1.9 | 1003 | 0.6 | 14.5 | 74 | 25 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2018-01-11 10:02 | 46.6 | 37.3 | 0.6 | 15.5 | -0.8 | 0.8 | 1003 | 0.67 | 15.4 | 75 | 25 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2018-01-11 10:00 | 41.8 | 35.1 | 0.5 | 22.6 | -2.2 | 2.2 | 1003 | 1.3 | 21.2 | 93 | 22 | 30.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2018-01-11 09:58 | 49.3 | 40.2 | 0 | 10.5 | -0.1 | 0.1 | 1003 | 0.3 | 10.1 | 52 | 25 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2018-01-11 09:57 | 31.1 | 32.8 | 0 | 36.1 | -0.9 | 0.9 | 1003 | 1.27 | 9.6 | 31 | 12 | 31.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2018-01-11 09:55 | 38.1 | 33.7 | 1.2 | 27 | -0.6 | 0.6 | 1004 | 1.59 | 10.9 | 43 | 15 | 28.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2018-01-11 09:49 | 49.8 | 39.2 | 0 | 11 | -3.2 | 3.2 | 1004 | 2.01 | 26.5 | 138 | 40 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2018-01-11 09:48 | 47.6 | 40.3 | 0 | 12.1 | -2.5 | 2.5 | 1004 | 1.07 | 19.1 | 95 | 30 | 33.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2018-01-11 09:46 | 48.1 | 40.1 | 0 | 11.8 | 0 | 0 | 1004 | 0.03 | 0.7 | 3 | 20 | 29.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2018-01-11 09:44 | 45.5 | 40.9 | 0.1 | 13.5 | -2 | 2 | 1004 | 1.39 | 10 | 47 | 20 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2018-01-11 09:43 | 48.4 | 44 | 0.6 | 7 | -57.6 | 57.6 | 1004 | 10.35 | 56.2 | 285 | 70 | 46.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2018-01-10 14:58 | 63.3 | 42.3 | 0 | 0 | -16.1 | 16.1 | 1008 | 20.12 | 85.2 | 565 | 99 | 30.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2018-01-10 14:57 | 62.1 | 42.4 | 0 | 0 | -30.8 | 30.8 | 1008 | 0.16 | 3.5 | 22 | 99 | 30.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2018-01-10 14:56 | 61.9 | 42.1 | 0 | 0 | -13.5 | 13.5 | 1008 | 24.36 | 93.7 | 608 | 99 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2018-01-10 14:55 | 62.1 | 42.9 | 0 | 0 | -7.5 | 7.5 | 1008 | 24.44 | 93.9 | 611 | 99 | 30.8 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2018-01-10 14:51 | 56.3 | 38.2 | 0 | 5.5 | -2.4 | 2.4 | 1008 | 2.77 | 14.7 | 86 | 25 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2018-01-10 14:50 | 50.6 | 36.1 | 0 | 13.3 | -0.4 | 0.4 | 1008 | 2.57 | 14.1 | 74 | 25 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2018-01-10 14:48 | 55 | 37.6 | 0.1 | 7.3 | -0.8 | 0.8 | 1008 | 3.21 | 15.8 | 91 | 25 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2018-01-10 14:46 | 57.5 | 38.4 | 0 | 4.1 | -0.9 | 0.9 | 1008 | 3.96 | 17.6 | 106 | 25 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2018-01-10 14:44 | 47.8 | 34.8 | 1.3 | 16.1 | 0 | 0 | 1008 | 0.58 | 6.6 | 33 | 15 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2018-01-10 14:42 | 49.6 | 35.1 | 0.9 | 14.4 | -0.1 | 0.1 | 1008 | 1.9 | 12.1 | 63 | 20 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2018-01-10 14:40 | 51.9 | 36.6 | 0 | 11.5 | -1 | 1 | 1007 | 4.38 | 18.5 | 100 | 25 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-01-10 14:34 | 61.7 | 41.1 | 0 | 0 | -6.7 | 6.7 | 1007 | 16.01 | 35.3 | 228 | 40 | 32.7 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2018-01-10 14:29 | 59.3 | 40 | 0 | 0.7 | 0.1 | -0.1 | 1007 | 2.96 | 7.5 | 46 | 20 | 35.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2018-01-10 14:27 | 56.4 | 38 | 0.5 | 5.1 | -4 | 4 | 1007 | 4.76 | 40.9 | 242 | 45 | 39.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2018-01-10 14:26 | 59.5 | 41.5 | 0 | 0 | -17.7 | 17.7 | 1007 | 4.4 | 18.2 | 113 | 45 | 34.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2018-01-10 14:23 | 61 | 40.3 | 0 | 0 | -26 | 26 | 1007 | 3.21 | 33.5 | 214 | 60 | 36.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2018-01-10 14:22 | 58.9 | 39.7 | 0 | 1.4 | -15.7 | 15.7 | 1007 | 23.01 | 41.7 | 257 | 50 | 36.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2018-01-10 14:20 | 44.6 | 34.2 | 0.9 | 20.3 | 0.1 | -0.1 | 1007 | 0.02 | 0.6 | 3 | 2 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2018-01-10 14:18 | 54.7 | 38.7 | 0 | 6.6 | -0.7 | 0.7 | 1007 | 1.9 | 5.9 | 34 | 15 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2018-01-10 14:17 | 60.1 | 39.1 | 0 | 0.8 | -42.5 | 42.5 | 1007 | 9.94 | 96.4 | 607 | 99 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2018-01-10 14:16 | 52.4 | 35.2 | 0.1 | 12.3 | -1.2 | 1.2 | 1007 | 18.02 | 2 | 11 | 5 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2018-01-10 14:15 | 59.8 | 38.6 | 0 | 1.6 | -0.6 | 0.6 | 1007 | 1.6 | 11.2 | 70 | 20 | 32.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2018-01-10 14:13 | 56.1 | 37.9 | 0.1 | 5.9 | -4.3 | 4.3 | 1007 | 3.41 | 34.7 | 204 | 50 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2018-01-10 14:11 | 54.8 | 39.4 | 0 | 5.8 | -0.7 | 0.7 | 1007 | 2.83 | 14.5 | 83 | 30 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2018-01-10 14:10 | 53.5 | 37.7 | 0 | 8.8 | -32.4 | 32.4 | 1007 | 23.25 | 89.2 | 500 | 99 | 37.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2018-01-10 14:02 | 5.7 | 4.7 | 9.4 | 80.2 | 0 | 0 | 1007 | -0.01 | 0 | 0 | 0 | 34.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2018-01-10 14:01 | 57.7 | 41.2 | 0 | 1.1 | -5.6 | 5.6 | 1007 | 3.18 | 15.4 | 93 | 25 | 41.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2018-01-10 14:00 | 57.4 | 43.3 | 0 | 0 | -34.2 | 34.2 | 1007 | 22.05 | 138.3 | 831 | 99 | 47.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2018-01-10 13:59 | 43 | 38.7 | 0.1 | 18.2 | -11.7 | 11.7 | 1007 | >>>> | 0 | 0 | 99 | 36.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2018-01-10 13:56 | 59.1 | 41.8 | 0 | 0 | -2.1 | 2.1 | 1007 | 1.23 | 20.9 | 129 | 25 | 34.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2018-01-10 13:55 | 51.3 | 39.6 | 0 | 9.1 | -2.3 | 2.3 | 1007 | 1.37 | 21.5 | 116 | 25 | 42.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2018-01-10 13:54 | 49.1 | 38 | 0 | 12.9 | -5 | 5 | 1007 | 4.62 | 39.7 | 204 | 40 | 39.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2018-01-10 13:53 | 60.5 | 42.2 | 1.1 | 0 | -0.2 | 0.2 | 1007 | 9.62 | 13.5 | 85 | 28 | 32.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2018-01-10 13:51 | 57.9 | 39.7 | 0 | 2.4 | -6.6 | 6.6 | 1007 | 23.06 | 42.1 | 255 | 50 | 33.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2018-01-10 13:49 | 53.5 | 38.9 | 0 | 7.6 | -17.1 | 17.1 | 1007 | 1.37 | 21.7 | 121 | 20 | 37 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2018-01-10 13:48 | 58.2 | 39.7 | 0 | 2.1 | -1.2 | 1.2 | 1007 | 1.07 | 19.5 | 119 | 28 | 34.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2018-01-10 13:47 | 50 | 36.2 | 1.9 | 11.9 | -0.2 | 0.2 | 1007 | 11.28 | 7.4 | 38 | 15 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2018-01-10 13:46 | 53.8 | 41.8 | 0 | 4.4 | -0.1 | 0.1 | 1007 | 4.97 | 4.8 | 27 | 10 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2018-01-10 12:28 | 36.5 | 30.8 | 0 | 32.7 | 0 | 0 | 1008 | 0.03 | 0.7 | 2 | 5 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2018-01-10 12:26 | 0.7 | 0.6 | 20.3 | 78.4 | -48.4 | 48.4 | 1008 | -0.06 | 0 | 0 | 2 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2018-01-10 12:24 | 0.3 | 0.1 | 20.7 | 78.9 | -48.8 | 48.8 | 1008 | 0.03 | 1.4 | 0 | 0 | 27.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2018-01-10 12:22 | 51 | 36.7 | 0 | 12.3 | -3.4 | 3.4 | 1008 | 7.6 | 12 | 64 | 25 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2018-01-10 12:20 | 50.1 | 37.2 | 0 | 12.7 | -4.6 | 4.6 | 1009 | 7.95 | 24.8 | 130 | 40 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2018-01-10 12:17 | 61.1 | 40 | 0 | 0 | -49.2 | 49.2 | 1009 | 0.31 | 4.8 | 30 | 20 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2018-01-10 12:15 | 0.5 | 0.2 | 20.7 | 78.6 | -47.8 | 47.8 | 1008 | -0.06 | 0 | 0 | 0 | 27.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2018-01-10 12:12 | 61.2 | 39.7 | 0 | 0 | -3 | 3 | 1008 | 27.35 | 23.1 | 148 | 40 | 29 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2018-01-10 12:10 | 37.3 | 33.4 | 0 | 29.3 | -0.3 | 0.3 | 1009 | 0.29 | 4.6 | 18 | 15 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2018-01-10 12:07 | 1.4 | 1.1 | 20.4 | 77.1 | -48.9 | 48.9 | 1009 | -0.08 | 0 | 0 | 0 | 29.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-01-10 12:05 | 0.3 | 0 | 20.8 | 78.9 | -49.2 | 49.2 | 1009 | 0.05 | 7 | 0 | 5 | 25.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2018-01-10 12:04 | 0.3 | 0 | 20.8 | 78.9 | -49.2 | 49.2 | 1009 | 0.05 | 7 | 0 | 5 | 25.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2018-01-10 12:01 | 57.6 | 37.7 | 0 | 4.7 | -4.5 | 4.5 | 1009 | 29.88 | 24.2 | 146 | 50 | 26.3 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2018-01-10 11:58 | 0.3 | 0 | 20.8 | 78.9 | -48.2 | 48.2 | 1009 | -0.15 | 0 | 0 | 20 | 27.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2018-01-10 11:51 | 60.2 | 40.1 | 0.1 | 0 | -52.2 | 52.2 | 1008 | 10.73 | 100.6 | 634 | 80 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2018-01-10 11:44 | 55.6 | 38.7 | 0 | 5.7 | -1.1 | 1.1 | 1008 | 2.89 | 7.4 | 43 | 15 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2018-01-10 11:43 | 57 | 38 | 0 | 5 | -1.2 | 1.2 | 1008 | 0.59 | 14.8 | 88 | 25 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2018-01-10 11:41 | 58.1 | 40.4 | 0.5 | 1 | -46.7 | 46.7 | 1008 | 0.62 | 6.7 | 41 | 70 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-01-10 11:40 | 29.7 | 20.1 | 11.4 | 38.8 | -48.1 | 48.1 | 1008 | -0.07 | 0 | 0 | 99 | 23.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2018-01-10 11:39 | 29.7 | 20.1 | 11.4 | 38.8 | -48.1 | 48.1 | 1008 | -0.07 | 0 | 0 | 99 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2018-01-10 11:38 | 58.1 | 38 | 0.8 | 3.1 | 0 | 0 | 1008 | 0.11 | 2.9 | 17 | 15 | 33 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2018-01-10 11:36 | 57.3 | 39.4 | 0 | 3.3 | -4.4 | 4.4 | 1008 | 3.24 | 15.8 | 95 | 40 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2018-01-10 11:35 | 57.1 | 39.7 | 0 | 3.2 | -0.5 | 0.5 | 1009 | 3.76 | 8.5 | 50 | 20 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2018-01-10 11:33 | 0.3 | 0.1 | 20.8 | 78.8 | -1.1 | 1.1 | 1008 | 0.03 | 1.4 | 0 | 0 | 23 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2018-01-10 11:32 | 61.8 | 39.1 | 0 | 0 | -48.8 | 48.8 | 1009 | 0.16 | 3.5 | 22 | 99 | 26.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2018-01-10 11:31 | 0.5 | 0.2 | 20.7 | 78.6 | -5.1 | 5.1 | 1009 | 0.04 | 0.8 | 0 | 0 | 26.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2018-01-10 11:30 | 58.9 | 39.8 | 0.1 | 1.2 | -4.4 | 4.4 | 1009 | 2.28 | 13.3 | 82 | 25 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2018-01-10 11:29 | 55.4 | 40.6 | 0 | 4 | -2 | 2 | 1009 | 0.3 | 4.8 | 27 | 25 | 32.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2018-01-10 11:27 | 57.1 | 39.1 | 0 | 3.8 | -0.8 | 0.8 | 1009 | 2.96 | 15.3 | 91 | 27 | 25.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2018-01-10 11:22 | 44.7 | 35.8 | 0 | 19.5 | -1 | 1 | 1009 | 1.12 | 19.4 | 91 | 40 | 40.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2018-01-10 11:20 | 52.5 | 36.3 | 2.1 | 9.1 | -0.5 | 0.5 | 1009 | 0.21 | 4 | 22 | 30 | 28.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2018-01-10 11:18 | 57.6 | 38.3 | 0 | 4.1 | -0.7 | 0.7 | 1009 | 0.39 | 2.7 | 16 | 40 | 26 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2018-01-10 11:16 | 60.8 | 40.1 | 0 | 0 | -0.4 | 0.4 | 1009 | 0.12 | 3 | 19 | 50 | 28.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2018-01-10 11:14 | 57.8 | 39.4 | 0 | 2.8 | -2 | 2 | 1009 | 0.31 | 10.4 | 63 | 99 | 43.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2018-01-10 11:11 | 61.2 | 40.5 | 0 | 0 | -43 | 43 | 1009 | 0.28 | 10 | 64 | 40 | 29.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2018-01-10 11:10 | 51.9 | 35 | 0.5 | 12.6 | -3.6 | 3.6 | 1009 | 2.01 | 12.4 | 67 | 20 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2018-01-10 11:09 | 51.9 | 37.3 | 0 | 10.8 | -15.4 | 15.4 | 1009 | 13.43 | 8.1 | 44 | 20 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2018-01-10 11:08 | 61.3 | 40.8 | 0 | 0 | -40.7 | 40.7 | 1009 | 0.46 | 12.7 | 82 | 25 | 25.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2018-01-10 11:06 | 48.4 | 35.3 | 0 | 16.3 | -14.3 | 14.3 | 1009 | 3.72 | 16.7 | 84 | 40 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2018-01-10 11:05 | 49.4 | 35.7 | 1.4 | 13.5 | -4.7 | 4.7 | 1009 | 0.96 | 29.9 | 155 | 40 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2018-01-10 11:04 | 59.1 | 40.2 | 0 | 0.7 | -0.4 | 0.4 | 1009 | 6.37 | 22.2 | 137 | 20 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2018-01-10 11:03 | 60.9 | 40.9 | 0 | 0 | -42.5 | 42.5 | 1009 | 8.86 | 54.8 | 350 | 99 | 40.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2018-01-10 11:02 | 56.3 | 38.4 | 0 | 5.3 | -17.4 | 17.4 | 1009 | 1.05 | 19.2 | 113 | 40 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2018-01-10 11:00 | 39.4 | 31.6 | 1.9 | 27.1 | -9 | 9 | 1009 | 0.74 | 7.4 | 30 | 10 | 33.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2018-01-10 10:58 | 53.8 | 38.7 | 0 | 7.5 | -0.2 | 0.2 | 1009 | 0.33 | 5 | 28 | 10 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2018-01-10 10:57 | 56.5 | 38.9 | 0 | 4.6 | -3.7 | 3.7 | 1009 | 3.67 | 36.4 | 215 | 40 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2018-01-10 10:56 | 48.3 | 32.9 | 2 | 16.8 | -4 | 4 | 1009 | 0.37 | 2.6 | 13 | 10 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2018-01-10 10:54 | 28 | 28.1 | 0 | 43.9 | 0 | 0 | 1009 | 0.54 | 0.3 | 1 | 5 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2018-01-10 10:53 | 34.8 | 26.2 | 4.4 | 34.6 | -21.5 | 21.5 | 1009 | 1 | 8.6 | 31 | 20 | 28.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2018-01-10 10:50 | 49.6 | 35.1 | 0 | 15.3 | -20.1 | 20.1 | 1009 | 7.47 | 51.4 | 267 | 50 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2018-01-10 10:49 | 55.3 | 34.6 | 0 | 10.1 | -3.1 | 3.1 | 1010 | 2.01 | 6.3 | 36 | 15 | 24.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2018-01-10 10:48 | 64 | 36.5 | 0 | 0 | -6.6 | 6.6 | 1010 | 26.37 | 2.5 | 17 | 50 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2018-01-10 10:47 | 32.4 | 29.8 | 0 | 37.8 | -40.3 | 40.3 | 1010 | 0.39 | 11.3 | 38 | 40 | 33.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2018-01-10 10:09 | 59.6 | 42.1 | 0 | 0 | -0.3 | 0.3 | 1008 | 0.56 | 14.4 | 90 | 50 | 23.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2018-01-10 10:06 | 58.3 | 41.2 | 0 | 0.5 | -28.6 | 28.6 | 1008 | 1.16 | 20.3 | 124 | 25 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2018-01-10 10:06 | 1.1 | 2.5 | 18.5 | 77.9 | 0 | 0 | 1008 | 0.02 | 0.6 | 0 | 0 | 23.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2018-01-10 10:04 | 0.4 | 0.2 | 20.9 | 78.5 | 0.1 | -0.1 | 1008 | 0.02 | 2.8 | 0 | 0 | 23.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2018-01-10 10:03 | 1.5 | 0.8 | 19.5 | 78.2 | 0 | 0 | 1008 | 0 | 0.4 | 0 | 0 | 25.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2018-01-10 09:57 | 45.6 | 37.3 | 0 | 17.1 | -5 | 5 | 1008 | 12.16 | 29.8 | 142 | 40 | 37.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2018-01-10 09:56 | 47 | 35.4 | 3.2 | 14.4 | -41.5 | 41.5 | 1008 | 4.42 | 61.8 | 304 | 80 | 45.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2018-01-10 09:55 | 40.7 | 36.1 | 0 | 23.2 | -1.4 | 1.4 | 1008 | 1.43 | 10.2 | 43 | 20 | 30.9 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2018-01-10 09:53 | 2.8 | 2.5 | 19.1 | 75.6 | 0 | 0 | 1008 | -0.11 | 0 | 0 | 0 | 28.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2018-01-10 09:52 | 49.4 | 38.6 | 0 | 12 | -49.4 | 49.4 | 1008 | 2.05 | 42.7 | 221 | 99 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2018-01-10 09:51 | 31.3 | 32.3 | 0 | 36.4 | -0.7 | 0.7 | 1007 | 11.69 | 28.4 | 93 | 25 | 48 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2018-01-10 09:44 | 17.3 | 11.5 | 15.6 | 55.6 | -54 | 54 | 1007 | 0.05 | 1.8 | 3 | 99 | 22.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2018-01-10 09:42 | 60.5 | 42.5 | 0 | 0 | -53.9 | 53.9 | 1007 | -0.22 | 0 | 0 | 99 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2018-01-10 09:41 | 61.7 | 42.1 | 0 | 0 | -51.8 | 51.8 | 1007 | 2.63 | 48.4 | 313 | 99 | 41.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2018-01-10 09:40 | 22.6 | 15.5 | 14.1 | 47.8 | -53.8 | 53.8 | 1007 | -0.02 | 0 | 0 | 99 | 19.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2018-01-10 09:38 | 12.7 | 22.6 | 0.9 | 63.8 | 0.1 | -0.1 | 1007 | 0.23 | 4 | 5 | 0 | 21.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2018-01-10 09:36 | 48.7 | 38.2 | 0 | 13.1 | -0.9 | 0.9 | 1008 | 16.94 | 8.9 | 45 | 20 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2018-01-10 09:35 | 41.9 | 32.1 | 4.1 | 21.9 | -2.6 | 2.6 | 1007 | 2 | 26.7 | 117 | 20 | 26.1 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2018-01-10 09:33 | 57.3 | 41.7 | 0.7 | 0.3 | -53.4 | 53.4 | 1008 | 0.7 | 15 | 90 | 99 | 45 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2018-01-10 09:32 | 0.5 | 0.4 | 20.9 | 78.2 | -41.3 | 41.3 | 1008 | 0.03 | 1.5 | 0 | 0 | 21 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2018-01-10 09:30 | 47.3 | 35.7 | 3.7 | 13.3 | -53.7 | 53.7 | 1008 | -0.02 | 0 | 0 | 25 | 19.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2018-01-10 09:24 | 56.8 | 41.2 | 0 | 2 | -31.7 | 31.7 | 1008 | 17.57 | 75.8 | 451 | 99 | 49 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2018-01-10 09:23 | 60.3 | 42.4 | 0 | 0 | -38.4 | 38.4 | 1008 | 7.76 | 50.9 | 322 | 99 | 42.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2018-01-10 09:22 | 59.8 | 42.3 | 0 | 0 | -37.3 | 37.3 | 1008 | 10.92 | 98.8 | 619 | 99 | 42 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2018-01-10 09:20 | 40.9 | 32.5 | 2.1 | 24.5 | -3.3 | 3.3 | 1008 | 0 | 0 | 0 | 0 | 29.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2018-01-10 09:19 | 43.2 | 32.7 | 4.8 | 19.3 | -29.4 | 29.4 | 1008 | 12.17 | 62.8 | 284 | 70 | 48.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2018-01-10 09:16 | 61.3 | 43 | 0 | 0 | -38.8 | 38.8 | 1008 | 0.3 | 10.1 | 64 | 40 | 39.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2018-01-10 09:13 | 0.8 | 0.6 | 20.7 | 77.9 | -24 | 24 | 1008 | -0.04 | 0 | 0 | 0 | 23.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2018-01-10 09:12 | 41.5 | 36 | 0.7 | 21.8 | -3.7 | 3.7 | 1008 | 6.44 | 21.7 | 94 | 35 | 35.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2018-01-10 09:10 | 56.3 | 41.3 | 0 | 2.4 | -2.5 | 2.5 | 1008 | 1.49 | 22.7 | 134 | 40 | 38.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2018-01-10 09:08 | 58.4 | 44.2 | 0 | 0 | -37.2 | 37.2 | 1008 | 7.45 | 49.5 | 303 | 80 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2018-01-10 09:07 | 26.2 | 18.7 | 15.4 | 39.7 | -18.8 | 18.8 | 1008 | 0.05 | 3.9 | 10 | 0 | 22.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2018-01-10 09:06 | 15.4 | 10.1 | 15.9 | 58.6 | -0.1 | 0.1 | 1008 | 0.05 | 2 | 3 | 5 | 26.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2018-01-10 09:05 | 60.6 | 44.5 | 0 | 0 | -38.6 | 38.6 | 1008 | -0.03 | 0 | 0 | 20 | 25.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2018-01-10 09:03 | 59.7 | 41.7 | 0 | 0 | -42.4 | 42.4 | 1008 | 7.85 | 83.4 | 522 | 99 | 44 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2018-01-10 09:01 | 51.7 | 39.2 | 0.1 | 9 | -5.4 | 5.4 | 1008 | 9.9 | 27.3 | 148 | 40 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2018-01-10 09:00 | 41.8 | 35.2 | 0.2 | 22.8 | -6.2 | 6.2 | 1008 | 12.06 | 29.7 | 130 | 40 | 36.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2018-01-10 08:58 | 50.2 | 38.7 | 0.3 | 10.8 | -7.3 | 7.3 | 1008 | 2.3 | 28.3 | 149 | 40 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2018-01-10 08:56 | 60.2 | 43.4 | 0 | 0 | -33.8 | 33.8 | 1008 | 0.53 | 13.5 | 85 | 25 | 28.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2018-01-08 14:41 | 60.7 | 42.1 | 0 | 0 | -28.4 | 28.4 | 1003 | 22.92 | 143.4 | 912 | 99 | 45.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2018-01-08 14:40 | 51.5 | 38.2 | 0 | 10.3 | -7.2 | 7.2 | 1003 | 11.78 | 29.4 | 159 | 40 | 41.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2018-01-08 14:38 | 61.7 | 41.7 | 0 | 0 | -25.9 | 25.9 | 1002 | 22.62 | 87.8 | 568 | 99 | 44.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2018-01-08 14:37 | 10.3 | 10 | 16.5 | 63.2 | -0.2 | 0.2 | 1002 | 0.25 | 4.2 | 4 | 0 | 29.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2018-01-08 14:35 | 60.3 | 42.1 | 0 | 0 | -40.4 | 40.4 | 1002 | 6.45 | 46.1 | 291 | 99 | 46.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2018-01-08 14:34 | 58.4 | 44 | 0 | 0 | -19.4 | 19.4 | 1003 | 0.22 | 4 | 24 | 20 | 32.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2018-01-08 14:32 | 59.7 | 43.4 | 0 | 0 | -0.2 | 0.2 | 1003 | 0.22 | 4.1 | 25 | 0 | 33.2 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2018-01-08 14:29 | 60.6 | 43.9 | 0 | 0 | -16.6 | 16.6 | 1003 | 22.96 | 144 | 915 | 80 | 43.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2018-01-08 14:28 | 7.8 | 18.7 | 8.5 | 65 | -41 | 41 | 1004 | 4.11 | 16.4 | 13 | 0 | 38 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2018-01-08 14:15 | 46.7 | 29 | 5 | 19.3 | -0.8 | 0.8 | 1004 | -0.05 | 0 | 0 | 0 | 29.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2018-01-08 14:14 | 54.6 | 37.9 | 0 | 7.5 | -9.5 | 9.5 | 1004 | 15.37 | 34.2 | 195 | 50 | 34.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2018-01-08 14:13 | 58.3 | 39.5 | 0 | 2.2 | -5 | 5 | 1004 | 8.53 | 55.1 | 337 | 50 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2018-01-08 14:11 | 62 | 40.9 | 0 | 0 | -1.6 | 1.6 | 1004 | 8.3 | 25.2 | 163 | 27 | 40.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2018-01-08 14:09 | 62.7 | 41.4 | 0 | 0 | -21.1 | 21.1 | 1004 | 2.09 | 12.5 | 82 | 40 | 40.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2018-01-08 14:08 | 47.9 | 47.8 | 0 | 4.3 | -41.4 | 41.4 | 1004 | 0.02 | 2.3 | 11 | 25 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2018-01-08 14:06 | 29.9 | 47.3 | 0 | 22.8 | -33.6 | 33.6 | 1004 | 5.7 | 18.9 | 59 | 20 | 38.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2018-01-08 14:05 | 62.3 | 39.7 | 0.1 | 0 | -19.9 | 19.9 | 1004 | 2.37 | 13.6 | 89 | 20 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2018-01-08 14:04 | 58.6 | 39 | 0 | 2.4 | -13.9 | 13.9 | 1004 | 19.31 | 38.7 | 237 | 50 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2018-01-08 14:02 | 20.2 | 12.3 | 17.1 | 50.4 | -6.3 | 6.3 | 1004 | 0.01 | 0.4 | 0 | 0 | 26.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2018-01-08 14:01 | 61.7 | 41.8 | 0 | 0 | 0.8 | -0.8 | 1004 | -0.01 | 0 | 0 | 2 | 27.4 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-12-14 14:50 | 63 | 41.6 | 0 | 0 | -17.3 | 17.3 | 1000 | 21.31 | 86.2 | 569 | 99 | 41.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-12-14 14:49 | 61.5 | 42.2 | 0 | 0 | -32.5 | 32.5 | 1000 | 0.41 | 5.5 | 35 | 99 | 33.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-12-14 14:48 | 60.8 | 41.8 | 0 | 0 | -12.1 | 12.1 | 1000 | 25.94 | 95.6 | 610 | 99 | 36.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-12-14 14:47 | 60.5 | 42.2 | 0 | 0 | -6.4 | 6.4 | 1000 | 20.47 | 85 | 539 | 90 | 37.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-12-14 14:43 | 58.5 | 39 | 0.1 | 2.4 | -1.6 | 1.6 | 1000 | 3.54 | 16.6 | 102 | 22 | 32.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-12-14 14:40 | 57.6 | 38.5 | 0 | 3.9 | -0.2 | 0.2 | 1000 | 1.92 | 12.2 | 74 | 20 | 31.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-12-14 14:39 | 59.6 | 39.1 | 0 | 1.3 | -0.6 | 0.6 | 1000 | 2.46 | 13.9 | 87 | 28 | 29.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-12-14 14:36 | 57.1 | 38.3 | 0 | 4.6 | -1.2 | 1.2 | 1000 | 4.34 | 18.5 | 110 | 30 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-12-14 14:34 | 43.3 | 32.8 | 1.9 | 22 | -0.5 | 0.5 | 1000 | 1.92 | 12.1 | 55 | 15 | 30.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-12-14 14:31 | 46.6 | 34.4 | 0.9 | 18.1 | -0.1 | 0.1 | 1000 | 1.99 | 12.3 | 60 | 25 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-12-14 14:29 | 51 | 35.9 | 0 | 13.1 | -1.2 | 1.2 | 1000 | 4.86 | 19.5 | 104 | 25 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-12-14 13:47 | 59.4 | 39.1 | 0 | 1.5 | -5 | 5 | 998 | 31.61 | 50 | 311 | 50 | 29.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-12-14 13:46 | 65.5 | 34.1 | 0 | 0.4 | -80.4 | 80.4 | 998 | 0.11 | 2.9 | 20 | 99 | 30.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-12-14 13:45 | 59.9 | 37.6 | 0 | 2.5 | -9.1 | 9.1 | 998 | 29.85 | 48.6 | 305 | 50 | 30.3 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-12-14 13:44 | 60.2 | 39.9 | 0 | 0 | 0 | 0 | 998 | 27.82 | 46.5 | 293 | 99 | 35.3 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-12-14 13:41 | 37 | 32 | 1.7 | 29.3 | -0.5 | 0.5 | 998 | 0.93 | 8.3 | 32 | 5 | 32.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-12-14 13:37 | 54.3 | 39.6 | 0.5 | 5.6 | -0.8 | 0.8 | 999 | 1.69 | 24.4 | 139 | 50 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-12-14 13:32 | 56.2 | 38.9 | 0 | 4.9 | -0.9 | 0.9 | 999 | 3.58 | 16.4 | 96 | 20 | 39.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-12-14 13:30 | 46.1 | 31.9 | 7.1 | 14.9 | -0.4 | 0.4 | 999 | -0.06 | 0 | 0 | 25 | 29.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-12-14 13:28 | 58.5 | 37.9 | 0 | 3.6 | -0.8 | 0.8 | 1000 | 0.12 | 1.5 | 9 | 20 | 27.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-12-14 13:26 | 59.7 | 39.9 | 0 | 0.4 | -0.2 | 0.2 | 1000 | 0.08 | 2.5 | 15 | 40 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-12-14 13:24 | 54.4 | 38.2 | 0 | 7.4 | -1.2 | 1.2 | 999 | 1 | 18.6 | 106 | 99 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-12-14 13:21 | 43.6 | 35.8 | 0 | 20.6 | -1.4 | 1.4 | 999 | 1.15 | 19.7 | 90 | 20 | 40.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-12-14 13:19 | 51.9 | 37.9 | 0 | 10.2 | -1.8 | 1.8 | 999 | 3.43 | 8.1 | 44 | 10 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-12-14 13:18 | 53 | 37.8 | 0 | 9.2 | -1.7 | 1.7 | 999 | 0.75 | 16.5 | 91 | 20 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-12-14 13:17 | 57.8 | 40.6 | 0.4 | 1.2 | -53.6 | 53.6 | 999 | 0.8 | 7.6 | 46 | 80 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-12-14 13:16 | 5.1 | 3.8 | 18.8 | 72.3 | -55.7 | 55.7 | 999 | -0.08 | 0 | 0 | 99 | 26.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-12-14 13:14 | 51.7 | 34.6 | 2.7 | 11 | 0 | 0 | 999 | 0.16 | 3.5 | 19 | 20 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-12-14 13:13 | 55.6 | 38.9 | 0 | 5.5 | -5.2 | 5.2 | 999 | 3.7 | 16.9 | 98 | 25 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-12-14 13:12 | 53.8 | 38.9 | 0 | 7.3 | -0.8 | 0.8 | 999 | 4.36 | 9.1 | 51 | 15 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-12-14 13:11 | 0 | 0.1 | 20.6 | 79.3 | -3.7 | 3.7 | 999 | 0.04 | 1.6 | 0 | 0 | 25.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-12-14 13:10 | 61.6 | 39.2 | 0 | 0 | -55 | 55 | 999 | 1.05 | 8.9 | 57 | 99 | 27 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-12-14 13:09 | 0.1 | 0.2 | 20.3 | 79.4 | -5.5 | 5.5 | 999 | 0.05 | 0.9 | 0 | 0 | 27.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2017-12-14 13:08 | 59.7 | 40.1 | 0.1 | 0.1 | -2.8 | 2.8 | 999 | 1.81 | 11.9 | 74 | 28 | 30.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-12-14 13:06 | 57.2 | 41.3 | 0 | 1.5 | -0.6 | 0.6 | 999 | 1.18 | 9.5 | 57 | 20 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-12-14 13:03 | 57.2 | 38.9 | 0 | 3.9 | -65.8 | 65.8 | 999 | 1.58 | 23.2 | 139 | 99 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-12-14 13:01 | 58.3 | 38.8 | 0 | 2.9 | -24.1 | 24.1 | 999 | 3.91 | 17.4 | 106 | 50 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-12-14 13:00 | 55.5 | 37.3 | 0.8 | 6.4 | -64.5 | 64.5 | 998 | 1.15 | 9.2 | 53 | 99 | 27 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-12-14 12:59 | 60.2 | 38.1 | 0 | 1.7 | -8.2 | 8.2 | 999 | 5.94 | 21.7 | 137 | 45 | 28.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-12-14 12:57 | 49.3 | 37.7 | 0 | 13 | -2.5 | 2.5 | 999 | 7.46 | 23.5 | 121 | 25 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-12-14 12:56 | 59.9 | 40.9 | 0 | 0 | -13.2 | 13.2 | 999 | 2.3 | 13.4 | 84 | 28 | 25.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-12-14 12:54 | 54 | 37.8 | 0.7 | 7.5 | -3.6 | 3.6 | 999 | 1.21 | 9.7 | 54 | 10 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-12-14 12:53 | 61.2 | 40 | 0 | 0 | 0.5 | -0.5 | 999 | 11.46 | 65 | 417 | 60 | 29.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-12-14 12:50 | 5.8 | 4.6 | 18.6 | 71 | -0.1 | 0.1 | 999 | -0.01 | 0 | 0 | 0 | 28.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-12-14 12:49 | 52.2 | 38.6 | 0 | 9.2 | -8.9 | 8.9 | 999 | 1.7 | 24.5 | 134 | 20 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-12-14 12:48 | 49.8 | 35.6 | 0 | 14.6 | -31.2 | 31.2 | 999 | 2.03 | 26.2 | 137 | 20 | 37.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-12-14 12:47 | 52.8 | 36.5 | 0 | 10.7 | -7.2 | 7.2 | 999 | 5 | 42.3 | 233 | 40 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-12-14 12:46 | 56.2 | 37.4 | 0.5 | 5.9 | -58.3 | 58.3 | 999 | -0.15 | 0 | 0 | 80 | 28.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-12-14 12:44 | 61.7 | 39.4 | 0 | 0 | -0.2 | 0.2 | 999 | 0.36 | 11.6 | 75 | 22 | 28.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-12-14 12:43 | 57.2 | 38.6 | 0 | 4.2 | -57.2 | 57.2 | 999 | 0.85 | 27.8 | 167 | 99 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-12-14 11:41 | 54.8 | 40.1 | 0.1 | 5 | -35.7 | 35.7 | 996 | 19.53 | 79.7 | 458 | 99 | 49.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-12-14 11:40 | 58.7 | 41.5 | 0 | 0 | -43.6 | 43.6 | 996 | 9.02 | 54.7 | 336 | 99 | 42.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-12-14 11:39 | 58.1 | 41.2 | 0 | 0.7 | -42.1 | 42.1 | 996 | 12.57 | 105.7 | 643 | 99 | 42.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-12-14 11:38 | 30.1 | 21.8 | 8 | 40.1 | -1 | 1 | 996 | -0.04 | 0 | 0 | 0 | 41.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-12-14 11:37 | 41.2 | 31.6 | 4.8 | 22.4 | -28 | 28 | 996 | 27.5 | 94.4 | 407 | 70 | 47.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-12-14 11:35 | 60.3 | 42 | 0.1 | 0 | -38.5 | 38.5 | 996 | 0.24 | 8.9 | 56 | 28 | 39.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-12-14 11:33 | 0 | 0.1 | 20.8 | 79.1 | -52.9 | 52.9 | 996 | 0.01 | 0.8 | 0 | 0 | 27 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-12-14 11:32 | 44.9 | 37 | 0.5 | 17.6 | -5 | 5 | 996 | 6.87 | 22.5 | 106 | 20 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-12-14 11:31 | 54.9 | 40.1 | 0 | 5 | -35.9 | 35.9 | 996 | 1.77 | 24.5 | 140 | 40 | 36.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-12-14 11:29 | 58.3 | 43.7 | 0 | 0 | -43.9 | 43.9 | 996 | 7.35 | 49.1 | 300 | 80 | 42.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-12-14 11:28 | 0 | 0.1 | 21 | 78.9 | -5.4 | 5.4 | 996 | -0.09 | 0 | 0 | 0 | 27.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-12-14 11:27 | 2.3 | 2 | 20.5 | 75.2 | -23.2 | 23.2 | 996 | 0 | 0.3 | 0 | 0 | 29 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-12-14 11:26 | 61.8 | 42 | 0 | 0 | -26.4 | 26.4 | 996 | -0.07 | 0 | 0 | 0 | 31.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-12-14 11:25 | 59.3 | 41.1 | 0 | 0 | -49.4 | 49.4 | 996 | 8.38 | 85.9 | 534 | 99 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-12-14 11:23 | 52.2 | 38.6 | 0 | 9.2 | -7.5 | 7.5 | 996 | 11.75 | 29.9 | 163 | 40 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-12-14 11:22 | 46 | 35.9 | 0.2 | 17.9 | -8 | 8 | 996 | 14.19 | 32.4 | 156 | 40 | 35 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-12-14 11:21 | 51.8 | 38.9 | 0.2 | 9.1 | -8.9 | 8.9 | 996 | 2.56 | 30 | 163 | 40 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-12-14 11:19 | 59.1 | 42.4 | 0 | 0 | -36.8 | 36.8 | 996 | 0.37 | 11.2 | 69 | 20 | 30.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-12-14 11:07 | 42.4 | 32.3 | 2.9 | 22.4 | -0.3 | 0.3 | 998 | 3.65 | 8.2 | 36 | 10 | 34.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-12-14 11:05 | 52.3 | 36.7 | 1.2 | 9.8 | -4.8 | 4.8 | 998 | 9.39 | 57.4 | 315 | 40 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-12-14 11:04 | 51.1 | 34.3 | 2.4 | 12.2 | -27.3 | 27.3 | 998 | 3.93 | 17.2 | 92 | 25 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-12-14 11:03 | 58 | 39.7 | 0 | 2.3 | -37.3 | 37.3 | 998 | 4.39 | 39 | 237 | 50 | 33.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-12-14 11:02 | 56.4 | 38.3 | 0.8 | 4.5 | -20.3 | 20.3 | 998 | 21.85 | 40.7 | 240 | 40 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-12-14 11:00 | 18.1 | 18.3 | 8.6 | 55 | -0.4 | 0.4 | 998 | 0.05 | 0.9 | 1 | 2 | 27.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-12-14 10:59 | 50.7 | 37.8 | 0 | 11.5 | -1.5 | 1.5 | 998 | 1.68 | 5.6 | 29 | 15 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-12-14 10:58 | 59.8 | 38.6 | 0 | 1.6 | -47.5 | 47.5 | 998 | 8.56 | 89.6 | 561 | 99 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-12-14 10:57 | 47.9 | 34.1 | 0 | 18 | -1.7 | 1.7 | 998 | 19.98 | 2.1 | 10 | 10 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-12-14 10:56 | 57.6 | 37.7 | 0 | 4.7 | -1.2 | 1.2 | 998 | 1.34 | 10.2 | 62 | 20 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-12-14 10:55 | 52.9 | 36.5 | 0.5 | 10.1 | -6.1 | 6.1 | 998 | 3.57 | 35.5 | 197 | 40 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-12-14 10:53 | 48.7 | 37.7 | 0 | 13.6 | -1.4 | 1.4 | 998 | 3.25 | 15.5 | 79 | 25 | 38.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-12-14 10:52 | 51.9 | 37.3 | 0 | 10.8 | -36.2 | 36.2 | 998 | 24.42 | 91.2 | 495 | 99 | 36 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-12-14 10:44 | 4.8 | 4 | 9.9 | 81.3 | 0 | 0 | 997 | 0.02 | 0.6 | 0 | 0 | 31.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-12-14 10:43 | 55.7 | 39.2 | 0 | 5.1 | -6.8 | 6.8 | 997 | 3.69 | 16.6 | 97 | 20 | 39.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-12-14 10:42 | 54.2 | 40.8 | 0 | 5 | -34.5 | 34.5 | 997 | 29.44 | 160.5 | 912 | 99 | 45.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-12-14 10:41 | 0 | 0.1 | 20.5 | 79.4 | -4.1 | 4.1 | 997 | 0.02 | 1.1 | 0 | 0 | 23.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-12-14 10:39 | 58.1 | 41.4 | 0.3 | 0.2 | -3.4 | 3.4 | 997 | 1.34 | 21.8 | 133 | 20 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-12-14 10:38 | 54.2 | 39.6 | 0 | 6.2 | -3.3 | 3.3 | 997 | 1.73 | 24.4 | 138 | 25 | 41 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-12-14 10:37 | 48.6 | 37.7 | 0 | 13.7 | -6 | 6 | 997 | 5.06 | 41.6 | 212 | 40 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-12-14 10:36 | 44.2 | 33.8 | 3 | 19 | -0.7 | 0.7 | 997 | 7.64 | 11.9 | 55 | 20 | 30.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-12-14 10:34 | 56.9 | 39 | 0 | 4.1 | -7.9 | 7.9 | 997 | 25.08 | 44.1 | 263 | 50 | 31.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-12-14 10:33 | 52.2 | 38.1 | 0 | 9.7 | -31.4 | 31.4 | 997 | 0.91 | 17.6 | 96 | 20 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-12-14 10:32 | 49.3 | 35.5 | 1.6 | 13.6 | -1.7 | 1.7 | 997 | 0.82 | 17 | 88 | 20 | 30.6 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-12-14 10:30 | 39.1 | 28.4 | 5 | 27.5 | -0.6 | 0.6 | 997 | 18.26 | 9.4 | 38 | 5 | 26.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-12-14 10:29 | 38.2 | 35.4 | 0 | 26.4 | -0.7 | 0.7 | 997 | 6.08 | 5.3 | 21 | 10 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-12-14 10:21 | 58.5 | 42.3 | 0 | 0 | -53.3 | 53.3 | 997 | 2.41 | 45.9 | 281 | 99 | 42.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-12-14 10:20 | 54.3 | 40.1 | 1.4 | 4.2 | -0.1 | 0.1 | 997 | -0.01 | 0 | 0 | 0 | 32.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-12-14 10:19 | 58.5 | 43.6 | 0 | 0 | -54.6 | 54.6 | 997 | 1.11 | 8.8 | 54 | 99 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-12-14 10:18 | 57.6 | 40.9 | 0.5 | 1 | -55.4 | 55.4 | 997 | -0.1 | 0 | 0 | 99 | 28.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-12-14 10:17 | 52.8 | 39.1 | 0 | 8.1 | -14.4 | 14.4 | 997 | 11.93 | 64.4 | 356 | 50 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-12-14 10:15 | 58.7 | 41.1 | 0 | 0.2 | -28 | 28 | 997 | 2.48 | 13.5 | 83 | 25 | 37.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-12-14 10:14 | 0.4 | 6.1 | 16.5 | 77 | -5.6 | 5.6 | 997 | 0.01 | 1.5 | 0 | 0 | 35.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-12-14 10:13 | 52.7 | 39.1 | 0 | 8.2 | -26.4 | 26.4 | 997 | 6.65 | 47 | 260 | 50 | 44.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-12-14 10:12 | 54.3 | 39.3 | 0 | 6.4 | -53.6 | 53.6 | 997 | 3.27 | 53.5 | 305 | 99 | 40.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-12-14 10:11 | 44.2 | 39.6 | 0 | 16.2 | -1.5 | 1.5 | 997 | 0.16 | 3.3 | 15 | 40 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-12-14 09:07 | 37 | 30.5 | 0.1 | 32.4 | -97.1 | 97.1 | 997 | 2.09 | 11.8 | 33 | 35 | 23.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-12-14 09:06 | 0 | 0.2 | 19.9 | 79.9 | -11.1 | 11.1 | 997 | 0.28 | 0.2 | 0 | 0 | 24.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-12-14 09:05 | 38.6 | 29.4 | 1.7 | 30.3 | -101.4 | 101.4 | 997 | -0.02 | 0 | 0 | 50 | 23.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-12-14 09:04 | 30.4 | 31.4 | 0 | 38.2 | -69.3 | 69.3 | 997 | >>>> | 0 | 0 | 50 | 22.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-12-14 09:01 | 36.7 | 28.3 | 0 | 35 | -98.9 | 98.9 | 997 | 2.5 | 3.2 | 9 | 40 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-12-14 09:00 | 36 | 29.5 | 0.6 | 33.9 | -34.2 | 34.2 | 996 | 0.52 | 6 | 16 | 5 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-12-14 08:59 | 0.3 | 0.7 | 18.8 | 80.2 | 0 | 0 | 997 | 0 | 0 | 0 | 0 | 21.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-12-14 08:58 | 42.7 | 37.8 | 0.1 | 19.4 | -99.5 | 99.5 | 997 | 1.03 | 17.3 | 77 | 99 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2017-12-14 08:57 | 11.9 | 16.2 | 10.1 | 61.8 | -0.1 | 0.1 | 997 | 1.02 | 8.7 | 10 | 5 | 22.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-12-14 08:55 | 43.1 | 36.6 | 0.1 | 20.2 | -9.2 | 9.2 | 997 | 3.26 | 3.9 | 17 | 5 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-12-14 08:49 | 44.8 | 34.2 | 0 | 21 | -36.6 | 36.6 | 997 | 0.98 | 8.6 | 40 | 15 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-12-14 08:46 | 35.7 | 30 | 0.3 | 34 | -76.8 | 76.8 | 997 | 0.09 | 2.5 | 6 | 5 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-12-14 08:44 | 0.8 | 0.1 | 19.8 | 79.3 | 0 | 0 | 997 | -0.02 | 0 | 0 | 0 | 26 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-12-14 08:43 | 35.6 | 32.5 | 0 | 31.9 | -34 | 34 | 997 | 10.34 | 27.3 | 101 | 20 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-12-14 08:42 | 32.4 | 29 | 3.7 | 34.9 | -93 | 93 | 997 | 0.05 | 0.4 | 1 | 10 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-12-14 08:40 | 1.4 | 0.6 | 19.8 | 78.2 | -7.6 | 7.6 | 997 | -0.2 | 0 | 0 | 0 | 23.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-12-14 08:38 | 44.1 | 36.3 | 0 | 19.6 | -1.2 | 1.2 | 997 | -0.06 | 0 | 0 | 5 | 23.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-12-14 08:37 | 14.5 | 9.3 | 16.1 | 60.1 | -0.2 | 0.2 | 997 | -0.06 | 0 | 0 | 5 | 22.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-12-14 08:36 | 44.8 | 36 | 0 | 19.2 | -99 | 99 | 997 | 3.31 | 13.7 | 64 | 99 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-12-14 08:34 | 45.2 | 34.7 | 0.5 | 19.6 | -100.1 | 100.1 | 997 | 0 | 0 | 0 | 25 | 22.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-12-14 08:33 | 43.5 | 34.8 | 0 | 21.7 | -95.6 | 95.6 | 997 | -0.04 | 0 | 0 | 10 | 22.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-12-14 08:31 | 48.4 | 35.2 | 0 | 16.4 | -37.2 | 37.2 | 997 | 2.22 | 11.7 | 59 | 15 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-12-14 08:30 | 43.7 | 33.9 | 0 | 22.4 | -2.3 | 2.3 | 997 | 0.79 | 7.8 | 36 | 10 | 22.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2017-12-13 13:27 | 1.6 | 0.1 | 19.8 | 78.5 | -33.4 | 33.4 | 995 | 0.03 | 1.4 | 0 | 0 | 40.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-12-13 13:26 | 58.5 | 41.1 | 0 | 0 | -55.5 | 55.5 | 995 | 2.7 | 49.7 | 357 | 99 | 42.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2017-12-13 13:25 | 22 | 9.3 | 13.9 | 54.8 | -56.7 | 56.7 | 995 | -0.03 | 0 | 0 | 99 | 39.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-12-13 13:22 | 22.3 | 10.5 | 14.4 | 52.8 | -56.9 | 56.9 | 995 | 0 | 0.3 | 0 | 99 | 39.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-12-13 13:21 | 34.5 | 22.9 | 6.2 | 36.4 | 0 | 0 | 996 | -0.05 | 0 | 0 | 0 | 40.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-12-13 13:19 | 60.6 | 38.3 | 0 | 1.1 | -0.5 | 0.5 | 996 | 14.26 | 8.4 | 53 | 22 | 34.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-12-13 13:18 | 54.2 | 34.4 | 2.3 | 9.1 | -2 | 2 | 996 | 2.01 | 26.6 | 151 | 25 | 41.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-12-13 13:17 | 56.7 | 41.9 | 0 | 0 | -54.5 | 54.5 | 996 | 0.21 | 8.3 | 58 | 99 | 44.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2017-12-13 13:16 | 57.3 | 41.4 | 0 | 0 | -54.3 | 54.3 | 996 | 0.01 | 0.6 | 4 | 99 | 38.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-12-13 13:14 | 55.8 | 35.7 | 3.2 | 5.3 | -54.2 | 54.2 | 996 | -0.06 | 0 | 0 | 20 | 38.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-12-13 13:11 | 2.6 | 2.5 | 18.6 | 76.3 | 0.1 | -0.1 | 996 | -0.04 | 0 | 0 | 0 | 37.1 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-12-13 13:09 | 57.3 | 42.5 | 0 | 0 | -33.3 | 33.3 | 996 | 0.16 | 7.5 | 53 | 20 | 35.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-12-13 13:08 | 13 | 9.5 | 3.8 | 73.7 | 0 | 0 | 996 | -0.01 | 0 | 0 | 0 | 40 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-12-13 13:07 | 3.4 | 3.5 | 16.9 | 76.2 | 0 | 0 | 996 | -0.01 | 0 | 0 | 0 | 40.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-12-13 13:02 | 57.8 | 40.4 | 0 | 0 | -2.7 | 2.7 | 996 | 7.17 | 23.4 | 149 | 42 | 39.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-12-13 12:59 | 54.8 | 42 | 0 | 0 | -36.4 | 36.4 | 996 | 1.93 | 41.7 | 283 | 60 | 46 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-12-13 12:57 | 56.2 | 38.7 | 0 | 5.1 | -1.1 | 1.1 | 996 | 1.39 | 10.3 | 61 | 15 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-12-13 12:56 | 3.5 | 1.2 | 19.3 | 76 | 0 | 0 | 996 | -0.02 | 0 | 0 | 0 | 34.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-12-13 12:55 | 58.2 | 39.6 | 0.1 | 0 | -50 | 50 | 996 | 1.14 | 32.5 | 208 | 99 | 33.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-12-13 12:53 | 56.5 | 39.2 | 0 | 4.3 | -0.4 | 0.4 | 999 | 11.65 | 29.2 | 173 | 40 | 50.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-12-13 11:27 | 45.4 | 33.3 | 0.1 | 21.2 | -0.2 | 0.2 | 999 | 0.05 | 2 | 9 | 10 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-12-13 11:26 | 58.9 | 37.2 | 0 | 3.9 | -16.5 | 16.5 | 998 | 8.23 | 54.3 | 335 | 50 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-12-13 11:25 | 58.9 | 37.2 | 0 | 3.9 | -16.5 | 16.5 | 998 | 8.23 | 54.3 | 335 | 50 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-12-13 11:23 | 54.3 | 35.3 | 0.2 | 10.2 | -1.6 | 1.6 | 998 | 1.44 | 22.6 | 128 | 25 | 39.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-12-13 11:22 | 56.5 | 36 | 0 | 7.5 | -4.4 | 4.4 | 998 | 1.95 | 26.5 | 157 | 40 | 36.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-12-13 11:20 | 49.8 | 33.5 | 0 | 16.7 | -51.4 | 51.4 | 999 | 1.63 | 23.5 | 123 | 40 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-12-13 11:19 | 43.8 | 26.1 | 6.2 | 23.9 | -0.2 | 0.2 | 999 | 0.38 | 5.4 | 25 | 10 | 29.2 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-12-13 11:17 | 60.4 | 38.7 | 0 | 0.9 | -0.3 | 0.3 | 999 | 7.84 | 6.2 | 39 | 17 | 33.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-12-13 11:15 | 58.4 | 39.6 | 0 | 0 | -0.5 | 0.5 | 999 | 1.65 | 5.6 | 37 | 10 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-12-13 11:14 | 56.3 | 41.3 | 0 | 0 | 0.2 | -0.2 | 999 | 1.49 | 2.7 | 19 | 7 | 31.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-12-13 11:04 | 50.4 | 37.2 | 0.1 | 12.3 | -11.2 | 11.2 | 999 | 8.11 | 52.3 | 276 | 50 | 45.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-12-13 11:03 | 49 | 24.5 | 9.4 | 17.1 | -47.9 | 47.9 | 999 | 0.01 | 2.8 | 14 | 90 | 33.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-12-13 11:02 | 49.5 | 38.2 | 0 | 12.3 | -2.5 | 2.5 | 999 | 8.38 | 6.2 | 32 | 20 | 41.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-12-13 11:00 | 57.5 | 40.3 | 0 | 2.2 | -1.2 | 1.2 | 999 | 0.74 | 16.3 | 98 | 25 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-12-13 10:59 | 55.7 | 38.9 | 0 | 5.4 | -3.1 | 3.1 | 999 | 0.83 | 17.3 | 101 | 20 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-12-13 10:58 | 58.6 | 38.9 | 0 | 2.5 | -0.3 | 0.3 | 999 | 0.39 | 11.8 | 72 | 10 | 34.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-12-13 10:57 | 21.9 | 13.5 | 8.2 | 56.4 | -0.4 | 0.4 | 999 | -0.02 | 0 | 0 | 0 | 37.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-12-13 10:55 | 55.9 | 37 | 0 | 7.1 | -0.3 | 0.3 | 999 | 0.02 | 2.8 | 16 | 10 | 40 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-12-13 10:54 | 61.2 | 40.6 | 0 | 0 | -0.4 | 0.4 | 999 | 1.11 | 19.8 | 127 | 40 | 40.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-12-13 10:52 | 54.2 | 39.6 | 0 | 6.2 | -22.6 | 22.6 | 999 | 19.75 | 81.9 | 465 | 80 | 40 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-12-13 10:51 | 52.1 | 39 | 0 | 8.9 | -0.5 | 0.5 | 999 | 0.21 | 8.5 | 46 | 15 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-12-13 10:50 | 52.2 | 38.7 | 0 | 9.1 | -1 | 1 | 999 | 2.9 | 14.8 | 81 | 20 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-12-13 10:46 | 61.7 | 38.8 | 0.2 | 0 | -3.6 | 3.6 | 999 | 10.59 | 28.8 | 186 | 45 | 34.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-12-13 10:45 | 62.4 | 39.6 | 0 | 0 | -13 | 13 | 999 | 7.76 | 24.6 | 161 | 40 | 32 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-12-13 10:43 | 50.9 | 31.7 | 1.1 | 16.3 | -4.1 | 4.1 | 999 | 4.78 | 19.4 | 103 | 20 | 31.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-12-13 09:25 | 37.4 | 34 | 0 | 28.6 | -0.1 | 0.1 | 999 | 1.5 | 10.5 | 41 | 20 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-12-13 09:23 | 27.4 | 28.4 | 0 | 44.2 | -4.6 | 4.6 | 999 | 4.61 | 18.4 | 53 | 25 | 26.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-12-13 09:21 | 32.5 | 30.4 | 1.4 | 35.7 | -0.3 | 0.3 | 999 | 2.39 | 13.3 | 45 | 18 | 27.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-12-13 09:18 | 38.3 | 33.6 | 0 | 28.1 | 0.1 | -0.1 | 999 | 0.72 | 7.3 | 29 | 6 | 29.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-12-13 09:17 | 40.1 | 33.5 | 0 | 26.4 | -19.5 | 19.5 | 999 | 1.28 | 9.7 | 41 | 13 | 28.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-12-13 09:14 | 39.6 | 32.3 | 0 | 28.1 | -3.3 | 3.3 | 999 | 1.73 | 40 | 166 | 37 | 32.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-12-13 09:13 | 39.2 | 34 | 0 | 26.8 | -1.9 | 1.9 | 999 | 11.03 | 14.2 | 58 | 17 | 30.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-12-13 09:11 | 38.2 | 32.4 | 0.4 | 29 | -4.8 | 4.8 | 998 | 9.42 | 26.3 | 105 | 22 | 35 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-12-13 09:07 | 43 | 35.5 | 0 | 21.5 | -1.2 | 1.2 | 998 | 0.05 | 1.8 | 8 | 5 | 37.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-12-13 09:06 | 42.2 | 36.8 | 0 | 21 | -59.1 | 59.1 | 998 | 0.37 | 17.6 | 78 | 99 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-12-13 09:05 | 40.2 | 35.8 | 0 | 24 | -0.3 | 0.3 | 998 | 8.79 | 25.2 | 106 | 22 | 38.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-12-13 09:03 | 37.3 | 33.8 | 0 | 28.9 | -0.3 | 0.3 | 998 | 13.08 | 15.4 | 60 | 15 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-12-13 09:02 | 44.2 | 39.8 | 0 | 16 | -2.2 | 2.2 | 998 | 16.48 | 8.7 | 40 | 15 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-12-13 09:00 | 45.3 | 41.9 | 0 | 12.8 | -43.6 | 43.6 | 998 | 7.28 | 21.8 | 103 | 50 | 51.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-12-13 08:59 | 48.1 | 41.7 | 0.1 | 10.1 | -9.7 | 9.7 | 998 | 1.01 | 18.3 | 92 | 20 | 39.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-12-13 08:57 | 55 | 44.8 | 0 | 0.2 | -17.8 | 17.8 | 998 | 16.97 | 34.4 | 198 | 50 | 47.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-12-13 08:56 | 50.5 | 42.5 | 1.5 | 5.5 | -36 | 36 | 998 | 7 | 5.6 | 29 | 20 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-12-13 08:55 | 27.9 | 33.2 | 0.2 | 38.7 | -1.3 | 1.3 | 998 | 8.92 | 1.3 | 4 | 2 | 31.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-12-12 16:09 | 59.5 | 40.4 | 0 | 0.1 | -29.4 | 29.4 | 1004 | 4.54 | 64.5 | 402 | 80 | 40 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2017-12-12 16:07 | 58.1 | 49.9 | 0 | 0 | -13.3 | 13.3 | 1004 | 8.69 | 53.9 | 328 | 55 | 34.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2017-12-12 16:05 | 54 | 57.7 | 0 | >>>> | -4.9 | 4.9 | 1004 | 1.69 | 23.1 | 130 | 25 | 35.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2017-12-12 16:04 | 56.3 | 53.1 | 0 | 0 | -4.7 | 4.7 | 1004 | 3.51 | 33.8 | 199 | 45 | 37.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2017-12-12 16:02 | 49.2 | 58.4 | 0 | 0 | -3.2 | 3.2 | 1004 | 4.04 | 35.3 | 182 | 40 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2017-12-12 16:01 | 47.5 | 58.4 | 0 | 0 | -25.2 | 25.2 | 1004 | 0.21 | 7.8 | 39 | 5 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-12-12 15:58 | 55.7 | 40.9 | 0.6 | 2.8 | -2.8 | 2.8 | 1004 | -0.2 | 0 | 0 | 10 | 29.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-12-12 15:57 | 50.7 | 38.2 | 0.2 | 10.9 | -2.6 | 2.6 | 1004 | 6.78 | 22.5 | 119 | 40 | 36 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-12-12 15:56 | 32.3 | 30.9 | 0 | 36.8 | -0.6 | 0.6 | 1004 | 1.22 | 2.3 | 7 | 5 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-12-12 15:54 | 51.4 | 38.8 | 0 | 9.8 | -43.3 | 43.3 | 1004 | 16.68 | 120.3 | 648 | 99 | 44.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-12-12 15:53 | 51.9 | 39.1 | 0 | 9 | -12.9 | 12.9 | 1004 | 10.27 | 59.5 | 323 | 50 | 36.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-12-12 15:52 | 57.3 | 41.6 | 0 | 1.1 | -37.9 | 37.9 | 1004 | 19.15 | 37.8 | 227 | 99 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-12-12 15:51 | 46.4 | 38 | 0 | 15.6 | -0.1 | 0.1 | 1004 | 0.09 | 5.6 | 27 | 5 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-12-12 15:50 | 46.7 | 32.9 | 3.9 | 16.5 | -5.7 | 5.7 | 1004 | 9.22 | 56.9 | 278 | 40 | 34.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-12-12 15:47 | 50.2 | 38.6 | 0 | 11.2 | -22.7 | 22.7 | 1004 | 2.54 | 46.8 | 246 | 50 | 51.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-12-12 15:46 | 57 | 42.1 | 0 | 0.9 | -0.2 | 0.2 | 1004 | 0.91 | 0.4 | 2 | 2 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-12-12 15:44 | 54.2 | 38.1 | 0.2 | 7.5 | -0.4 | 0.4 | 1004 | 0.31 | 4.8 | 27 | 5 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-12-12 15:43 | 51.5 | 40 | 0 | 8.5 | -0.4 | 0.4 | 1004 | 2.08 | 12.3 | 66 | 20 | 39.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-12-12 15:42 | 52.7 | 41.4 | 0 | 5.9 | -42.1 | 42.1 | 1004 | 11.59 | 7.1 | 39 | 99 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-12-12 15:40 | 45.3 | 37.8 | 0 | 16.9 | -1.9 | 1.9 | 1004 | 11.61 | 28.4 | 135 | 25 | 52.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-12-12 15:39 | 56.1 | 39.6 | 0 | 4.3 | -30.1 | 30.1 | 1004 | 16.27 | 119.5 | 702 | 80 | 50.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-12-12 15:38 | 54.8 | 40.9 | 0 | 4.3 | -0.3 | 0.3 | 1004 | 3.92 | 8.4 | 48 | 15 | 39.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-12-12 15:37 | 50.6 | 38.5 | 0 | 10.9 | -1.9 | 1.9 | 1004 | 1.37 | 21.7 | 115 | 25 | 38.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-12-12 15:35 | 42.4 | 36.3 | 0.7 | 20.6 | 0 | 0 | 1004 | 14.1 | 1.7 | 7 | 5 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-12-12 15:22 | 1.1 | 1.6 | 19.2 | 78.1 | -0.2 | 0.2 | 1005 | 0.02 | 1.1 | 0 | 0 | 30.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-12-12 15:20 | 57.2 | 40.2 | 0.5 | 2.1 | -0.2 | 0.2 | 1005 | 0.06 | 1.1 | 6 | 0 | 29.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-12-12 15:19 | 0.3 | 0.1 | 20.2 | 79.4 | 0 | 0 | 1005 | -0.04 | 0 | 0 | 0 | 27.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-12-12 15:18 | 56.3 | 41.3 | 0.4 | 2 | -9.8 | 9.8 | 1005 | -0.1 | 0 | 0 | 15 | 37.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-12-12 15:16 | 49.8 | 38.8 | 0 | 11.4 | -0.4 | 0.4 | 1005 | 4.45 | 9.1 | 47 | 15 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-12-12 15:15 | 52.8 | 37 | 0 | 10.2 | -25.7 | 25.7 | 1006 | 14.69 | 72 | 398 | 70 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-12-12 15:14 | 50.8 | 37.1 | 0 | 12.1 | -2.5 | 2.5 | 1006 | 0.51 | 13.5 | 72 | 20 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-12-12 15:13 | 51.9 | 40.1 | 0 | 8 | -0.7 | 0.7 | 1006 | 0.53 | 13.7 | 74 | 20 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-12-12 15:11 | 53.9 | 39.4 | 0 | 6.7 | -1.9 | 1.9 | 1006 | 0.61 | 14.8 | 84 | 20 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-12-12 15:07 | 54 | 38.7 | 0.3 | 7 | -0.7 | 0.7 | 1006 | 0.82 | 17.3 | 98 | 20 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-12-12 15:06 | 46.5 | 36.1 | 0.4 | 17 | -2.1 | 2.1 | 1006 | 1.35 | 21.8 | 106 | 25 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-12-12 15:04 | 56.5 | 41.2 | 0 | 2.3 | -0.2 | 0.2 | 1006 | 0.39 | 11.7 | 69 | 25 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-12-12 15:03 | 39.3 | 35.5 | 0 | 25.2 | -0.9 | 0.9 | 1006 | 1.4 | 10.1 | 41 | 20 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-12-12 15:02 | 59 | 41.8 | 0 | 0 | 0 | 0 | 1006 | 0.82 | 8 | 49 | 12 | 26.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-12-12 14:57 | 58.6 | 40 | 0 | 1.4 | -3.2 | 3.2 | 1006 | 2.31 | 28.9 | 177 | 20 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-12-12 14:56 | 57.6 | 41 | 0 | 1.4 | -1.6 | 1.6 | 1006 | 1.14 | 20.2 | 122 | 25 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-12-12 14:55 | 57.6 | 41.5 | 0 | 0.9 | -1.2 | 1.2 | 1006 | 1.99 | 12.3 | 74 | 25 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-12-12 14:54 | 59.7 | 41.2 | 0 | 0 | 0.3 | -0.3 | 1006 | 0.03 | 0.7 | 4 | 5 | 35.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-12-12 14:51 | 57.8 | 43.4 | 0 | 0 | -84.4 | 84.4 | 1006 | 0.1 | 5.5 | 33 | 80 | 39.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2017-12-11 14:52 | 36.4 | 31.5 | 0 | 32.1 | 0 | 0 | 1011 | 0.03 | 0.6 | 2 | 5 | 30.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2017-12-11 14:50 | 0.4 | 0.2 | 20.5 | 78.9 | -51.6 | 51.6 | 1011 | -0.03 | 0 | 0 | 0 | 28.8
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2017-12-11 14:49 | 0.3 | 0.1 | 20.5 | 79.1 | -51.4 | 51.4 | 1011 | -0.02 | 0 | 0 | 0 | 28.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2017-12-11 14:48 | 50.6 | 37.4 | 0 | 12 | -3.8 | 3.8 | 1011 | 8.19 | 12.4 | 66 | 20 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-12-11 14:45 | 48.2 | 37.2 | 0 | 14.6 | -4.6 | 4.6 | 1011 | 7.96 | 24.6 | 124 | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2017-12-11 14:43 | 59.1 | 40.3 | 0.4 | 0.2 | -53.1 | 53.1 | 1011 | 7.45 | 23.6 | 146 | 40 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2017-12-11 14:41 | 0.6 | 0.3 | 20.5 | 78.6 | -50.9 | 50.9 | 1011 | -0.15 | 0 | 0 | 0 | 27.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2017-12-11 14:39 | 60.6 | 40.2 | 0 | 0 | -2.6 | 2.6 | 1011 | 29.36 | 23.9 | 151 | 50 | 29.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-12-11 14:37 | 43 | 35.7 | 0 | 21.3 | -0.4 | 0.4 | 1011 | 0.36 | 5.2 | 23 | 10 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2017-12-11 14:34 | 0.9 | 0.6 | 20.5 | 78 | -50.5 | 50.5 | 1011 | -0.06 | 0 | 0 | 0 | 27.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2017-12-11 14:32 | 0.2 | 0 | 20.7 | 79.1 | -50.7 | 50.7 | 1011 | -0.13 | 0 | 0 | 10 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2017-12-11 14:29 | 62.3 | 39 | 0 | 0 | -2.9 | 2.9 | 1012 | 19.72 | 19.8 | 129 | 45 | 26.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2017-12-11 14:25 | 0.2 | 1.1 | 20.3 | 78.4 | -51.5 | 51.5 | 1012 | -0.16 | 0 | 0 | 10 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2017-12-11 14:22 | 0.2 | 0.7 | 20.2 | 78.9 | -51.2 | 51.2 | 1012 | 0.04 | 6 | 0 | 25 | 27.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-12-11 14:13 | 60.9 | 41.4 | 0 | 0 | -34.5 | 34.5 | 1012 | 0.24 | 9.1 | 58 | 30 | 29.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-12-11 14:12 | 52.3 | 35.6 | 0.3 | 11.8 | -3.6 | 3.6 | 1012 | 1.92 | 12.2 | 67 | 20 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-12-11 14:11 | 55.7 | 38.1 | 0 | 6.2 | -11.7 | 11.7 | 1012 | 14.45 | 8.4 | 49 | 20 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-12-11 14:10 | 60.3 | 41.4 | 0 | 0 | -22.9 | 22.9 | 1012 | 0.14 | 7.2 | 45 | 22 | 25.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-12-11 14:08 | 49.5 | 36.4 | 0 | 14.1 | -14.4 | 14.4 | 1012 | 3.44 | 16.1 | 83 | 40 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-12-11 14:07 | 50 | 36.4 | 1.2 | 12.4 | -3.9 | 3.9 | 1012 | 0.93 | 29.5 | 155 | 40 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-12-11 14:06 | 60.3 | 41.6 | 0 | 0 | -0.1 | 0.1 | 1012 | 4.72 | 19.2 | 121 | 20 | 31.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-12-11 14:04 | 60.6 | 41.5 | 0 | 0 | -36.5 | 36.5 | 1012 | 3.04 | 32.3 | 205 | 99 | 36.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-12-11 14:03 | 57.9 | 39 | 0 | 3.1 | -14.8 | 14.8 | 1012 | 0.81 | 17 | 103 | 40 | 33.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-12-11 13:58 | 41.2 | 32.8 | 1.5 | 24.5 | -18.2 | 18.2 | 1012 | 0.87 | 8 | 34 | 15 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-12-11 13:57 | 53.8 | 39.1 | 0 | 7.1 | 0 | 0 | 1012 | 0.32 | 5 | 28 | 5 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-12-11 13:56 | 56.5 | 39.4 | 0 | 4.1 | -3.7 | 3.7 | 1012 | 4.08 | 38.5 | 228 | 40 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-12-11 13:55 | 53.3 | 35.5 | 0 | 11.2 | -4.8 | 4.8 | 1012 | 0.36 | 2.6 | 14 | 5 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-12-11 13:54 | 0.2 | 0.5 | 20.1 | 79.2 | -9.1 | 9.1 | 1012 | 1.87 | 0.6 | 0 | 2 | 25.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-12-11 13:52 | 46.7 | 35 | 0 | 18.3 | -29.2 | 29.2 | 1012 | 0.49 | 6 | 29 | 15 | 26.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-12-11 13:51 | 53.4 | 36.5 | 0 | 10.1 | -20.3 | 20.3 | 1012 | 6.83 | 49.5 | 277 | 50 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-12-11 13:49 | 42.1 | 28.7 | 1.3 | 27.9 | -11.3 | 11.3 | 1012 | 2.72 | 7.2 | 31 | 8 | 25.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-12-11 13:48 | 64.6 | 37.6 | 0 | 0 | -15.2 | 15.2 | 1012 | 24.82 | 2.4 | 16 | 30 | 27.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-12-11 13:46 | 41.6 | 32.3 | 0 | 26.1 | -31.5 | 31.5 | 1012 | 0.15 | 7 | 30 | 50 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-12-11 11:30 | 3.7 | 2 | 19.3 | 75 | -0.9 | 0.9 | 1012 | 0.16 | 7.4 | 2 | 0 | 27.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-12-11 11:29 | 54.9 | 36.8 | 0 | 8.3 | -10 | 10 | 1012 | 15.05 | 34.1 | 196 | 50 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-12-11 11:28 | 59.4 | 38.8 | 0 | 1.8 | -4.8 | 4.8 | 1013 | 8.47 | 55.4 | 345 | 50 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-12-11 11:27 | 57.1 | 38.7 | 0 | 4.2 | -1.6 | 1.6 | 1012 | 8.16 | 25 | 150 | 40 | 36.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-12-11 11:26 | 54.9 | 38.6 | 0 | 6.5 | -35.4 | 35.4 | 1012 | 1.08 | 8.9 | 51 | 20 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-12-11 11:25 | 63.4 | 38.9 | 0 | 0 | -19.4 | 19.4 | 1013 | 1.21 | 21.1 | 140 | 30 | 28 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-12-11 11:23 | 55.8 | 37.7 | 0 | 6.5 | -10.6 | 10.6 | 1013 | 13.82 | 32.6 | 191 | 40 | 32.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-12-11 11:22 | 63.7 | 39.1 | 0 | 0 | -13.1 | 13.1 | 1013 | 1.33 | 10.4 | 69 | 25 | 24.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-12-11 11:20 | 59.6 | 38 | 0 | 2.4 | -12.4 | 12.4 | 1013 | 16.1 | 35.8 | 223 | 40 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-12-11 11:19 | 55.6 | 38.2 | 0 | 6.2 | -1.8 | 1.8 | 1013 | 12.76 | 15.7 | 91 | 20 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-12-11 11:18 | 55.6 | 38.8 | 0 | 5.6 | -2.6 | 2.6 | 1013 | 12.96 | 31.5 | 183 | 40 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-12-11 11:09 | 61.6 | 41.8 | 0 | 0 | -30.5 | 30.5 | 1012 | 20.56 | 136.1 | 878 | 99 | 45.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-12-11 11:08 | 52.6 | 38.3 | 0 | 9.1 | -7 | 7 | 1012 | 8.36 | 25 | 138 | 40 | 36.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-12-11 11:07 | 54.6 | 38.9 | 0 | 6.5 | -25.9 | 25.9 | 1012 | 20.45 | 83.1 | 475 | 99 | 42.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-12-11 11:06 | 11.6 | 7.3 | 16.6 | 64.5 | -12.5 | 12.5 | 1012 | 16.96 | 35.2 | 42 | 0 | 36.4 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-12-11 11:04 | 61 | 42.6 | 0 | 0 | -41.2 | 41.2 | 1012 | 2.89 | 30.9 | 197 | 99 | 46.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-12-11 11:02 | 32.6 | 30.9 | 1.5 | 35 | -10.1 | 10.1 | 1012 | 1.55 | 10.5 | 36 | 20 | 35.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-12-11 11:01 | 50.8 | 43.5 | 0 | 5.7 | -3.7 | 3.7 | 1012 | 12.98 | 30.7 | 163 | 40 | 36.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-12-11 10:59 | 59.8 | 42.3 | 0 | 0 | -11.8 | 11.8 | 1012 | 6.14 | 75.1 | 471 | 70 | 41.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-12-11 10:58 | 54.1 | 39.8 | 1.5 | 4.6 | -44.8 | 44.8 | 1011 | 0.02 | 1.2 | 7 | 99 | 29.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-11-27 13:52 | 32.2 | 29.7 | 0.3 | 37.8 | -94.8 | 94.8 | 1008 | 0.7 | 6.9 | 23 | 50 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-11-27 13:51 | 5.5 | 8.7 | 12.8 | 73 | -6.2 | 6.2 | 1008 | 1.36 | 0.5 | 0 | 0 | 24.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-11-27 13:49 | 33.8 | 27.9 | 2.3 | 36 | -98.2 | 98.2 | 1008 | -0.04 | 0 | 0 | 40 | 23.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-11-27 13:48 | 37.2 | 30.9 | 0 | 31.9 | -79 | 79 | 1008 | 19.96 | 9.4 | 36 | 99 | 22.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-11-27 13:46 | 32.7 | 28.8 | 0 | 38.5 | -95.5 | 95.5 | 1008 | 2.18 | 3 | 10 | 50 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-11-27 13:45 | 32.1 | 28.9 | 0.9 | 38.1 | -34 | 34 | 1008 | 0.55 | 6.3 | 21 | 5 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-11-27 13:44 | 0.2 | 0.1 | 20.1 | 79.6 | 0 | 0 | 1008 | -0.01 | 0 | 0 | 0 | 22.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-11-27 13:42 | 49.9 | 37.1 | 0 | 13 | -97.1 | 97.1 | 1008 | 0.68 | 14.3 | 74 | 99 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2017-11-27 13:41 | 18.7 | 15.5 | 10.8 | 55 | 0 | 0 | 1008 | 1.19 | 9.5 | 18 | 10 | 22.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-11-27 13:40 | 51.9 | 35.9 | 0 | 12.2 | -10.1 | 10.1 | 1008 | 3.07 | 3.9 | 21 | 5 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-11-27 13:38 | 43.1 | 32.4 | 0 | 24.5 | -36.1 | 36.1 | 1008 | 0.73 | 7.4 | 33 | 10 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-11-27 13:35 | 28.9 | 29.6 | 0.3 | 41.2 | -94.9 | 94.9 | 1008 | 0.17 | 3.4 | 10 | 5 | 23.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-11-27 13:33 | 0.1 | 0.1 | 20.3 | 79.5 | 0 | 0 | 1008 | -0.01 | 0 | 0 | 0 | 25.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-11-27 13:31 | 34.9 | 31 | 0.2 | 33.9 | -33.4 | 33.4 | 1008 | 10.96 | 28.2 | 103 | 25 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-11-27 13:30 | 29.1 | 26.7 | 3.3 | 40.9 | -97.5 | 97.5 | 1008 | -0.1 | 0 | 0 | 25 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-11-27 13:28 | 11.9 | 7.8 | 18.4 | 61.9 | -13.6 | 13.6 | 1008 | 0.11 | 0.1 | 0 | 0 | 22.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-11-27 13:26 | 44.7 | 35.3 | 0 | 20 | -1.2 | 1.2 | 1008 | 0.03 | 1.4 | 6 | 5 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-11-27 13:25 | 26.5 | 21.2 | 7.6 | 44.7 | -0.3 | 0.3 | 1008 | 0.78 | 1.9 | 5 | 5 | 22.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-11-27 13:23 | 42.9 | 33.9 | 0 | 23.2 | -94.1 | 94.1 | 1008 | 1.15 | 8 | 36 | 99 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-11-27 13:21 | 42.2 | 30.2 | 1.9 | 25.7 | -94.5 | 94.5 | 1008 | -0.01 | 0 | 0 | 40 | 22.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-11-27 13:20 | 46.2 | 35 | 1 | 17.8 | -97 | 97 | 1008 | 0.02 | 1.3 | 6 | 25 | 22.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-11-27 13:18 | 45.7 | 34.5 | 0.1 | 19.7 | -32.8 | 32.8 | 1008 | 1.75 | 10.3 | 49 | 20 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-11-27 13:17 | 39.1 | 33.2 | 0.3 | 27.4 | -1.7 | 1.7 | 1008 | 0.85 | 8 | 33 | 10 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-11-24 12:27 | 58.1 | 41.2 | 0 | 0.7 | 0 | 0 | 1004 | 0.41 | 5.5 | 34 | 5 | 34.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-11-24 12:26 | 54.7 | 39.2 | 0 | 6.1 | -36.7 | 36.7 | 1004 | 5.84 | 72.4 | 415 | 50 | 39.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-11-24 12:18 | 46.5 | 34.7 | 1.8 | 17 | -0.1 | 0.1 | 1005 | 3.52 | 34.9 | 170 | 20 | 37.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-11-24 12:17 | 48.9 | 34.8 | 1.9 | 14.4 | -3.7 | 3.7 | 1005 | 8.33 | 53.9 | 276 | 40 | 38 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-11-24 12:16 | 54.3 | 36 | 1.5 | 8.2 | -31.7 | 31.7 | 1005 | 2.3 | 13.1 | 74 | 25 | 33 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-11-24 12:14 | 56.3 | 39.5 | 0 | 4.2 | -40.6 | 40.6 | 1005 | 1.76 | 24.5 | 145 | 50 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-11-24 12:13 | 56.4 | 38.6 | 0.7 | 4.3 | -20.9 | 20.9 | 1005 | 17.32 | 36.1 | 213 | 40 | 35 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-11-24 12:12 | 16.1 | 13.2 | 11 | 59.7 | -0.1 | 0.1 | 1005 | 0.09 | 1.2 | 2 | 2 | 30.6 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-11-24 12:11 | 50.6 | 37.9 | 0 | 11.5 | -0.9 | 0.9 | 1005 | 1.31 | 4.9 | 26 | 5 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-11-24 12:10 | 56.1 | 38.2 | 0 | 5.7 | -41.1 | 41.1 | 1005 | 9.91 | 95.8 | 563 | 99 | 32.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-11-24 12:09 | 47.4 | 33.8 | 0.4 | 18.4 | -1.4 | 1.4 | 1005 | 17.24 | 9.2 | 45 | 5 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-11-24 12:07 | 55.4 | 37.4 | 0.1 | 7.1 | -0.8 | 0.8 | 1005 | 1.03 | 8.9 | 52 | 20 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-11-24 12:06 | 52.9 | 36.8 | 0.4 | 9.9 | -5.1 | 5.1 | 1005 | 3.21 | 33.6 | 186 | 40 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-11-24 12:05 | 49.8 | 38.3 | 0 | 11.9 | -0.9 | 0.9 | 1005 | 3.11 | 15.1 | 79 | 30 | 41 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-11-24 12:03 | 51.1 | 37.3 | 0 | 11.6 | -31.8 | 31.8 | 1004 | 21.62 | 85.7 | 459 | 99 | 36.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-11-24 11:54 | 0.4 | 0.1 | 19.6 | 79.9 | -0.2 | 0.2 | 1004 | 0.15 | 1.6 | 0 | 0 | 33.2 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-11-24 11:53 | 52.3 | 37.8 | 0 | 9.9 | -5.1 | 5.1 | 1004 | 3.22 | 15.4 | 84 | 20 | 39.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-11-24 11:52 | 50.4 | 39.1 | 0 | 10.5 | -32.9 | 32.9 | 1004 | 22.51 | 139.8 | 739 | 99 | 45.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-11-24 11:51 | 40.5 | 35 | 0.3 | 24.2 | -3.3 | 3.3 | 1004 | 0.07 | 2.2 | 9 | 5 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-11-24 11:49 | 58.3 | 41.8 | 0.1 | 0 | -1.3 | 1.3 | 1004 | 0.51 | 13.5 | 82 | 20 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-11-24 11:48 | 52.4 | 39.5 | 0 | 8.1 | -1.9 | 1.9 | 1004 | 1.22 | 20.4 | 112 | 25 | 41.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-11-24 11:46 | 47.4 | 37.3 | 0 | 15.3 | -5.1 | 5.1 | 1004 | 4.48 | 39.6 | 196 | 40 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-11-24 11:45 | 51.7 | 38.2 | 1.2 | 8.9 | -0.3 | 0.3 | 1004 | 6.69 | 11.2 | 60 | 20 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-11-24 11:44 | 54.3 | 38.4 | 0 | 7.3 | -6.8 | 6.8 | 1004 | 21.89 | 40.9 | 233 | 40 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-11-24 11:43 | 50.2 | 37.6 | 0 | 12.2 | -21.9 | 21.9 | 1004 | 0.74 | 15.9 | 83 | 20 | 34.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-11-24 11:41 | 26.2 | 17.6 | 10.7 | 45.5 | -1.5 | 1.5 | 1004 | 1.79 | 25 | 69 | 10 | 33.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-11-24 11:40 | 37.5 | 28.2 | 4.5 | 29.8 | -0.6 | 0.6 | 1004 | 19.95 | 9.8 | 38 | 20 | 29.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-11-24 11:37 | 45.6 | 38.4 | 0 | 16 | -0.4 | 0.4 | 1004 | 5.3 | 4.9 | 23 | 15 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-11-24 11:02 | 58 | 42.2 | 0.1 | 0 | -47.3 | 47.3 | 1004 | 1.94 | 41.3 | 251 | 99 | 41.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-11-24 11:01 | 58.8 | 42.8 | 0 | 0 | -0.1 | 0.1 | 1004 | -0.02 | 0 | 0 | 0 | 33.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-11-24 10:59 | 58.1 | 43.7 | 0 | 0 | -48 | 48 | 1004 | 1.02 | 8.5 | 52 | 99 | 37.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-11-24 10:58 | 57.9 | 42.1 | 0.3 | 0 | -49.1 | 49.1 | 1004 | 0.14 | 3.2 | 19 | 99 | 27.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-11-24 10:57 | 51.8 | 39 | 0 | 9.2 | -9.5 | 9.5 | 1004 | 10.76 | 61.4 | 333 | 50 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-11-24 10:56 | 57 | 41.4 | 0 | 1.6 | -28 | 28 | 1004 | 1.67 | 11 | 66 | 15 | 37.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-11-24 10:55 | 0.9 | 5.5 | 16.3 | 77.3 | -5.1 | 5.1 | 1004 | 0 | 0 | 0 | 0 | 37.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-11-24 10:54 | 51.4 | 39.1 | 0 | 9.5 | -23.7 | 23.7 | 1004 | 5.69 | 43.4 | 233 | 50 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-11-24 10:53 | 53 | 39 | 0 | 8 | -46.2 | 46.2 | 1004 | 2.17 | 43.7 | 243 | 99 | 39.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-11-24 10:51 | 45.9 | 38.1 | 0.9 | 15.1 | -1.6 | 1.6 | 1003 | 1.61 | 10.6 | 51 | 40 | 48.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-11-24 10:41 | 62.2 | 42.2 | 0 | 0 | -19.5 | 19.5 | 1006 | 22.24 | 88.1 | 574 | 99 | 38.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-11-24 10:39 | 61.2 | 42.8 | 0 | 0 | -35.7 | 35.7 | 1006 | 0.45 | 5.8 | 37 | 99 | 28.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-11-24 10:38 | 60.6 | 42.8 | 0 | 0 | -11.4 | 11.4 | 1006 | 18.84 | 82 | 520 | 90 | 31.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-11-24 10:36 | 60.3 | 43 | 0 | 0 | -2.4 | 2.4 | 1006 | 28.2 | 46.6 | 295 | 99 | 31.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-11-24 10:33 | 55 | 38.5 | 0.4 | 6.1 | -1.4 | 1.4 | 1006 | 2.64 | 14.3 | 82 | 25 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-11-24 10:32 | 55.1 | 38.5 | 0 | 6.4 | -0.1 | 0.1 | 1006 | 0.59 | 6.8 | 39 | 22 | 28.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-11-24 10:30 | 57 | 39.3 | 0 | 3.7 | -0.2 | 0.2 | 1006 | 1.23 | 9.8 | 58 | 25 | 28.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-11-24 10:27 | 53.7 | 38.1 | 0 | 8.2 | -0.9 | 0.9 | 1006 | 4.02 | 17.7 | 99 | 40 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-11-24 10:26 | 38.6 | 30.9 | 2.5 | 28 | -0.6 | 0.6 | 1006 | 2.26 | 13.1 | 53 | 20 | 28.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-11-24 10:23 | 41.3 | 32 | 2.1 | 24.6 | -0.2 | 0.2 | 1006 | 1.44 | 10.5 | 45 | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-11-24 10:21 | 47.3 | 35.4 | 0.1 | 17.2 | -0.9 | 0.9 | 1005 | 4.64 | 18.9 | 93 | 40 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-11-24 10:15 | 51.6 | 33 | 3.2 | 12.2 | 0 | 0 | 1005 | -0.09 | 0 | 0 | 0 | 27.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-11-24 10:14 | 54.4 | 38.1 | 0 | 7.5 | -6.2 | 6.2 | 1005 | 16.94 | 36 | 205 | 40 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-11-24 10:12 | 55.3 | 38.6 | 0 | 6.1 | -4.6 | 4.6 | 1005 | 8.91 | 56.2 | 326 | 50 | 34.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-11-24 10:11 | 50.8 | 38.3 | 0 | 10.9 | -1.9 | 1.9 | 1005 | 8.02 | 24.4 | 130 | 40 | 38.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-11-24 10:10 | 49.2 | 37.5 | 0.5 | 12.8 | -41.9 | 41.9 | 1005 | 0.38 | 5.2 | 27 | 20 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-11-24 10:08 | 61.4 | 39.7 | 0 | 0 | -8.6 | 8.6 | 1005 | 0.58 | 14.6 | 93 | 25 | 28 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-11-24 10:07 | 52.1 | 37.7 | 0 | 10.2 | -11.3 | 11.3 | 1005 | 14.54 | 33.1 | 181 | 40 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-11-24 10:06 | 57.1 | 37.6 | 1.1 | 4.2 | -8.3 | 8.3 | 1005 | 0.91 | 8.5 | 51 | 10 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-11-24 10:04 | 56.1 | 38.2 | 0 | 5.7 | -10.6 | 10.6 | 1005 | 16.87 | 36.3 | 213 | 40 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-11-24 10:03 | 51.8 | 38 | 0 | 10.2 | -1.2 | 1.2 | 1005 | 13.28 | 15.9 | 86 | 20 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-11-24 10:02 | 49.8 | 38.1 | 0 | 12.1 | -2.7 | 2.7 | 1005 | 13.08 | 31.2 | 163 | 40 | 35.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-11-24 09:15 | 56.6 | 39.9 | 0 | 3.5 | -57.1 | 57.1 | 1003 | 1.09 | 19.4 | 115 | 99 | 27.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-11-24 09:13 | 52.2 | 38.5 | 0 | 9.3 | -22.2 | 22.2 | 1003 | 3.33 | 15.9 | 87 | 40 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-11-24 09:12 | 55.3 | 38.3 | 0.7 | 5.7 | -57.3 | 57.3 | 1003 | 1.33 | 9.9 | 57 | 99 | 25.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-11-24 09:10 | 51.4 | 36.3 | 0 | 12.3 | -9.3 | 9.3 | 1003 | 5 | 19.7 | 106 | 5 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-11-24 09:09 | 44.5 | 37.6 | 0 | 17.9 | -3.4 | 3.4 | 1003 | 10.83 | 28.1 | 131 | 40 | 37.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-11-24 09:07 | 53.1 | 38.5 | 1.8 | 6.6 | -6.3 | 6.3 | 1003 | 1.24 | 9.8 | 54 | 20 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-11-24 09:05 | 51.4 | 37.9 | 0.9 | 9.8 | -2.7 | 2.7 | 1003 | 1.17 | 9.5 | 51 | 15 | 25.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-11-24 09:04 | 56.8 | 40.7 | 0 | 2.5 | -23.1 | 23.1 | 1003 | 27.68 | 98.7 | 587 | 99 | 30.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-11-24 09:03 | 46.5 | 37.5 | 0 | 16 | -1.5 | 1.5 | 1003 | 5.87 | 20.9 | 102 | 25 | 32.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-11-24 09:01 | 49.1 | 38.9 | 0 | 12 | -4.9 | 4.9 | 1003 | 1.7 | 24.4 | 125 | 20 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-11-24 08:59 | 50.1 | 36.5 | 0 | 13.4 | -25.5 | 25.5 | 1003 | 1.8 | 24.8 | 130 | 40 | 36.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-11-24 08:58 | 47.4 | 36 | 0 | 16.6 | -5.3 | 5.3 | 1003 | 3.79 | 36.5 | 181 | 40 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-11-24 08:57 | 37.2 | 29.1 | 4.9 | 28.8 | -43.3 | 43.3 | 1003 | -0.06 | 0 | 0 | 70 | 24.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-11-24 08:55 | 38.3 | 32.3 | 1.7 | 27.7 | -0.3 | 0.3 | 1003 | 0.25 | 9.5 | 38 | 10 | 24.9 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-11-24 08:54 | 51.6 | 39.2 | 0 | 9.2 | -43.5 | 43.5 | 1004 | 0.7 | 25.2 | 136 | 99 | 30 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-11-24 08:44 | 57.8 | 41.1 | 0 | 1.1 | -0.2 | 0.2 | 1004 | 1.61 | 11 | 66 | 30 | 38.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-11-24 08:41 | 43.4 | 36.6 | 0 | 20 | -1 | 1 | 1004 | 1.16 | 19.8 | 90 | 40 | 39.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-11-24 08:39 | 52.9 | 39.3 | 0 | 7.8 | -1.1 | 1.1 | 1004 | 2.79 | 7.3 | 40 | 10 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-11-24 08:38 | 59.3 | 40.6 | 0 | 0.1 | -0.7 | 0.7 | 1004 | 0.35 | 11.3 | 70 | 20 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-11-24 08:37 | 55.5 | 41.7 | 0.6 | 2.2 | -43.7 | 43.7 | 1004 | 1.16 | 9.1 | 53 | 70 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-11-24 08:35 | 15.5 | 11.1 | 13.6 | 59.8 | -45.1 | 45.1 | 1004 | -0.15 | 0 | 0 | 99 | 22.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-11-24 08:33 | 46.9 | 33.7 | 3.7 | 15.7 | -0.7 | 0.7 | 1004 | 0.28 | 4.6 | 22 | 10 | 23.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-11-24 08:32 | 53.6 | 40.4 | 0 | 6 | -4.2 | 4.2 | 1004 | 2.95 | 15 | 84 | 25 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-11-24 08:30 | 51.5 | 40.1 | 0.1 | 8.3 | -0.7 | 0.7 | 1004 | 3.53 | 8.1 | 44 | 20 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-11-24 08:28 | 0.2 | 0.2 | 19.9 | 79.7 | -4 | 4 | 1004 | -0.01 | 0 | 0 | 0 | 24.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-11-24 08:27 | 59.8 | 40.7 | 0 | 0 | -45.3 | 45.3 | 1004 | 0.18 | 3.7 | 23 | 99 | 24.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-11-24 08:26 | 10.7 | 6.9 | 16.1 | 66.3 | -24.5 | 24.5 | 1004 | 0.11 | 1.4 | 1 | 2 | 23.9 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2017-11-24 08:24 | 54.3 | 39.1 | 1.2 | 5.4 | -4 | 4 | 1004 | 2.26 | 13.2 | 75 | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-11-24 08:22 | 54.4 | 41.9 | 0.2 | 3.5 | -0.6 | 0.6 | 1004 | 0.93 | 8.4 | 48 | 20 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-11-23 14:38 | 28.5 | 29.2 | 1.2 | 41.1 | 0 | 0 | 999 | 0.07 | 2.3 | 6 | 5 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-11-23 14:37 | 50.9 | 37.6 | 0 | 11.5 | -15.3 | 15.3 | 1000 | 7.57 | 51.2 | 273 | 50 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-11-23 14:36 | 46 | 35.4 | 0.4 | 18.2 | -1.8 | 1.8 | 1000 | 0.98 | 18.3 | 88 | 40 | 38.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-11-23 14:34 | 48.1 | 36 | 0 | 15.9 | -4.2 | 4.2 | 1000 | 1.93 | 25.9 | 130 | 40 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-11-23 14:33 | 40 | 33.4 | 0 | 26.6 | -56.9 | 56.9 | 1000 | 1.21 | 20 | 83 | 40 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-11-23 14:32 | 37.8 | 27.5 | 5.5 | 29.2 | -2.8 | 2.8 | 1000 | 7.28 | 23.6 | 93 | 20 | 28.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-11-23 14:30 | 49.3 | 37.7 | 0.3 | 12.7 | -0.3 | 0.3 | 1000 | 7.44 | 5.9 | 30 | 15 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-11-23 14:29 | 48.9 | 37.1 | 0 | 14 | -0.8 | 0.8 | 1000 | 1.58 | 5.4 | 27 | 15 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-11-23 14:28 | 59.4 | 41.1 | 0 | 0 | 0 | 0 | 1000 | 0.73 | 1.9 | 11 | 7 | 28.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-11-23 14:18 | 42.1 | 34.3 | 0.6 | 23 | -15.5 | 15.5 | 1000 | 14.54 | 69.2 | 305 | 65 | 44.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-11-23 14:15 | 54.8 | 40.4 | 0 | 4.8 | -42.8 | 42.8 | 1000 | 0.07 | 8 | 46 | 90 | 29.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-11-23 14:14 | 45.2 | 37.1 | 0 | 17.7 | -2.6 | 2.6 | 1000 | 7.78 | 5.9 | 28 | 20 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-11-23 14:13 | 50.9 | 38.3 | 0 | 10.8 | -1.5 | 1.5 | 1000 | 0.62 | 14.9 | 79 | 25 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-11-23 14:11 | 45.4 | 35.9 | 0.2 | 18.5 | -5.2 | 5.2 | 1000 | 1.54 | 23.3 | 111 | 35 | 28.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-11-23 14:10 | 31.3 | 30.2 | 0.7 | 37.8 | -1.8 | 1.8 | 1000 | 1.15 | 19.9 | 65 | 15 | 28 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-11-23 14:08 | 15.9 | 10.5 | 11 | 62.6 | -0.6 | 0.6 | 1000 | -0.02 | 0 | 0 | 0 | 24.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-11-23 14:07 | 33.8 | 30.7 | 0.3 | 35.2 | -1.1 | 1.1 | 1000 | 0.03 | 3.2 | 11 | 5 | 30 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-11-23 14:05 | 50.2 | 37.6 | 0.1 | 12.1 | -0.8 | 0.8 | 999 | 1.01 | 18.6 | 98 | 25 | 40.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-11-23 14:04 | 48.8 | 38.2 | 0.1 | 12.9 | -21.8 | 21.8 | 999 | 17.8 | 77.2 | 395 | 80 | 39.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-11-23 14:02 | 46.3 | 37.5 | 0 | 16.2 | -0.7 | 0.7 | 1000 | 0.16 | 7.3 | 35 | 10 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-11-23 14:01 | 40.5 | 33.8 | 0.7 | 25 | -1.7 | 1.7 | 999 | 5.34 | 20 | 85 | 25 | 29.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-11-23 13:58 | 57.9 | 43 | 0 | 0 | 0.1 | -0.1 | 999 | 0.88 | 8.2 | 50 | 22 | 28.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-11-23 13:55 | 41.4 | 34.7 | 0 | 23.9 | -6.8 | 6.8 | 999 | 7.52 | 23.7 | 103 | 22 | 28.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-11-23 13:54 | 53.3 | 39.6 | 1.1 | 6 | -0.1 | 0.1 | 999 | 2.02 | 12.4 | 69 | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-11-23 13:52 | 43.2 | 36.3 | 0 | 20.5 | 0 | 0 | 999 | 0.59 | 6.7 | 30 | 10 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-11-23 13:51 | 57.5 | 41 | 0.1 | 1.4 | -15 | 15 | 999 | 0.85 | 8 | 48 | 20 | 27.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-11-23 13:49 | 48.6 | 37.6 | 0.3 | 13.5 | -3.6 | 3.6 | 999 | 1.45 | 36.9 | 188 | 40 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-11-23 13:48 | 58 | 41.5 | 0 | 0.5 | -0.7 | 0.7 | 999 | 6.12 | 10.8 | 65 | 20 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-11-23 13:47 | 53.4 | 38.9 | 0.3 | 7.4 | -4.8 | 4.8 | 999 | 8.7 | 25.7 | 144 | 40 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-11-23 13:36 | 58.5 | 41.3 | 0.2 | 0 | -1.6 | 1.6 | 998 | -0.03 | 0 | 0 | 0 | 36.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-11-23 13:35 | 56.2 | 41.6 | 0 | 2.2 | -54.5 | 54.5 | 998 | 0.7 | 24.8 | 146 | 99 | 38.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-11-23 13:34 | 51.3 | 39.2 | 0.1 | 9.4 | -0.5 | 0.5 | 998 | 8.16 | 24.6 | 132 | 25 | 39.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-11-23 13:32 | 48.8 | 37 | 0 | 14.2 | -0.3 | 0.3 | 998 | 12.14 | 15.1 | 77 | 20 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-11-23 13:31 | 53.7 | 41.2 | 0.2 | 4.9 | -1.7 | 1.7 | 999 | 15.37 | 8.5 | 48 | 15 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-11-23 13:29 | 52.2 | 41.2 | 0.1 | 6.5 | -40.4 | 40.4 | 999 | 6.75 | 21.4 | 117 | 70 | 51.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-11-23 13:28 | 52.5 | 40 | 0.4 | 7.1 | -9 | 9 | 999 | 1.36 | 21.5 | 118 | 20 | 39 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-11-23 13:26 | 57.1 | 41.9 | 0 | 1 | -16 | 16 | 999 | 14.13 | 31.8 | 190 | 50 | 47 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-11-23 13:25 | 48.9 | 37.7 | 2.7 | 10.7 | -38.8 | 38.8 | 999 | 4.45 | 4.5 | 23 | 20 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-11-23 13:24 | 33.2 | 33.1 | 0.2 | 33.5 | -1.2 | 1.2 | 1001 | 8.45 | 1.3 | 4 | 5 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-11-23 11:41 | 58 | 41.2 | 0 | 0.8 | 0 | 0 | 1000 | 1.67 | 24.2 | 147 | 50 | 37.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-11-23 11:37 | 0.7 | 1.5 | 18.8 | 79 | 0 | 0 | 1000 | -0.01 | 0 | 0 | 0 | 33.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-11-23 11:36 | 57.6 | 41.3 | 0.1 | 1 | -28.2 | 28.2 | 1000 | 0.23 | 8.9 | 54 | 5 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-11-23 11:35 | 1.2 | 1.9 | 15.9 | 81 | 0 | 0 | 1000 | 0.03 | 3.2 | 0 | 0 | 32.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-11-23 11:33 | 1.5 | 3.2 | 17.7 | 77.6 | 0.1 | -0.1 | 1000 | 0.03 | 1.5 | 0 | 0 | 35.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-11-23 11:31 | 53.4 | 39.2 | 0 | 7.4 | -2.8 | 2.8 | 1000 | 7 | 22.9 | 128 | 25 | 37.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-11-23 11:30 | 50.1 | 37.6 | 1.4 | 10.9 | -34.1 | 34.1 | 1000 | 4.4 | 61.7 | 324 | 60 | 47.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-11-23 11:29 | 46.1 | 36.9 | 0 | 17 | -1.1 | 1.1 | 1000 | 1.42 | 10.2 | 49 | 15 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-11-23 11:28 | 2.2 | 1.7 | 18.9 | 77.2 | -2.6 | 2.6 | 1000 | 0.03 | 1.3 | 0 | 0 | 35.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-11-23 11:27 | 51.7 | 38.1 | 0.1 | 10.1 | -48.8 | 48.8 | 1000 | 1.25 | 33.3 | 181 | 70 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-11-23 11:25 | 40.7 | 34.9 | 0 | 24.4 | -0.8 | 0.8 | 1000 | 18.42 | 35.9 | 153 | 40 | 51.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-11-23 11:15 | 59 | 39.4 | 0 | 1.6 | 0 | 0 | 1002 | -0.06 | 0 | 0 | 20 | 36.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-11-23 11:13 | 53.6 | 34.2 | 1.9 | 10.3 | 0.3 | -0.3 | 1003 | -0.01 | 0 | 0 | 20 | 36.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-11-23 11:11 | 34.9 | 19.4 | 8.6 | 37.1 | 0.4 | -0.4 | 1002 | 0.01 | 0.7 | 2 | 40 | 36 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-11-23 11:08 | 59.6 | 39.7 | 0 | 0.7 | 1.1 | -1.1 | 1002 | 0.04 | 3.7 | 23 | 99 | 39.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-11-23 11:06 | 58.5 | 39.9 | 0 | 1.6 | -14.4 | 14.4 | 1002 | 0.31 | 10.4 | 63 | 20 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-11-23 11:05 | 48.9 | 33.6 | 0.9 | 16.6 | -2.3 | 2.3 | 1002 | 1.65 | 11.2 | 57 | 20 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-11-23 11:04 | 48.7 | 34.8 | 0.3 | 16.2 | -0.3 | 0.3 | 1002 | 19.31 | 9.7 | 49 | 20 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-11-23 11:02 | 50.1 | 37.2 | 0.4 | 12.3 | -9.8 | 9.8 | 1002 | 0.65 | 15.1 | 79 | 20 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-11-23 11:01 | 56.3 | 38.3 | 0 | 5.4 | -13.6 | 13.6 | 1003 | 3.09 | 15.3 | 90 | 25 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-11-23 11:00 | 47.9 | 35.1 | 1.4 | 15.6 | -4.1 | 4.1 | 1002 | 0.98 | 30.2 | 151 | 40 | 35.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-11-23 10:59 | 56.9 | 39.9 | 0 | 3.2 | -0.3 | 0.3 | 1003 | 5.34 | 20.2 | 120 | 25 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-11-23 10:57 | 58.1 | 40.3 | 0 | 1.6 | -43.7 | 43.7 | 1003 | 7.39 | 49.8 | 303 | 99 | 40.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-11-23 10:56 | 56.8 | 38.2 | 0 | 5 | -15 | 15 | 1003 | 0.89 | 17.8 | 105 | 40 | 34.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-11-23 10:55 | 42.8 | 33.2 | 1.2 | 22.8 | -18.2 | 18.2 | 1003 | 0.61 | 6.6 | 29 | 20 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-11-23 10:53 | 51.5 | 37.9 | 0.1 | 10.5 | -0.1 | 0.1 | 1003 | 0.29 | 4.7 | 25 | 5 | 33 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-11-23 10:52 | 56.6 | 38.8 | 0 | 4.6 | -3.6 | 3.6 | 1003 | 3.95 | 37.6 | 223 | 40 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-11-23 10:51 | 57.8 | 36.3 | 0 | 5.9 | -1.7 | 1.7 | 1003 | 0.2 | 1.9 | 11 | 5 | 35.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-11-23 10:50 | 25.1 | 26.8 | 0.4 | 47.7 | -0.9 | 0.9 | 1003 | 19.39 | 2 | 5 | 5 | 33.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-11-23 10:48 | 33.5 | 26.1 | 4 | 36.4 | -33.9 | 33.9 | 1003 | 1.41 | 10.1 | 35 | 20 | 31.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-11-23 10:46 | 51.1 | 35.2 | 0 | 13.7 | -19.7 | 19.7 | 1003 | 8.74 | 55.7 | 298 | 50 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-11-23 10:45 | 51.4 | 31.8 | 2.2 | 14.6 | -1.9 | 1.9 | 1003 | 3.38 | 8.1 | 43 | 20 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-11-23 10:44 | 63.1 | 36.5 | 0 | 0.4 | -7.9 | 7.9 | 1003 | 11.28 | 1.6 | 10 | 15 | 36.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-11-23 10:42 | 39.1 | 31.6 | 0 | 29.3 | -49.8 | 49.8 | 1003 | 0.78 | 16 | 65 | 50 | 35 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-11-23 09:31 | 48.3 | 33.6 | 2.6 | 15.5 | -29.4 | 29.4 | 1000 | 0.3 | 16.6 | 84 | 5 | 31.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-11-23 09:29 | 50.1 | 37.4 | 0.4 | 12.1 | -2.4 | 2.4 | 1000 | 6.78 | 22.4 | 117 | 30 | 38.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-11-23 09:28 | 44.1 | 35.4 | 0 | 20.5 | -0.4 | 0.4 | 1000 | 1.49 | 2.6 | 12 | 5 | 36.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-11-23 09:27 | 52.9 | 38.6 | 0 | 8.5 | -44.8 | 44.8 | 1000 | 13.74 | 109.6 | 607 | 99 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-11-23 09:26 | 54.2 | 38.9 | 0 | 6.9 | -12.3 | 12.3 | 1000 | 9.71 | 58 | 329 | 50 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-11-23 09:24 | 56.8 | 41 | 0 | 2.2 | -28.9 | 28.9 | 1000 | 15.22 | 33.9 | 201 | 99 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-11-23 09:22 | 35.9 | 32.3 | 0 | 31.8 | -0.2 | 0.2 | 1000 | 0.35 | 11 | 41 | 2 | 29.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-11-23 09:21 | 42.3 | 29.8 | 5.1 | 22.8 | -9.5 | 9.5 | 1001 | 16.14 | 74.7 | 331 | 50 | 37.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-11-23 09:18 | 49.7 | 37.8 | 0.3 | 12.2 | -23.4 | 23.4 | 1000 | 1.23 | 32.5 | 169 | 50 | 52.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-11-23 09:16 | 19.1 | 19.4 | 6.8 | 54.7 | -0.3 | 0.3 | 1001 | 11.11 | 7.2 | 14 | 2 | 28.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-11-23 09:14 | 54.5 | 38.8 | 0.1 | 6.6 | -0.3 | 0.3 | 1000 | 0.33 | 5 | 29 | 5 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-11-23 09:12 | 46.9 | 38.1 | 0 | 15 | -0.3 | 0.3 | 1000 | 1.11 | 8.9 | 44 | 20 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-11-23 09:11 | 52.8 | 41.1 | 0 | 6.1 | -41 | 41 | 1000 | 11.51 | 7.1 | 39 | 99 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-11-23 09:10 | 43.3 | 36.7 | 0 | 20 | -2.4 | 2.4 | 1000 | 13.99 | 31.2 | 141 | 25 | 53.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-11-23 09:08 | 55.5 | 39.3 | 0 | 5.2 | -26.9 | 26.9 | 1001 | 15.7 | 117.5 | 683 | 80 | 50.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-11-23 09:06 | 53.1 | 40.9 | 0 | 6 | -0.3 | 0.3 | 1001 | 4.36 | 8.9 | 49 | 15 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-11-23 09:05 | 49.3 | 37.9 | 0 | 12.8 | -1.8 | 1.8 | 1001 | 1.55 | 23.1 | 119 | 25 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-11-23 09:02 | 40.9 | 35.5 | 1.8 | 21.8 | -0.2 | 0.2 | 1001 | 12.24 | 1.6 | 7 | 5 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-11-23 08:53 | 49 | 37.9 | 0.2 | 12.9 | -2.3 | 2.3 | 1002 | 7.62 | 24 | 123 | 40 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-11-23 08:52 | 1 | 1.7 | 19.2 | 78.1 | -0.2 | 0.2 | 1002 | 0.03 | 1.4 | 0 | 0 | 28.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-11-23 08:50 | 57.3 | 41.2 | 0.7 | 0.8 | -0.8 | 0.8 | 1002 | 0.04 | 0.8 | 5 | 5 | 30.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-11-23 08:49 | 0.3 | 0.2 | 19.8 | 79.7 | 0 | 0 | 1002 | 0.01 | 1 | 0 | 0 | 29.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-11-23 08:47 | 58 | 43.7 | 0 | 0 | -8.4 | 8.4 | 1002 | 0.41 | 5.5 | 33 | 5 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-11-23 08:46 | 40.1 | 36.7 | 0.2 | 23 | -2.3 | 2.3 | 1002 | 10.92 | 14 | 59 | 20 | 31 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-11-23 08:43 | 51.3 | 38.3 | 0.2 | 10.2 | -26.3 | 26.3 | 1002 | 14.13 | 70.1 | 377 | 70 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-11-23 08:42 | 22.1 | 13.8 | 10.4 | 53.7 | 0.5 | -0.5 | 1002 | 0 | 1.1 | 2 | 5 | 25.9 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-11-23 08:39 | 48.8 | 40 | 0 | 11.2 | -1.1 | 1.1 | 1002 | 0.77 | 16.4 | 84 | 25 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-11-23 08:37 | 50.8 | 40.4 | 0 | 8.8 | -2.8 | 2.8 | 1002 | 0.58 | 14.3 | 76 | 20 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-11-23 08:34 | 46 | 37.4 | 1.3 | 15.3 | -3.2 | 3.2 | 1002 | 1.81 | 25.2 | 121 | 22 | 27.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-11-23 08:30 | 38.7 | 34.1 | 1.7 | 25.5 | -4.9 | 4.9 | 1002 | 2.81 | 31 | 126 | 35 | 30.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-11-23 08:28 | 45.2 | 37.2 | 1.9 | 15.7 | -2.4 | 2.4 | 1002 | 0.48 | 12.8 | 60 | 20 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-11-23 08:26 | 33.8 | 35.3 | 0.2 | 30.7 | -1.2 | 1.2 | 1002 | 1.63 | 10.8 | 38 | 15 | 28.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-11-23 08:23 | 46 | 38 | 1.3 | 14.7 | -0.2 | 0.2 | 1002 | 0.93 | 8.3 | 40 | 15 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-11-22 11:52 | 54.2 | 39.4 | 0 | 6.4 | -29.7 | 29.7 | 1009 | 18 | 76.7 | 436 | 99 | 49.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-11-22 11:51 | 56.7 | 40.4 | 0 | 2.9 | -36.7 | 36.7 | 1009 | 7.8 | 50.9 | 302 | 99 | 43.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-11-22 11:50 | 55.9 | 39.5 | 0 | 4.6 | -34.2 | 34.2 | 1009 | 10.56 | 97 | 567 | 99 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-11-22 11:49 | 44.3 | 33.5 | 0 | 22.2 | -0.8 | 0.8 | 1009 | -0.24 | 0 | 0 | 0 | 45.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-11-22 11:48 | 46.7 | 35.1 | 1.1 | 17.1 | -27.6 | 27.6 | 1009 | 18.3 | 77 | 377 | 99 | 50.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-11-22 11:46 | 57.8 | 41 | 0 | 1.2 | -32.5 | 32.5 | 1009 | 0.04 | 3.4 | 21 | 20 | 40.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-11-22 11:45 | 9.4 | 5.7 | 16.7 | 68.2 | -18 | 18 | 1009 | -0.29 | 0 | 0 | 0 | 35.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-11-22 11:44 | 45.3 | 36.8 | 0 | 17.9 | -3.2 | 3.2 | 1009 | 5.96 | 21 | 99 | 40 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-11-22 11:42 | 54.2 | 39.3 | 0 | 6.5 | -2.5 | 2.5 | 1009 | 1.63 | 23.8 | 135 | 25 | 39.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-11-22 11:41 | 56.8 | 42.5 | 0 | 0.7 | -41 | 41 | 1009 | 5.4 | 42.1 | 251 | 70 | 42.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-11-22 11:40 | 51.2 | 38.3 | 0.2 | 10.3 | -19.4 | 19.4 | 1009 | -0.14 | 0 | 0 | 0 | 36.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-11-22 11:38 | 40.3 | 28.4 | 4.8 | 26.5 | -21.3 | 21.3 | 1009 | -0.21 | 0 | 0 | 0 | 36.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-11-22 11:36 | 56.4 | 42.6 | 0 | 1 | -39.5 | 39.5 | 1009 | -0.11 | 0 | 0 | 10 | 37.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-11-22 11:35 | 57.2 | 40.7 | 0 | 2.1 | -42.5 | 42.5 | 1009 | 4.69 | 64.2 | 385 | 99 | 44.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-11-22 11:33 | 50.2 | 37.9 | 0 | 11.9 | -5.8 | 5.8 | 1009 | 10.31 | 27.9 | 146 | 40 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-11-22 11:32 | 48.2 | 37.3 | 0 | 14.5 | -6.3 | 6.3 | 1009 | 12.36 | 30.3 | 153 | 40 | 36.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-11-22 11:31 | 51.5 | 39.2 | 0 | 9.3 | -7.2 | 7.2 | 1009 | 2.19 | 27.7 | 149 | 40 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-11-22 11:30 | 57.1 | 41 | 0 | 1.9 | -18.9 | 18.9 | 1008 | 1.04 | 19 | 113 | 20 | 33.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2017-11-22 11:27 | 56.9 | 41.4 | 0 | 1.7 | -50.6 | 50.6 | 1008 | -0.05 | 0 | 0 | 99 | 38.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2017-11-22 11:25 | 6.8 | 4.2 | 17 | 72 | -51.7 | 51.7 | 1008 | -0.13 | 0 | 0 | 99 | 38.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-11-22 11:24 | 58 | 41.3 | 0 | 0.7 | -49.8 | 49.8 | 1008 | 2.91 | 50.6 | 307 | 99 | 42.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-11-22 11:23 | 41.8 | 31 | 3.8 | 23.4 | -52.3 | 52.3 | 1008 | -0.05 | 0 | 0 | 99 | 36.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-11-22 11:21 | 7.5 | 20 | 1.8 | 70.7 | 0 | 0 | 1008 | 0.01 | 0.9 | 0 | 0 | 38 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-11-22 11:19 | 49.3 | 38 | 0 | 12.7 | -0.6 | 0.6 | 1008 | 14.11 | 8.1 | 42 | 20 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-11-22 11:18 | 41.5 | 32.2 | 1.7 | 24.6 | -1.9 | 1.9 | 1008 | 1.75 | 24.4 | 106 | 20 | 42.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-11-22 11:16 | 55.2 | 40.5 | 0 | 4.3 | -50.6 | 50.6 | 1008 | 0.35 | 10.5 | 61 | 99 | 47.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2017-11-22 11:15 | 0.2 | 0.2 | 20 | 79.6 | -43.6 | 43.6 | 1008 | -0.08 | 0 | 0 | 0 | 38.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-11-22 11:13 | 52.8 | 38 | 0 | 9.2 | -53.1 | 53.1 | 1007 | -0.02 | 0 | 0 | 25 | 37.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2017-11-22 10:39 | 58.1 | 48 | 0 | 0 | 0.6 | -0.6 | 1009 | 0.59 | 14.1 | 86 | 50 | 36.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2017-11-22 10:38 | 47.8 | 59.1 | 0 | 0 | -1.4 | 1.4 | 1008 | 0.72 | 14.8 | 74 | 25 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2017-11-22 10:37 | 63.9 | 47.5 | 0 | 0 | 0.3 | -0.3 | 1008 | 0.27 | 9.6 | 64 | 35 | 35.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2017-11-22 10:35 | 59.2 | 48.9 | 0 | 0 | 0 | 0 | 1008 | 0.22 | 8.6 | 53 | 50 | 35.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2017-11-22 10:34 | 51.5 | 55.5 | 0 | 0 | -12.7 | 12.7 | 1009 | 0.05 | 4 | 22 | 5 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-11-22 10:30 | 60.4 | 38.2 | 0 | 1.4 | -0.6 | 0.6 | 1009 | 5.72 | 21.4 | 135 | 60 | 28.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-11-22 10:27 | 64.4 | 33.8 | 0 | 1.8 | -39.5 | 39.5 | 1009 | 3.59 | 16.9 | 114 | 99 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-11-22 10:25 | 59.4 | 37.3 | 0 | 3.3 | -4.4 | 4.4 | 1009 | 16.76 | 36.5 | 227 | 50 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-11-22 10:24 | 58.6 | 39.8 | 0 | 1.6 | -0.5 | 0.5 | 1009 | 10.45 | 28.3 | 174 | 99 | 36.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-11-22 10:21 | 57.6 | 36.7 | 0 | 5.7 | -3.2 | 3.2 | 1009 | 10.21 | 28.3 | 170 | 40 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-11-22 10:20 | 57.2 | 36.9 | 0 | 5.9 | -10 | 10 | 1009 | 5.46 | 20.6 | 124 | 25 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-11-22 10:19 | 55.7 | 36.1 | 0 | 8.2 | -3.9 | 3.9 | 1008 | 4.67 | 19.1 | 112 | 20 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-11-22 10:16 | 57.8 | 38.8 | 0 | 3.4 | -2.5 | 2.5 | 1008 | 1.75 | 25.2 | 152 | 25 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-11-22 10:15 | 57.9 | 40.1 | 0 | 2 | 0 | 0 | 1008 | 0.06 | 4.7 | 28 | 22 | 30.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-11-22 10:13 | 58 | 40.2 | 0 | 1.8 | -0.1 | 0.1 | 1008 | 1.25 | 9.8 | 59 | 20 | 34 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-11-22 10:12 | 58.7 | 39.3 | 0 | 2 | 0 | 0 | 1008 | 0.12 | 1.4 | 9 | 10 | 39 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-11-22 10:11 | 56.8 | 42 | 0 | 1.2 | -80.7 | 80.7 | 1008 | 0.21 | 8.2 | 49 | 70 | 39.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-11-21 14:46 | 59.6 | 43 | 0 | 0 | -30.5 | 30.5 | 1012 | 18.81 | 128.9 | 805 | 99 | 46.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-11-21 14:45 | 50.4 | 38.8 | 0 | 10.8 | -2.9 | 2.9 | 1012 | 11.4 | 28.9 | 152 | 40 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-11-21 14:44 | 52.2 | 39.3 | 0 | 8.5 | -26.1 | 26.1 | 1011 | 20.72 | 82.9 | 454 | 99 | 43.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-11-21 14:43 | 51 | 40.2 | 0 | 8.8 | -17.5 | 17.5 | 1011 | 18.42 | 36.4 | 194 | 50 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-11-21 14:41 | 59 | 43.6 | 0 | 0 | -41 | 41 | 1011 | 2.17 | 26.5 | 164 | 99 | 47.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-11-21 14:40 | 59.1 | 43.6 | 0 | 0 | -6.8 | 6.8 | 1012 | 0.06 | 2 | 12 | 20 | 37.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-11-21 14:38 | 45.9 | 38.1 | 0 | 16 | -3.4 | 3.4 | 1011 | 15.26 | 33.2 | 160 | 40 | 40.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-11-21 14:28 | 57.9 | 43 | 0 | 0 | -14.7 | 14.7 | 1011 | 7.97 | 84.6 | 513 | 70 | 44.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-11-21 14:27 | 45.8 | 35.1 | 4.7 | 14.4 | -45.2 | 45.2 | 1011 | -0.21 | 0 | 0 | 99 | 36.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2017-11-21 07:50 | 56.8 | 41.7 | 0 | 1.5 | -3.7 | 3.7 | 1012 | 7.16 | 11.8 | 70 | 25 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2017-11-21 07:47 | 49.9 | 39.3 | 0.2 | 10.6 | -45.8 | 45.8 | 1012 | 11.25 | 29 | 152 | 40 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2017-11-21 07:43 | 59.5 | 40.3 | 0 | 0.2 | -2.6 | 2.6 | 1011 | 26.21 | 22.8 | 142 | 40 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2017-11-21 07:41 | 61.1 | 38.9 | 0 | 0 | -2.9 | 2.9 | 1011 | 15.22 | 17.5 | 112 | 35 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2017-11-20 13:53 | 39.7 | 31.1 | 0.2 | 29 | 0 | 0 | 1017 | 0.06 | 1.1 | 4 | 5 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2017-11-20 13:51 | 6.4 | 4 | 16.6 | 73 | -43.9 | 43.9 | 1016 | 0.07 | 2.2 | 1 | 2 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2017-11-20 13:48 | 0.4 | 0 | 19.9 | 79.7 | -44.6 | 44.6 | 1016 | 0.02 | 1.2 | 0 | 2 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2017-11-20 13:45 | 58.4 | 39.4 | 0 | 2.2 | 0.2 | -0.2 | 1016 | 0.16 | 1.7 | 10 | 10 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-11-20 13:41 | 46.6 | 35.3 | 0 | 18.1 | -4.6 | 4.6 | 1016 | 8.04 | 25.2 | 123 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2017-11-20 13:38 | 58.3 | 39.1 | 0.2 | 2.4 | -45 | 45 | 1016 | 5.53 | 20.7 | 127 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2017-11-20 13:35 | 2.3 | 1.3 | 19.5 | 76.9 | -45.2 | 45.2 | 1016 | 0.14 | 3.2 | 0 | 2 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2017-11-20 13:31 | 58.9 | 38.5 | 0 | 2.6 | -1.5 | 1.5 | 1016 | 19.92 | 20 | 123 | 40 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-11-20 13:29 | 58.5 | 39.7 | 0 | 1.8 | 0.1 | -0.1 | 1016 | -0.09 | 0 | 0 | 10 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2017-11-20 13:22 | 0.9 | 0.5 | 20 | 78.6 | -44.3 | 44.3 | 1016 | 0.32 | 17 | 1 | 2 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2017-11-20 13:19 | 0.3 | 0 | 20.2 | 79.5 | -45.4 | 45.4 | 1016 | 0.43 | 19.8 | 0 | 2 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2017-11-20 13:16 | 61.6 | 37.7 | 0 | 0.7 | -1.2 | 1.2 | 1016 | 10.53 | 14.6 | 94 | 25 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2017-11-20 13:12 | 0.3 | 0.1 | 20.7 | 78.9 | -45.9 | 45.9 | 1016 | 0.03 | 5.1 | 0 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2017-11-20 13:10 | 57.4 | 39.2 | 0.4 | 3 | -48.3 | 48.3 | 1016 | 7.41 | 83.4 | 501 | 99 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-10-26 17:24 | 44.5 | 35.3 | 0.7 | 19.5 | -5.3 | 5.3 | 999 | 12.91 | 31.7 | 148 | 35 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-10-26 17:22 | 50.4 | 38.6 | 0 | 11 | -19.3 | 19.3 | 999 | 21.02 | 40.3 | 213 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-10-26 17:20 | 25.9 | 28.7 | 0 | 45.4 | -2.1 | 2.1 | 999 | 1.31 | 9.9 | 27 | 10 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-10-26 17:18 | 43.6 | 36.4 | 0 | 20 | -3.8 | 3.8 | 999 | 19.15 | 38.5 | 176 | 40 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-10-26 17:16 | 56.1 | 40.9 | 0 | 3 | -23 | 23 | 1000 | 31.54 | 107 | 629 | 99 | 20 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-10-26 17:12 | 56 | 38.2 | 0 | 5.8 | -6.8 | 6.8 | 1000 | 18.87 | 39 | 229 | 55 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-10-26 17:10 | 56.5 | 38.4 | 0 | 5.1 | -5.6 | 5.6 | 1001 | 10.95 | 64.1 | 379 | 55 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-10-26 17:08 | 48.5 | 37.6 | 0 | 13.9 | -3.1 | 3.1 | 1001 | 15.36 | 34.7 | 176 | 38 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-10-26 17:06 | 45 | 36.4 | 0.2 | 18.4 | -9.3 | 9.3 | 1001 | 7.38 | 23.9 | 112 | 27 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-10-26 17:04 | 55.7 | 37.7 | 0 | 6.6 | -11.8 | 11.8 | 1001 | 19.29 | 39.3 | 229 | 45 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-10-26 17:02 | 53.8 | 38.3 | 0 | 7.9 | -1.3 | 1.3 | 1001 | 14.37 | 16.8 | 95 | 25 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-10-26 17:01 | 47.3 | 37.5 | 0.1 | 15.1 | -3.2 | 3.2 | 1001 | 15.55 | 34.9 | 173 | 40 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-10-26 15:57 | 44.4 | 33.8 | 1.1 | 20.7 | -29.3 | 29.3 | 998 | 8.58 | 90.3 | 421 | 60 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-10-26 15:53 | 49.1 | 37 | 0 | 13.9 | -0.8 | 0.8 | 1000 | 16.59 | 78.1 | 402 | 17 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-10-26 15:49 | 49 | 37.2 | 0 | 13.8 | -5.1 | 5.1 | 999 | 4.64 | 41.2 | 211 | 43 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-10-26 15:47 | 59.7 | 41.7 | 0 | 0 | -33.7 | 33.7 | 999 | 0.7 | 7.3 | 46 | 25 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-10-26 15:45 | 56.8 | 42.1 | 0 | 1.1 | -0.2 | 0.2 | 1000 | 1.26 | 10 | 59 | 45 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-10-26 15:39 | 55.3 | 38.2 | 0 | 6.5 | -17.9 | 17.9 | 1000 | 2.24 | 13.3 | 77 | 35 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-10-26 15:37 | 54.2 | 36.6 | 0 | 9.2 | -5.8 | 5.8 | 1000 | 3.32 | 16.4 | 93 | 40 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-10-26 15:36 | 52.5 | 39.3 | 0 | 8.2 | -3.4 | 3.4 | 1000 | 10.8 | 29.2 | 161 | 40 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-10-26 15:34 | 55 | 37.7 | 1.4 | 5.9 | -5.5 | 5.5 | 1000 | 1.24 | 9.9 | 57 | 25 | 20 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-10-26 15:32 | 58.4 | 39.6 | 0 | 2 | -26.2 | 26.2 | 1000 | 20.59 | 87 | 532 | 90 | 20 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-10-26 15:30 | 52.3 | 38.3 | 0 | 9.4 | -1.1 | 1.1 | 1000 | 6.19 | 22.2 | 121 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-10-26 15:29 | 55.8 | 39.6 | 0.1 | 4.5 | -1.7 | 1.7 | 1000 | 0.68 | 15.9 | 93 | 28 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-10-26 15:09 | 59 | 37.1 | 0 | 3.9 | -15.1 | 15.1 | 1000 | 0.69 | 16.1 | 99 | 40 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-10-26 15:08 | 51.6 | 36 | 0 | 12.4 | -4.7 | 4.7 | 1000 | 4.03 | 38.7 | 209 | 40 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-10-26 15:06 | 44.3 | 32.9 | 1.5 | 21.3 | -0.8 | 0.8 | 1000 | 0.53 | 14 | 65 | 20 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-10-26 14:28 | 28.6 | 27.9 | 0.4 | 43.1 | -0.5 | 0.5 | 1000 | 0.91 | 8.3 | 24 | 5 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-10-26 14:27 | 45 | 33.9 | 0.2 | 20.9 | -2.3 | 2.3 | 1000 | 1.48 | 23.3 | 110 | 28 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-10-26 14:25 | 46 | 34.4 | 0 | 19.6 | -6.2 | 6.2 | 1000 | 3.09 | 33.6 | 162 | 37 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-10-26 14:23 | 44.4 | 34.4 | 0 | 21.2 | -59.9 | 59.9 | 1000 | 1.35 | 21.6 | 100 | 40 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-10-26 14:20 | 44.7 | 33.1 | 1.4 | 20.8 | -5.6 | 5.6 | 1000 | 11.95 | 30.7 | 144 | 40 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-10-26 14:19 | 49 | 37.3 | 0.4 | 13.3 | -0.7 | 0.7 | 1000 | 7.12 | 5.9 | 30 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-10-26 14:14 | 42.1 | 33.7 | 0.3 | 23.9 | -17.4 | 17.4 | 1000 | 18.61 | 81.6 | 360 | 70 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-10-26 14:12 | 47.2 | 33.8 | 0 | 19 | -1.9 | 1.9 | 1000 | 4.37 | 4.6 | 23 | 23 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-10-26 14:10 | 47.6 | 36.3 | 0.1 | 16 | -1.8 | 1.8 | 999 | 1.48 | 23.3 | 116 | 22 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-10-26 14:08 | 43.6 | 34.9 | 0 | 21.5 | -7.8 | 7.8 | 1000 | 2.3 | 28.8 | 131 | 40 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-10-26 14:05 | 32.7 | 30 | 0.9 | 36.4 | -3 | 3 | 1000 | 2.52 | 29.9 | 102 | 25 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-10-26 14:02 | 29.4 | 28 | 0.3 | 42.3 | -1.5 | 1.5 | 1000 | 0.05 | 4.1 | 12 | 8 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-10-26 14:00 | 41.6 | 32.6 | 1 | 24.8 | -2.3 | 2.3 | 999 | 2.33 | 29.1 | 127 | 25 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-10-26 13:58 | 48.9 | 37.6 | 0 | 13.5 | -21.6 | 21.6 | 999 | 17.83 | 80 | 410 | 78 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-10-26 13:56 | 44.5 | 36.1 | 0 | 19.4 | -1.1 | 1.1 | 999 | 0.09 | 5.6 | 26 | 12 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-10-26 13:51 | 37.3 | 30.3 | 4 | 28.4 | -0.8 | 0.8 | 999 | 2.55 | 14.1 | 55 | 22 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-10-26 13:50 | 39.8 | 33.8 | 0 | 26.4 | -9.3 | 9.3 | 999 | 11.51 | 29.7 | 124 | 40 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-10-26 13:48 | 53.6 | 39 | 0.9 | 6.5 | -0.2 | 0.2 | 999 | 1.86 | 12.1 | 68 | 25 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-10-26 13:46 | 26.4 | 28.5 | 0.7 | 44.4 | 0 | 0 | 999 | 2.28 | 13.1 | 36 | 15 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-10-26 13:44 | 58.9 | 40.4 | 0.1 | 0.6 | -5.4 | 5.4 | 998 | 0.63 | 7.1 | 44 | 27 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-10-26 13:39 | 60.4 | 41.4 | 0 | 0 | -13.6 | 13.6 | 998 | 10.37 | 27.6 | 175 | 50 | 45 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-10-26 13:38 | 56.8 | 40.7 | 0.7 | 1.8 | -39.3 | 39.3 | 998 | 4.29 | 4.5 | 26 | 20 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-10-26 13:29 | 43.7 | 30.7 | 4.3 | 21.3 | -13.7 | 13.7 | 998 | 21.9 | 87.3 | 399 | 70 | 35.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-10-26 13:27 | 59 | 41.9 | 0 | 0 | 0.2 | -0.2 | 998 | 1.22 | 9.6 | 59 | 25 | 34.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-10-26 13:24 | 43.9 | 36.3 | 0 | 19.8 | -2.6 | 2.6 | 999 | 15.44 | 32.8 | 151 | 42 | 52.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-10-26 13:20 | 59.3 | 41.7 | 0 | 0 | 0 | 0 | 999 | -0.12 | 0 | 0 | 25 | 24 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-10-26 13:18 | 50.9 | 37.9 | 0 | 11.2 | -2.5 | 2.5 | 998 | 0.22 | 9 | 48 | 25 | 22.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-10-26 13:16 | 43.8 | 33.7 | 2.5 | 20 | -4.2 | 4.2 | 999 | 0.46 | 12.6 | 58 | 22 | 35.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-10-26 13:14 | 57.1 | 41.3 | 0 | 1.6 | -0.1 | 0.1 | 998 | 1.04 | 9 | 54 | 27 | 24.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-10-26 13:10 | 51.6 | 37.3 | 0 | 11.1 | -29.8 | 29.8 | 998 | 20.44 | 38.7 | 209 | 70 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-10-26 12:20 | 46.2 | 35.8 | 2.2 | 15.8 | -39.5 | 39.5 | 998 | 6.75 | 76.1 | 368 | 70 | 47.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-10-26 12:18 | 50.6 | 38.1 | 0 | 11.3 | -0.7 | 0.7 | 998 | 1.49 | 10.7 | 57 | 25 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-10-26 12:16 | 44.4 | 36.5 | 0 | 19.1 | -0.6 | 0.6 | 1000 | 17.23 | 35 | 162 | 40 | 48.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-10-26 12:12 | 38 | 33.5 | 0 | 28.5 | -2 | 2 | 999 | 1.8 | 24.5 | 97 | 25 | 39.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-10-26 12:08 | 47.9 | 36.3 | 0 | 15.8 | -3.5 | 3.5 | 1000 | 0.36 | 11.3 | 57 | 18 | 23.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-10-26 12:07 | 61.6 | 39.8 | 0 | 0 | -0.3 | 0.3 | 1000 | 0.15 | 7.5 | 48 | 25 | 19.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-10-26 12:05 | 56.9 | 40.2 | 0.8 | 2.1 | -43.6 | 43.6 | 1000 | 0.61 | 6.7 | 40 | 75 | 26.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-10-26 12:02 | 50.1 | 34.1 | 3 | 12.8 | -0.5 | 0.5 | 1000 | 0.19 | 3.9 | 20 | 20 | 17.4 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-10-26 12:01 | 58.7 | 40 | 0 | 1.3 | -3.4 | 3.4 | 1000 | 0.2 | 8.5 | 52 | 27 | 24 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-10-26 11:59 | 60.3 | 40.4 | 0 | 0 | -0.1 | 0.1 | 1000 | 1 | 9 | 56 | 22 | 21.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-10-26 11:54 | 61.7 | 41.3 | 0 | 0 | -30.3 | 30.3 | 1000 | 0.16 | 7.5 | 48 | 35 | 20.9 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-10-26 11:52 | 46.3 | 35.1 | 0.3 | 18.3 | -0.6 | 0.6 | 1000 | 20.8 | 10.2 | 49 | 10 | 19.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-10-26 11:50 | 60.3 | 41.5 | 0 | 0 | -3.8 | 3.8 | 1000 | -0.14 | 0 | 0 | 15 | 19.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-10-26 11:47 | 60.6 | 40.5 | 0 | 0 | -34.4 | 34.4 | 1000 | 0.79 | 7.8 | 49 | 27 | 24.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-10-26 11:45 | 58.7 | 39.1 | 0 | 2.2 | -10.8 | 10.8 | 1000 | 0.66 | 15.5 | 95 | 25 | 29 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-10-26 11:43 | 58 | 39.8 | 0 | 2.2 | -0.4 | 0.4 | 1000 | 0.74 | 7.7 | 47 | 17 | 21.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-10-26 11:41 | 60.1 | 40.2 | 0 | 0 | -2.4 | 2.4 | 1000 | 2.93 | 33.1 | 208 | 45 | 21.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-10-26 11:39 | 63.3 | 37.6 | 0 | 0 | -1.7 | 1.7 | 1000 | 0.06 | 1 | 7 | 7 | 17.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-10-26 11:37 | 58.5 | 38.1 | 0 | 3.4 | -37.9 | 37.9 | 1000 | 0.21 | 4 | 24 | 30 | 21.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-10-26 11:35 | 61.2 | 38.1 | 0 | 0.7 | -12.9 | 12.9 | 1000 | 4.4 | 40.6 | 260 | 50 | 24.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-10-26 11:33 | 42.4 | 33 | 0.3 | 24.3 | -42.3 | 42.3 | 1000 | 0.46 | 12.5 | 55 | 40 | 26.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X468 | 2017-10-23 15:56 | 56.4 | 37.7 | 1.1 | 4.8 | -4.2 | 4.2 | 1009 | 2.26 | 13.4 | 79 | 25 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-10-23 15:19 | 63.2 | 40.7 | 0 | 0 | -11.7 | 11.7 | 1011 | 15.17 | 73.1 | 484 | 99 | 41.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-10-23 15:18 | 62.6 | 41.6 | 0 | 0 | -22.5 | 22.5 | 1011 | 0.08 | 2.4 | 16 | 99 | 32.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-10-23 15:16 | 61.8 | 41.2 | 0 | 0 | -4.5 | 4.5 | 1011 | 13.23 | 32 | 207 | 70 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-10-23 15:15 | 61.4 | 41.5 | 0 | 0 | 0.1 | -0.1 | 1011 | 19.24 | 38.6 | 248 | 70 | 35.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-10-23 15:11 | 57.2 | 37.2 | 0.3 | 5.3 | -1.4 | 1.4 | 1011 | 1.87 | 12.1 | 72 | 25 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-10-23 15:09 | 54.5 | 36.3 | 0 | 9.2 | -0.2 | 0.2 | 1011 | 0.2 | 3.9 | 22 | 20 | 30.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-10-23 15:07 | 57.8 | 37.2 | 0.2 | 4.8 | 0 | 0 | 1011 | 0.68 | 7.3 | 44 | 25 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-10-23 15:05 | 55.6 | 36.5 | 0 | 7.9 | -0.4 | 0.4 | 1011 | 2.25 | 13.3 | 77 | 25 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-10-23 15:03 | 51.6 | 35.2 | 0.5 | 12.7 | 0.2 | -0.2 | 1011 | 0.07 | 2.3 | 12 | 20 | 30 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-10-23 15:00 | 45.4 | 32.3 | 1.3 | 21 | 0 | 0 | 1011 | 1.14 | 9.4 | 44 | 25 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-10-23 14:58 | 49.7 | 34.2 | 0.2 | 15.9 | -0.3 | 0.3 | 1011 | 3.23 | 15.9 | 83 | 40 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-10-23 14:17 | 35.1 | 29.8 | 0.1 | 35 | -95.8 | 95.8 | 1010 | 1.11 | 8.8 | 32 | 50 | 21.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-10-23 14:15 | 1.1 | 1.1 | 18.4 | 79.4 | -5.1 | 5.1 | 1010 | 1.11 | 0.5 | 0 | 0 | 25.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-10-23 14:14 | 42.3 | 30.1 | 0.6 | 27 | -96.4 | 96.4 | 1010 | -0.16 | 0 | 0 | 40 | 24.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-10-23 14:13 | 43.5 | 31.7 | 0 | 24.8 | -76.8 | 76.8 | 1010 | 19.96 | 9.6 | 43 | 99 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-10-23 14:11 | 39.1 | 29.4 | 0 | 31.5 | -93.3 | 93.3 | 1010 | 2.52 | 3.3 | 13 | 40 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-10-23 14:10 | 35.1 | 28.6 | 0.6 | 35.7 | -35.5 | 35.5 | 1010 | 0.21 | 3.9 | 14 | 5 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-10-23 14:08 | 0.1 | 0 | 21.5 | 78.4 | 0 | 0 | 1010 | -0.08 | 0 | 0 | 0 | 23.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-10-23 14:06 | 52.4 | 36.2 | 0 | 11.4 | -94.7 | 94.7 | 1009 | 0.85 | 16.2 | 89 | 99 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2017-10-23 14:05 | 24 | 17.6 | 9.9 | 48.5 | -0.1 | 0.1 | 1010 | 0.94 | 8.5 | 21 | 5 | 21.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-10-23 14:04 | 53.2 | 35 | 0 | 11.8 | -10.9 | 10.9 | 1010 | 2.88 | 3.8 | 21 | 15 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-10-23 14:03 | 45.2 | 31.5 | 0 | 23.3 | -33.5 | 33.5 | 1010 | 0.67 | 7.1 | 34 | 20 | 21.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-10-23 14:00 | 36.3 | 30.8 | 0 | 32.9 | -92.3 | 92.3 | 1010 | -0.02 | 0 | 0 | 5 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-10-23 13:58 | 0.2 | 0.1 | 19.5 | 80.2 | 0 | 0 | 1009 | 0 | 0 | 0 | 0 | 26.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-10-23 13:57 | 36.8 | 30.5 | 0 | 32.7 | -32.7 | 32.7 | 1009 | 10.21 | 27.4 | 106 | 20 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-10-23 13:55 | 34.3 | 28.1 | 1.7 | 35.9 | -94.5 | 94.5 | 1009 | -0.1 | 0 | 0 | 20 | 26.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-10-23 13:53 | 0.9 | 0.6 | 20.4 | 78.1 | -14.9 | 14.9 | 1009 | -0.04 | 0 | 0 | 0 | 22.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-10-23 13:51 | 49.7 | 35.2 | 0 | 15.1 | -0.9 | 0.9 | 1009 | -0.08 | 0 | 0 | 5 | 23.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-10-23 13:50 | 34.4 | 25.3 | 4.7 | 35.6 | -0.1 | 0.1 | 1009 | 0.38 | 1.3 | 4 | 5 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-10-23 13:48 | 46.9 | 33.8 | 0 | 19.3 | -93.6 | 93.6 | 1009 | 2.14 | 11.1 | 54 | 99 | 21.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-10-23 13:46 | 45.3 | 32.9 | 0.4 | 21.4 | -94.8 | 94.8 | 1009 | -0.28 | 0 | 0 | 40 | 25.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-10-23 13:44 | 54.2 | 36.7 | 0 | 9.1 | -94 | 94 | 1009 | -0.16 | 0 | 0 | 25 | 24.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-10-23 13:42 | 47.4 | 33.8 | 0 | 18.8 | -33.6 | 33.6 | 1009 | 2.13 | 11.5 | 57 | 20 | 21.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-10-23 13:41 | 42.4 | 33 | 0.1 | 24.5 | -1.4 | 1.4 | 1009 | 0.46 | 6 | 26 | 15 | 20.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-10-23 11:55 | 61.9 | 40.4 | 0 | 0 | -3.6 | 3.6 | 1011 | 30.35 | 49.3 | 320 | 50 | 26.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-10-23 11:53 | 25.5 | 14.8 | 13.5 | 46.2 | -66 | 66 | 1011 | -0.59 | 0 | 0 | 99 | 23.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-10-23 11:52 | 62 | 36.9 | 0 | 1.1 | -7.2 | 7.2 | 1010 | 22.63 | 43 | 279 | 60 | 26.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-10-23 11:50 | 63.9 | 40 | 0 | 0 | -8.3 | 8.3 | 1010 | >>>> | 0 | 0 | 99 | 35.7 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2017-10-23 11:47 | 58.8 | 49.8 | 0 | 0 | -5 | 5 | 1010 | 6.37 | 46.8 | 288 | 40 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2017-10-23 11:46 | 53.7 | 56.3 | 0 | 0 | -0.7 | 0.7 | 1010 | 1.47 | 21.9 | 123 | 25 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2017-10-23 11:44 | 56.1 | 53.5 | 0 | 0 | -0.7 | 0.7 | 1010 | 0.94 | 17.7 | 104 | 25 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2017-10-23 11:43 | 53.7 | 56 | 0 | 0 | -1.5 | 1.5 | 1010 | 1.64 | 23.1 | 130 | 25 | 29.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2017-10-23 11:42 | 49.2 | 57.1 | 0 | 0 | -13.3 | 13.3 | 1011 | -0.13 | 0 | 0 | 10 | 30.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-10-23 11:32 | 47.8 | 34.5 | 0 | 17.7 | -4.1 | 4.1 | 1011 | 0.34 | 11 | 55 | 20 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-10-23 11:31 | 61.8 | 38.6 | 0 | 0 | -0.5 | 0.5 | 1011 | 0.14 | 7.3 | 47 | 25 | 23.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-10-23 11:30 | 59 | 40 | 0.1 | 0.9 | -50 | 50 | 1010 | 1.08 | 8.9 | 55 | 70 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-10-23 11:27 | 8.7 | 5.3 | 16.9 | 69.1 | -51.7 | 51.7 | 1010 | -0.02 | 0 | 0 | 99 | 25.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-10-23 11:26 | 51 | 33.6 | 2.8 | 12.6 | 0 | 0 | 1009 | -0.17 | 0 | 0 | 7 | 35.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-10-23 11:24 | 58.5 | 38.7 | 0 | 2.8 | -3.7 | 3.7 | 1010 | 0.55 | 14.2 | 87 | 20 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-10-23 11:22 | 60 | 39.4 | 0 | 0.6 | -0.4 | 0.4 | 1010 | 0.82 | 8.1 | 50 | 15 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-10-23 11:21 | 25.4 | 17.4 | 11.9 | 45.3 | -16.6 | 16.6 | 1010 | 0.19 | 3.8 | 10 | 10 | 23.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-10-23 11:19 | 61.9 | 38.7 | 0 | 0 | -50.6 | 50.6 | 1010 | 0.92 | 8.4 | 54 | 99 | 24.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-10-23 11:18 | 14.4 | 9.2 | 16 | 60.4 | -11.5 | 11.5 | 1010 | -0.13 | 0 | 0 | 5 | 28.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-10-23 11:16 | 57.3 | 40.7 | 0 | 2 | -0.4 | 0.4 | 1010 | 1.64 | 11.2 | 67 | 25 | 30.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-10-23 10:02 | 42 | 34 | 1.7 | 22.3 | -33 | 33 | 1010 | 8.05 | 83.7 | 368 | 50 | 42.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-10-23 09:54 | 62.4 | 37.7 | 0.2 | 0 | 0.4 | -0.4 | 1010 | -0.07 | 0 | 0 | 99 | 19.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-10-23 09:51 | 49.2 | 36.8 | 0 | 14 | -3.6 | 3.6 | 1010 | 8.85 | 26.5 | 136 | 50 | 18.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-10-23 09:49 | 36.1 | 32.8 | 0 | 31.1 | -2 | 2 | 1010 | 1.78 | 25 | 94 | 40 | 24.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-10-23 09:45 | 61.6 | 40.1 | 0 | 0 | 0.3 | -0.3 | 1011 | -0.07 | 0 | 0 | 99 | 18.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-10-23 09:43 | 61.7 | 40.1 | 0 | 0 | 0.3 | -0.3 | 1011 | -0.05 | 0 | 0 | 99 | 18.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-10-23 09:40 | 61.8 | 40.1 | 0 | 0 | 0.4 | -0.4 | 1010 | 0.01 | 1.8 | 11 | 99 | 26.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-10-23 09:37 | 61.9 | 40.7 | 0 | 0 | -10.8 | 10.8 | 1010 | 0.47 | 13.3 | 86 | 25 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-10-23 09:36 | 51.9 | 33.5 | 1.7 | 12.9 | -2.2 | 2.2 | 1010 | 1.37 | 10.4 | 56 | 15 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-10-23 09:34 | 42.8 | 33.2 | 0.6 | 23.4 | -1 | 1 | 1010 | 31.64 | 12.5 | 56 | 30 | 20.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-10-23 09:32 | 60.6 | 41.3 | 0 | 0 | 0.4 | -0.4 | 1010 | -0.03 | 0 | 0 | 5 | 20.3 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-10-23 09:30 | 60.2 | 39.8 | 0 | 0 | -31.4 | 31.4 | 1010 | -0.23 | 0 | 0 | 20 | 21 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-10-23 09:27 | 49.8 | 35.5 | 1.5 | 13.2 | -5 | 5 | 1010 | 1 | 30.8 | 161 | 40 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-10-23 09:25 | 57.3 | 39.7 | 0 | 3 | -0.4 | 0.4 | 1010 | 5.16 | 20.1 | 120 | 25 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-10-23 09:24 | 60.7 | 41 | 0 | 0 | -39.3 | 39.3 | 1010 | 4.52 | 39.4 | 250 | 99 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-10-23 09:22 | 59.5 | 38.7 | 0 | 1.8 | -13.1 | 13.1 | 1010 | 0.87 | 17.8 | 111 | 40 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-10-23 09:20 | 47.8 | 36.1 | 0.5 | 15.6 | -22.2 | 22.2 | 1010 | 0.56 | 6.5 | 32 | 25 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-10-23 09:18 | 0.8 | 4.4 | 17.9 | 76.9 | 0.2 | -0.2 | 1010 | -0.13 | 0 | 0 | 5 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-10-23 09:16 | 60.3 | 39.6 | 0 | 0.1 | -3.1 | 3.1 | 1010 | 3.08 | 33.9 | 214 | 40 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-10-23 09:14 | 64.1 | 37.4 | 0 | 0 | -0.1 | 0.1 | 1010 | -0.07 | 0 | 0 | 10 | 19.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-10-23 09:12 | 2.5 | 4.6 | 16.6 | 76.3 | 0 | 0 | 1010 | -0.05 | 0 | 0 | 0 | 19.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-10-23 09:11 | 61.6 | 38.3 | 0 | 0.1 | -28.2 | 28.2 | 1010 | -0.04 | 0 | 0 | 25 | 22.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-10-23 09:09 | 61.3 | 37.8 | 0 | 0.9 | -14.3 | 14.3 | 1010 | 5.11 | 43.7 | 281 | 50 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-10-23 09:07 | 58.5 | 35.1 | 0.9 | 5.5 | -2.2 | 2.2 | 1010 | 3.16 | 8 | 49 | 15 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-10-23 09:05 | 22.4 | 13.8 | 14.2 | 49.6 | -0.2 | 0.2 | 1009 | -0.02 | 0 | 0 | 0 | 21.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-10-23 09:03 | 40.6 | 32.6 | 0 | 26.8 | -46.4 | 46.4 | 1009 | 2.34 | 28 | 119 | 45 | 29.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-10-20 15:32 | 60.4 | 41.2 | 0 | 0 | -33.6 | 33.6 | 1016 | 21.77 | 139.6 | 883 | 99 | 46 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-10-20 15:31 | 39.2 | 31.8 | 1.8 | 27.2 | -6.6 | 6.6 | 1016 | 14.13 | 32.3 | 132 | 40 | 35.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-10-20 15:29 | 49.8 | 38.7 | 0 | 11.5 | -28.7 | 28.7 | 1016 | 22.73 | 86.7 | 453 | 99 | 41.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-10-20 15:28 | 47.5 | 37.8 | 0 | 14.7 | -17.8 | 17.8 | 1016 | 23.89 | 41.7 | 207 | 40 | 37.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-10-20 15:25 | 61.3 | 41.8 | 0 | 0 | -46.8 | 46.8 | 1016 | 2.5 | 28.8 | 185 | 99 | 45 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-10-20 15:23 | 23 | 27.7 | 0 | 49.3 | -3 | 3 | 1016 | 3.92 | 16.7 | 40 | 20 | 32.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-10-20 15:21 | 42.4 | 36.4 | 0 | 21.2 | -6 | 6 | 1016 | 20.3 | 38.5 | 171 | 40 | 35 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-10-20 15:19 | 56.5 | 40.9 | 0 | 2.6 | -22 | 22 | 1016 | >>>> | 0 | 0 | 99 | 43.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-10-20 15:16 | 53.8 | 38.2 | 2.6 | 5.4 | -48.2 | 48.2 | 1016 | 0.07 | 2.2 | 12 | 99 | 21.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-10-20 15:04 | 19 | 12.3 | 15.7 | 53 | -1.6 | 1.6 | 1018 | -0.16 | 0 | 0 | 0 | 20.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-10-20 15:03 | 56.6 | 38.2 | 0 | 5.2 | -6.3 | 6.3 | 1018 | 17.75 | 37.2 | 221 | 40 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-10-20 15:02 | 57.1 | 38.5 | 0 | 4.4 | -5.2 | 5.2 | 1018 | 10.12 | 60.4 | 361 | 40 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-10-20 15:00 | 48.5 | 38 | 0 | 13.5 | -2.6 | 2.6 | 1018 | 14.27 | 32.4 | 165 | 40 | 38.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-10-20 14:58 | 45.3 | 36.8 | 0.2 | 17.7 | -1.5 | 1.5 | 1018 | 8.65 | 25 | 119 | 25 | 41.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-10-20 14:56 | 63 | 38.9 | 0 | 0 | -12.6 | 12.6 | 1018 | 0.85 | 17.8 | 117 | 20 | 24.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-10-20 14:55 | 50.7 | 37.6 | 0 | 11.7 | -22.3 | 22.3 | 1018 | 16.01 | 35.2 | 187 | 50 | 21.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-10-20 14:53 | 58.8 | 37 | 0.9 | 3.3 | -14.9 | 14.9 | 1018 | 1.59 | 11.3 | 70 | 20 | 21.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-10-20 14:51 | 56.9 | 37.5 | 0 | 5.6 | -10.8 | 10.8 | 1018 | 18.25 | 38.1 | 227 | 50 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-10-20 14:50 | 52.6 | 38.1 | 0 | 9.3 | -0.9 | 0.9 | 1018 | 13.54 | 16.2 | 89 | 25 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-10-20 14:48 | 46.3 | 37.5 | 0.1 | 16.1 | -3.1 | 3.1 | 1017 | 16.76 | 35.3 | 171 | 40 | 33.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-10-20 14:07 | 46 | 36 | 0 | 18 | -6.5 | 6.5 | 1018 | 9.79 | 27.7 | 133 | 25 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X465 | 2017-10-20 14:05 | 61.6 | 39.9 | 0 | 0 | -51.8 | 51.8 | 1018 | 1.19 | 9.6 | 62 | 10 | 20.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-10-20 14:01 | 27 | 28.7 | 0.2 | 44.1 | -0.7 | 0.7 | 1018 | 0.43 | 5.6 | 16 | 5 | 19.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2017-10-20 13:57 | 0.2 | 0.1 | 20.4 | 79.3 | -51.4 | 51.4 | 1018 | -0.09 | 0 | 0 | 0 | 20.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2017-10-20 13:55 | 61.3 | 39.8 | 0 | 0 | -2.3 | 2.3 | 1018 | 20.9 | 20.5 | 131 | 40 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2017-10-20 13:50 | 3.5 | 2.3 | 20.3 | 73.9 | -51.8 | 51.8 | 1018 | 0.08 | 8.7 | 3 | 2 | 19.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2017-10-20 13:47 | 0.4 | 0.3 | 21.2 | 78.1 | -51.4 | 51.4 | 1018 | 0.12 | 10.2 | 0 | 5 | 20.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2017-10-20 13:44 | 62.7 | 38.7 | 0.1 | 0 | -3.2 | 3.2 | 1018 | 11.14 | 15 | 99 | 25 | 20.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2017-10-20 13:41 | 0 | 0 | 21 | 79 | -51.7 | 51.7 | 1019 | 0.12 | 10.5 | 0 | 10 | 20.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2017-10-20 13:38 | 60.6 | 40.1 | 0 | 0 | -52.7 | 52.7 | 1018 | 4.63 | 66.5 | 422 | 50 | 22.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2017-10-20 13:17 | 56.8 | 39.5 | 0 | 3.7 | -0.6 | 0.6 | 1018 | 0.1 | 1.4 | 8 | 5 | 17 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2017-10-20 13:11 | 0 | 0.1 | 20.7 | 79.2 | -50.1 | 50.1 | 1017 | 0.12 | 2.9 | 0 | 0 | 21.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2017-10-20 13:09 | 5.7 | 9.8 | 13.7 | 70.8 | -49.5 | 49.5 | 1018 | 0.13 | 3 | 1 | 10 | 24 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2017-10-20 13:06 | 0 | 0 | 20.9 | 79.1 | -0.4 | 0.4 | 1017 | -0.07 | 0 | 0 | 0 | 24.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-10-20 11:39 | 0.2 | 0.1 | 21.1 | 78.6 | -10 | 10 | 1017 | 20.31 | 19.5 | 0 | 5 | 20.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-10-20 11:38 | 50.8 | 38.6 | 0 | 10.6 | -2.8 | 2.8 | 1017 | 3.68 | 16.5 | 88 | 25 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-10-20 11:36 | 50.4 | 39.5 | 0 | 10.1 | -32.1 | 32.1 | 1017 | 24.24 | 145.2 | 766 | 99 | 45.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-10-20 11:35 | 36.7 | 35.2 | 0.2 | 27.9 | -3.6 | 3.6 | 1017 | 0.2 | 3.8 | 15 | 2 | 21.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-10-20 11:32 | 48.4 | 35.2 | 3.4 | 13 | -2 | 2 | 1017 | 1.16 | 20.3 | 103 | 20 | 27.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-10-20 11:30 | 51.6 | 39.1 | 0 | 9.3 | -2.6 | 2.6 | 1017 | 1.21 | 20.4 | 110 | 25 | 39 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-10-20 11:29 | 46.7 | 36.7 | 0 | 16.6 | -5.8 | 5.8 | 1017 | 4.79 | 40.5 | 198 | 40 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-10-20 11:28 | 53.8 | 39.1 | 0.9 | 6.2 | -0.3 | 0.3 | 1017 | 4.93 | 9.7 | 55 | 15 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-10-20 11:26 | 54.6 | 37.9 | 0 | 7.5 | -7.2 | 7.2 | 1017 | 22.06 | 41.4 | 237 | 50 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-10-20 11:24 | 50.7 | 36.9 | 0 | 12.4 | -32.6 | 32.6 | 1017 | 0.82 | 16.8 | 89 | 20 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-10-20 11:23 | 47 | 33.5 | 1.9 | 17.6 | -3.6 | 3.6 | 1017 | 1.83 | 25.9 | 127 | 25 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-10-20 11:21 | 55.3 | 37.5 | 2 | 5.2 | 0 | 0 | 1017 | 1.01 | 2.2 | 13 | 0 | 19.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-10-20 11:20 | 42.5 | 36.2 | 0 | 21.3 | -0.5 | 0.5 | 1017 | 5.98 | 5.3 | 23 | 10 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-10-20 11:09 | 56.9 | 40.5 | 0.8 | 1.8 | -46.1 | 46.1 | 1016 | 2.84 | 50.1 | 298 | 99 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-10-20 11:07 | 57.4 | 41.9 | 0 | 0.7 | 0 | 0 | 1016 | -0.17 | 0 | 0 | 0 | 24.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-10-20 11:05 | 60.4 | 43.3 | 0 | 0 | -47.1 | 47.1 | 1016 | 1.93 | 11.8 | 75 | 99 | 33.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-10-20 11:03 | 60.5 | 41.8 | 0 | 0 | -48.9 | 48.9 | 1016 | 0.03 | 1.5 | 9 | 99 | 18.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-10-20 11:02 | 52.4 | 38.3 | 0 | 9.3 | -22.3 | 22.3 | 1016 | 13.49 | 69.4 | 381 | 70 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-10-20 11:00 | 61.1 | 42.2 | 0 | 0 | -26.9 | 26.9 | 1016 | 0.9 | 8.2 | 53 | 20 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-10-20 10:58 | 0.5 | 6 | 14.9 | 78.6 | -4.7 | 4.7 | 1016 | -0.08 | 0 | 0 | 0 | 28.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-10-20 10:57 | 52.4 | 38.2 | 0 | 9.4 | -23.6 | 23.6 | 1016 | 5.66 | 43.6 | 239 | 50 | 42.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-10-20 10:55 | 52.4 | 38.1 | 0 | 9.5 | -47.4 | 47.4 | 1016 | 2.86 | 50.5 | 277 | 99 | 37 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-10-20 10:54 | 46.8 | 38.2 | 0.2 | 14.8 | -0.6 | 0.6 | 1016 | 1.72 | 11.1 | 54 | 40 | 43.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-10-19 15:42 | 60.2 | 41.2 | 0 | 0 | -52.4 | 52.4 | 1006 | 3.28 | 55.3 | 348 | 99 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-10-19 15:40 | 56.4 | 40.3 | 0.7 | 2.6 | -54.8 | 54.8 | 1006 | 0.08 | 5.1 | 30 | 99 | 25.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-10-19 15:38 | 0.1 | 0.8 | 20.6 | 78.5 | 0 | 0 | 1006 | -0.02 | 0 | 0 | 0 | 24.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-10-19 15:36 | 59.8 | 41.1 | 0 | 0 | 0.3 | -0.3 | 1006 | -0.1 | 0 | 0 | 20 | 29.2 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-10-19 15:34 | 38.5 | 29 | 4.9 | 27.6 | -2.5 | 2.5 | 1006 | 2.11 | 26.8 | 108 | 25 | 39.3 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-10-19 15:32 | 58.8 | 41.7 | 0 | 0 | -53.3 | 53.3 | 1006 | 0.18 | 7.6 | 46 | 99 | 42 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-10-19 15:30 | 52.5 | 38.1 | 1.9 | 7.5 | -53.3 | 53.3 | 1006 | -0.12 | 0 | 0 | 25 | 25.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-10-19 15:24 | 50.2 | 35.5 | 0 | 14.3 | -4 | 4 | 1007 | 10.12 | 27.8 | 146 | 40 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-10-19 15:22 | 51.9 | 35.6 | 0.2 | 12.3 | -10.8 | 10.8 | 1007 | 5.07 | 19.9 | 108 | 25 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-10-19 15:20 | 47.6 | 34.4 | 0.5 | 17.5 | -5.2 | 5.2 | 1007 | 4.64 | 18.9 | 94 | 25 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-10-19 12:18 | 55.7 | 40 | 0 | 4.3 | -30 | 30 | 1005 | 19.63 | 80.4 | 469 | 99 | 48.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-10-19 12:16 | 58.9 | 41.5 | 0 | 0 | -38.1 | 38.1 | 1005 | 8.27 | 52.6 | 325 | 99 | 42.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-10-19 12:15 | 58.1 | 41.1 | 0 | 0.8 | -36.3 | 36.3 | 1005 | 12.43 | 105.5 | 642 | 99 | 42.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-10-19 12:14 | 46.9 | 35.6 | 0 | 17.5 | -2.7 | 2.7 | 1005 | -0.15 | 0 | 0 | 0 | 35.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-10-19 12:13 | 49.8 | 36.4 | 2.4 | 11.4 | -31 | 31 | 1005 | 20.6 | 82.6 | 431 | 99 | 44 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-10-19 12:11 | 60.5 | 41.7 | 0 | 0 | -11.2 | 11.2 | 1005 | -0.02 | 0 | 0 | 10 | 37.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-10-19 12:09 | 15.3 | 9.9 | 19 | 55.8 | -36.2 | 36.2 | 1005 | -0.05 | 0 | 0 | 0 | 28.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-10-19 12:08 | 47 | 36.6 | 0.4 | 16 | -3.2 | 3.2 | 1005 | 6.2 | 21.6 | 106 | 25 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-10-19 12:06 | 58.4 | 40.2 | 0 | 1.4 | -20.5 | 20.5 | 1005 | 1.04 | 19 | 116 | 40 | 36.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-10-19 12:04 | 59.6 | 43.4 | 0 | 0 | -40.9 | 40.9 | 1005 | 4.13 | 37.1 | 231 | 50 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-10-19 12:02 | 59.6 | 42.1 | 0 | 0 | -3 | 3 | 1005 | -0.34 | 0 | 0 | 0 | 28.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-10-19 12:01 | 0.4 | 0.4 | 19.7 | 79.5 | -24.3 | 24.3 | 1005 | -0.27 | 0 | 0 | 0 | 28 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-10-19 12:00 | 59.5 | 42.8 | 0 | 0 | -44.5 | 44.5 | 1005 | -0.22 | 0 | 0 | 10 | 28.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-10-19 11:58 | 60.1 | 41.1 | 0 | 0 | -47.7 | 47.7 | 1005 | 3.26 | 53.9 | 339 | 99 | 42.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-10-19 11:56 | 50.9 | 38.1 | 0 | 11 | -6.1 | 6.1 | 1005 | 10.54 | 28.4 | 151 | 40 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-10-19 11:55 | 52.8 | 38.5 | 0 | 8.7 | -6.2 | 6.2 | 1004 | 12.58 | 30.9 | 171 | 40 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-10-19 11:54 | 53.6 | 39.5 | 0 | 6.9 | -8.8 | 8.8 | 1004 | 2.08 | 27.2 | 152 | 40 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-10-19 11:52 | 26.7 | 18.9 | 11.6 | 42.8 | -0.2 | 0.2 | 1004 | -0.05 | 0 | 0 | 0 | 24.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-10-19 11:19 | 46.9 | 36.1 | 0.4 | 16.6 | -31.5 | 31.5 | 1005 | -0.06 | 0 | 0 | 20 | 25.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-10-19 11:17 | 49.2 | 37.5 | 0.3 | 13 | -2.6 | 2.6 | 1005 | 6.89 | 22.7 | 117 | 25 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-10-19 11:16 | 6.4 | 6.6 | 14 | 73 | -0.3 | 0.3 | 1005 | -0.12 | 0 | 0 | 0 | 35 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-10-19 11:15 | 52.4 | 38.6 | 0 | 9 | -43.9 | 43.9 | 1005 | 8.67 | 87.2 | 479 | 99 | 42.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-10-19 11:13 | 54.1 | 39 | 0 | 6.9 | -12.3 | 12.3 | 1005 | 9.55 | 58 | 328 | 40 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-10-19 11:12 | 57.8 | 41.2 | 0 | 1 | -26.4 | 26.4 | 1005 | 11.33 | 29.5 | 179 | 99 | 24.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-10-19 11:10 | 35.6 | 32 | 0 | 32.4 | -0.3 | 0.3 | 1005 | 0.09 | 5.7 | 21 | 15 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-10-19 11:09 | 41.7 | 30 | 4.7 | 23.6 | -20.9 | 20.9 | 1005 | 31.21 | 103.3 | 452 | 70 | 36.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-10-19 11:07 | 48.8 | 37.1 | 0.1 | 14 | -21.9 | 21.9 | 1005 | 2.09 | 42.5 | 217 | 40 | 52.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-10-19 11:05 | 0.7 | 6.4 | 14.5 | 78.4 | -0.5 | 0.5 | 1005 | -0.12 | 0 | 0 | 0 | 22.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-10-19 11:04 | 39.2 | 30.9 | 2.3 | 27.6 | -0.6 | 0.6 | 1005 | -0.08 | 0 | 0 | 5 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-10-19 11:02 | 58.2 | 41.7 | 0 | 0.1 | -1.3 | 1.3 | 1005 | 1.1 | 9.1 | 55 | 25 | 34.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-10-19 11:01 | 54 | 40.9 | 0 | 5.1 | -41 | 41 | 1005 | 3.97 | 4.2 | 24 | 99 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-10-19 10:59 | 40.4 | 34.9 | 0 | 24.7 | -2.9 | 2.9 | 1005 | 18.12 | 35.4 | 150 | 40 | 53 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-10-19 10:57 | 53.2 | 38.3 | 0 | 8.5 | -27.4 | 27.4 | 1005 | 14.61 | 113.1 | 630 | 80 | 50.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-10-19 10:56 | 53.4 | 39.7 | 0 | 6.9 | -0.4 | 0.4 | 1005 | 5.19 | 9.7 | 54 | 20 | 38.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-10-19 10:55 | 52 | 36.8 | 0 | 11.2 | -2.2 | 2.2 | 1005 | 1.35 | 21.8 | 119 | 25 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-10-19 10:54 | 36.6 | 32 | 2.8 | 28.6 | -0.3 | 0.3 | 1005 | 12.81 | 1.7 | 6 | 10 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-10-19 10:14 | 60.6 | 41 | 0 | 0 | 1.9 | -1.9 | 1005 | -0.09 | 0 | 0 | 2 | 32.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-10-19 10:11 | 57.3 | 41 | 0 | 1.7 | -53.7 | 53.7 | 1005 | 0.83 | 27 | 162 | 99 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-10-19 10:10 | 50.1 | 36.8 | 0.4 | 12.7 | -0.6 | 0.6 | 1006 | 8.24 | 24.9 | 130 | 25 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-10-19 10:08 | 50.1 | 36.8 | 0.4 | 12.7 | -0.6 | 0.6 | 1006 | 8.24 | 24.9 | 130 | 25 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-10-19 10:07 | 54.6 | 37.7 | 0 | 7.7 | -0.1 | 0.1 | 1006 | 0.12 | 6.6 | 38 | 15 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-10-19 10:05 | 51.5 | 39.3 | 0.3 | 8.9 | -2.6 | 2.6 | 1005 | 14.78 | 8.5 | 45 | 15 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-10-19 10:03 | 52.6 | 40.3 | 0 | 7.1 | -41.9 | 41.9 | 1005 | 7.43 | 22.5 | 124 | 50 | 51.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-10-19 10:02 | 55.7 | 39 | 0.4 | 4.9 | -9.6 | 9.6 | 1005 | 0.87 | 17.4 | 101 | 50 | 38.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-10-19 10:00 | 59.9 | 41.5 | 0 | 0 | -14.2 | 14.2 | 1005 | 10.38 | 27.6 | 173 | 40 | 45.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-10-19 09:58 | 57.2 | 41.4 | 0.3 | 1.1 | -37 | 37 | 1006 | 5.96 | 5.3 | 32 | 25 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-10-19 09:57 | 41.3 | 33.8 | 0 | 24.9 | -1.1 | 1.1 | 1007 | -0.04 | 0 | 0 | 3 | 21.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-10-19 09:15 | 50.1 | 37.9 | 0 | 12 | -3.3 | 3.3 | 1006 | 6.98 | 22.9 | 120 | 25 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-10-19 09:14 | 45.8 | 34.8 | 2.5 | 16.9 | -37.6 | 37.6 | 1006 | 8.36 | 84.7 | 406 | 80 | 48.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-10-19 09:11 | 45.8 | 34.8 | 2.5 | 16.9 | -37.6 | 37.6 | 1006 | 8.36 | 84.7 | 406 | 80 | 48.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-10-19 09:10 | 48.9 | 36.9 | 0 | 14.2 | -1.4 | 1.4 | 1006 | 1.47 | 10.6 | 54 | 15 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-10-19 09:08 | 0.2 | 0.1 | 20.7 | 79 | -0.5 | 0.5 | 1006 | 0.29 | 4.6 | 0 | 0 | 25.7 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-10-19 09:06 | 52.9 | 38.1 | 0 | 9 | -50.8 | 50.8 | 1006 | 0.92 | 29 | 161 | 50 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-10-19 09:05 | 45.9 | 36.2 | 0 | 17.9 | -1 | 1 | 1006 | 18.13 | 35.9 | 172 | 40 | 50 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-10-19 08:55 | 55.7 | 39.5 | 1.7 | 3.1 | 0 | 0 | 1006 | -0.07 | 0 | 0 | 50 | 27.8 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-10-19 08:53 | 58.4 | 41.2 | 0 | 0.4 | 0 | 0 | 1006 | 0.43 | 2.9 | 17 | 5 | 24.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-10-19 08:52 | 59 | 41.3 | 0 | 0 | -41.8 | 41.8 | 1006 | 0.05 | 4.2 | 26 | 10 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-10-19 08:50 | 0.1 | 0.1 | 21 | 78.8 | 0 | 0 | 1006 | -0.02 | 0 | 0 | 0 | 24.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-10-19 08:49 | 1.2 | 3.7 | 19.3 | 75.8 | 0 | 0 | 1007 | -0.03 | 0 | 0 | 0 | 24.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-10-19 08:45 | 44.1 | 33.1 | 2.3 | 20.5 | -0.8 | 0.8 | 1007 | 4.81 | 19 | 88 | 15 | 33.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-10-19 08:43 | 50.4 | 34.8 | 2 | 12.8 | -4 | 4 | 1007 | 8.28 | 54.6 | 288 | 50 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-10-19 08:41 | 58.4 | 38 | 0.4 | 3.2 | -36.8 | 36.8 | 1007 | 1.35 | 10.1 | 62 | 25 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-10-19 08:40 | 58.4 | 39.7 | 0 | 1.9 | -38.8 | 38.8 | 1007 | 2.22 | 27.9 | 171 | 50 | 30.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-10-19 08:39 | 55.9 | 38.2 | 0.7 | 5.2 | -23.9 | 23.9 | 1007 | 11.82 | 30 | 175 | 40 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-10-19 08:37 | 20.3 | 17.9 | 8.2 | 53.6 | -0.1 | 0.1 | 1007 | 0.07 | 1.1 | 2 | 5 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-10-19 08:35 | 49.1 | 36.7 | 0 | 14.2 | -0.4 | 0.4 | 1007 | 0.67 | 3.5 | 18 | 10 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-10-19 08:33 | 57.1 | 38 | 0 | 4.9 | -39.4 | 39.4 | 1007 | 10.42 | 99 | 592 | 99 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-10-19 08:32 | 42 | 25.6 | 4.6 | 27.8 | 0 | 0 | 1007 | -0.19 | 0 | 0 | 0 | 26.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-10-19 08:30 | 52.3 | 36 | 0 | 11.7 | -0.9 | 0.9 | 1007 | 0.62 | 7 | 38 | 20 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-10-19 08:28 | 51.4 | 35.5 | 0.5 | 12.6 | -5.8 | 5.8 | 1007 | 3.03 | 32.8 | 177 | 40 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-10-19 08:26 | 48.5 | 37.2 | 0 | 14.3 | -1.5 | 1.5 | 1007 | 3.45 | 15.9 | 81 | 25 | 39.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-10-19 08:25 | 52.3 | 37.3 | 0 | 10.4 | -31.4 | 31.4 | 1006 | 20.69 | 84.4 | 463 | 99 | 34 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-10-18 14:05 | 58.5 | 38.6 | 0.3 | 2.6 | -23.8 | 23.8 | 1013 | 0.09 | 5.7 | 35 | 99 | 27.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-10-18 14:03 | 59.5 | 38.4 | 0 | 2.1 | -8.3 | 8.3 | 1013 | 0.99 | 8.8 | 55 | 40 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-10-18 14:01 | 59.4 | 38.5 | 0 | 2.1 | -24.2 | 24.2 | 1013 | -0.21 | 0 | 0 | 99 | 30.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-10-18 14:00 | 60.9 | 37.2 | 0 | 1.9 | -2.4 | 2.4 | 1013 | 1.23 | 9.9 | 63 | 25 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-10-18 13:58 | 58.5 | 39.9 | 0 | 1.6 | 0.9 | -0.9 | 1013 | 1.73 | 11.6 | 71 | 40 | 32 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-10-18 13:52 | 57.7 | 38.5 | 0.3 | 3.5 | -3.3 | 3.3 | 1013 | 0.41 | 5.7 | 34 | 20 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-10-18 13:50 | 54.7 | 36.8 | 0.7 | 7.8 | -0.7 | 0.7 | 1013 | 0.39 | 5.5 | 32 | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-10-18 13:47 | 59.2 | 38.8 | 0 | 2 | -20.9 | 20.9 | 1013 | 8.74 | 56.1 | 348 | 90 | 30.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-10-18 13:45 | 58.7 | 39.8 | 0 | 1.5 | 0.3 | -0.3 | 1013 | 0.43 | 5.8 | 35 | 25 | 29.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-10-18 13:43 | 59 | 39.1 | 0 | 1.9 | -1 | 1 | 1013 | 0.26 | 9.8 | 60 | 20 | 28.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-10-18 13:41 | 59.5 | 37.2 | 0 | 3.3 | -11.4 | 11.4 | 1013 | 0.16 | 7.6 | 47 | 20 | 35.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-10-18 13:39 | 59.8 | 37 | 0 | 3.2 | -2.7 | 2.7 | 1013 | 2.48 | 30.3 | 190 | 40 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-10-18 13:38 | 36 | 23.6 | 8.7 | 31.7 | -27.9 | 27.9 | 1013 | -0.04 | 0 | 0 | 80 | 33.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-10-18 13:26 | 59.9 | 37.9 | 0 | 2.2 | 0 | 0 | 1012 | -0.06 | 0 | 0 | 15 | 30.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-10-18 13:25 | 57.1 | 37.6 | 0.3 | 5 | -27.3 | 27.3 | 1012 | 0.54 | 22.7 | 136 | 99 | 31 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-10-18 11:52 | 0.1 | 0 | 20.5 | 79.4 | 0.1 | -0.1 | 1013 | -0.21 | 0 | 0 | 5 | 30.2 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-10-18 11:50 | 50.2 | 35.6 | 0 | 14.2 | -15.4 | 15.4 | 1013 | 7.5 | 51.2 | 269 | 50 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-10-18 11:49 | 43.1 | 32.6 | 0.3 | 24 | -3.4 | 3.4 | 1013 | 1.75 | 24.5 | 110 | 22 | 39.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-10-18 11:47 | 45.3 | 33.5 | 0 | 21.2 | -6.5 | 6.5 | 1013 | 3.15 | 33.1 | 157 | 40 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-10-18 11:45 | 42 | 32.5 | 0 | 25.5 | -54.4 | 54.4 | 1013 | 2.38 | 28.1 | 123 | 50 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-10-18 11:44 | 42.3 | 32.3 | 0.8 | 24.6 | -7.2 | 7.2 | 1013 | 17.98 | 37 | 164 | 40 | 28.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-10-18 11:42 | 59.1 | 39.9 | 0 | 1 | 0.2 | -0.2 | 1013 | -0.14 | 0 | 0 | 15 | 30.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-10-18 11:37 | 46.7 | 35.2 | 0 | 18.1 | -1.5 | 1.5 | 1013 | 1.31 | 4.9 | 24 | 10 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-10-18 11:35 | 51.2 | 36.2 | 0.1 | 12.5 | -0.4 | 0.4 | 1013 | 0.68 | 1.8 | 9 | 10 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-10-18 11:14 | 56.2 | 37.5 | 0 | 6.3 | -4.1 | 4.1 | 1012 | 1.18 | 20.7 | 122 | 25 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-10-18 11:13 | 48.7 | 35.9 | 0.2 | 15.2 | -26.3 | 26.3 | 1011 | 28.02 | 45.2 | 230 | 70 | 37.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-10-18 11:11 | 51.5 | 36.9 | 0.1 | 11.5 | -1.4 | 1.4 | 1011 | 0.47 | 6 | 32 | 25 | 30.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-10-18 11:08 | 60.5 | 38.4 | 0 | 1.1 | 0.2 | -0.2 | 1011 | -0.14 | 0 | 0 | 10 | 30.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-10-18 11:06 | 56.4 | 40.6 | 0.8 | 2.2 | -72 | 72 | 1010 | 0.19 | 7.9 | 46 | 80 | 36 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-10-16 14:28 | 40.1 | 32.1 | 0.3 | 27.5 | -12.9 | 12.9 | 1015 | 11.69 | 62.2 | 262 | 80 | 44.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-10-16 14:26 | 58.2 | 39.6 | 0 | 2.2 | -28 | 28 | 1015 | -0.03 | 0 | 0 | 90 | 30.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-10-16 14:25 | 34.8 | 31 | 0 | 34.2 | -3.2 | 3.2 | 1015 | 13.33 | 7.8 | 28 | 15 | 39 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-10-16 14:23 | 47.4 | 35.9 | 0.3 | 16.4 | -1.9 | 1.9 | 1015 | 0.96 | 18.5 | 91 | 25 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-10-16 14:22 | 40.1 | 33.1 | 1.1 | 25.7 | -7.2 | 7.2 | 1015 | 2.82 | 31.4 | 132 | 40 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-10-16 14:20 | 37.2 | 30.5 | 0.8 | 31.5 | -2.6 | 2.6 | 1015 | 2.47 | 29.5 | 115 | 40 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-10-16 14:19 | 2.9 | 1.8 | 19.8 | 75.5 | -1.5 | 1.5 | 1015 | -0.1 | 0 | 0 | 0 | 29.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-10-16 14:17 | 31.2 | 26.5 | 1.3 | 41 | -2.3 | 2.3 | 1015 | 0.18 | 7.9 | 26 | 5 | 28.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-10-16 14:15 | 41 | 30.6 | 1.5 | 26.9 | -3.6 | 3.6 | 1015 | 4.7 | 39.7 | 170 | 40 | 47.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-10-16 14:14 | 47.5 | 36.1 | 0 | 16.4 | -20.5 | 20.5 | 1015 | 17.14 | 76.2 | 379 | 80 | 38.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-10-16 14:12 | 45.9 | 35.7 | 0 | 18.4 | -0.8 | 0.8 | 1015 | 0.04 | 3.9 | 18 | 15 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-10-16 14:07 | 32.8 | 25.4 | 6 | 35.8 | -9.2 | 9.2 | 1014 | 6.93 | 22.9 | 78 | 30 | 26.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-10-16 14:05 | 39 | 32.9 | 0 | 28.1 | -9.1 | 9.1 | 1014 | 11.52 | 29.4 | 120 | 50 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-10-16 14:04 | 39.2 | 29.7 | 4.4 | 26.7 | -0.8 | 0.8 | 1014 | 3.81 | 17.1 | 70 | 20 | 26.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-10-16 14:01 | 30 | 28.8 | 1.4 | 39.8 | -0.1 | 0.1 | 1014 | 1.31 | 9.8 | 31 | 20 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-10-16 14:00 | 59.9 | 39.8 | 0 | 0.3 | -1.8 | 1.8 | 1014 | 0.45 | 5.9 | 37 | 20 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-10-16 13:59 | 58.8 | 38.8 | 0 | 2.4 | -2.2 | 2.2 | 1014 | 1.38 | 36.8 | 227 | 40 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-10-16 13:55 | 56.7 | 38 | 0.4 | 4.9 | -4.3 | 4.3 | 1015 | 8.52 | 25.7 | 153 | 40 | 32.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-10-16 13:24 | 41.6 | 33.1 | 0 | 25.3 | -2.4 | 2.4 | 1015 | 7.79 | 24.3 | 106 | 40 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-10-16 13:20 | 59.1 | 38.9 | 0 | 2 | -0.5 | 0.5 | 1015 | -0.05 | 0 | 0 | 5 | 28.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-10-16 13:19 | 0.1 | 0 | 19.9 | 80 | 0 | 0 | 1015 | -0.07 | 0 | 0 | 0 | 31.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-10-16 13:14 | 39.8 | 32.9 | 1.7 | 25.6 | -0.8 | 0.8 | 1014 | 0.04 | 3.7 | 15 | 5 | 27.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-10-16 13:12 | 49 | 34.7 | 0 | 16.3 | -26.8 | 26.8 | 1014 | 13.59 | 69.3 | 356 | 50 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-10-16 13:10 | 58.9 | 40.1 | 0 | 1 | 0 | 0 | 1014 | 0.22 | 9 | 55 | 25 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-10-16 13:08 | 44.1 | 34.1 | 0 | 21.8 | -5.8 | 5.8 | 1014 | 0.93 | 18.2 | 84 | 25 | 25.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-10-16 13:06 | 49.4 | 36.1 | 0 | 14.5 | -3.4 | 3.4 | 1014 | 1.5 | 23.3 | 120 | 40 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-10-16 13:03 | 39 | 30.1 | 4 | 26.9 | -13 | 13 | 1013 | 3.39 | 33.8 | 138 | 35 | 39.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-10-16 13:01 | 58.4 | 40.6 | 0 | 1 | 0.4 | -0.4 | 1013 | -0.01 | 0 | 0 | 20 | 25.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-10-10 12:20 | 60.9 | 40.9 | 0 | 0 | -41.7 | 41.7 | 1008 | 1.75 | 24.1 | 154 | 99 | 47.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-10-10 12:18 | 61.2 | 40.8 | 0 | 0 | -30.5 | 30.5 | 1008 | 16.58 | 122.3 | 785 | 99 | 46 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-10-10 12:15 | 61.2 | 40.7 | 0 | 0 | -24.5 | 24.5 | 1008 | 20.62 | 84.7 | 543 | 99 | 39.6 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-10-10 12:14 | 59.7 | 40.5 | 0 | 0 | -13.4 | 13.4 | 1008 | 20.56 | 39.5 | 247 | 60 | 36.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-10-10 12:11 | 53.4 | 40.3 | 0 | 6.3 | -1.2 | 1.2 | 1008 | 3.33 | 15.7 | 88 | 25 | 37.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-10-10 12:10 | 57.5 | 40.7 | 0 | 1.8 | -3.8 | 3.8 | 1008 | 15.45 | 34.2 | 206 | 55 | 36.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-10-10 12:07 | 59.7 | 41.1 | 0 | 0 | -18.3 | 18.3 | 1008 | 26.63 | 95.5 | 597 | 88 | 43.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-10-10 12:01 | 61 | 38.9 | 0 | 0.1 | -4.3 | 4.3 | 1009 | 11.91 | 30.9 | 197 | 50 | 26.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-10-10 11:57 | 60.5 | 40.1 | 0 | 0 | -1.8 | 1.8 | 1008 | 9.81 | 27.7 | 175 | 50 | 32.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-10-10 11:54 | 59.7 | 40.2 | 0 | 0.1 | -0.5 | 0.5 | 1008 | 4.07 | 17.5 | 109 | 40 | 42.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-10-10 11:52 | 59.1 | 36.8 | 0.5 | 3.6 | -5.4 | 5.4 | 1008 | -0.12 | 0 | 0 | 20 | 26.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-10-10 11:50 | 60.8 | 39.4 | 0 | 0 | -23.7 | 23.7 | 1008 | 11.43 | 29.8 | 189 | 55 | 29.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-10-10 11:48 | 56.8 | 36.3 | 1 | 5.9 | -13.8 | 13.8 | 1008 | 1.04 | 9.1 | 54 | 20 | 23.3 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-10-10 11:43 | 61.2 | 39.8 | 0 | 0 | -0.3 | 0.3 | 1007 | 4.51 | 9.4 | 60 | 30 | 24.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-10-10 11:41 | 60.9 | 40.8 | 0 | 0 | -1.8 | 1.8 | 1007 | 8.97 | 26.5 | 169 | 45 | 30 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X459 | 2017-10-09 16:28 | 37 | 28.5 | 3.2 | 31.3 | -1.1 | 1.1 | 1004 | -0.8 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X467 | 2017-10-09 16:25 | 26.9 | 29.5 | 1.6 | 42 | -29.3 | 29.3 | 1004 | 0.4 | 5.4 | 15 | 5 | 20 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X466 | 2017-10-09 16:21 | 27.7 | 18.9 | 10.2 | 43.2 | -29.9 | 29.9 | 1004 | 0.14 | 3.3 | 9 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X458 | 2017-10-09 16:18 | 60.7 | 39.7 | 0 | 0 | 0 | 0 | 1004 | -0.06 | 0 | 0 | 5 | 20 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X464 | 2017-10-09 16:10 | 0.1 | 0.4 | 19.6 | 79.9 | -29.8 | 29.8 | 1004 | -0.07 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X457 | 2017-10-09 16:07 | 61.2 | 39.8 | 0 | 0 | 1 | -1 | 1004 | 0.08 | 1.2 | 8 | 25 | 20 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X463 | 2017-10-09 16:04 | 0.5 | 0.6 | 19.1 | 79.8 | -31.3 | 31.3 | 1004 | 0.01 | 2.7 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X462 | 2017-10-09 16:01 | 38.2 | 25.5 | 6.8 | 29.5 | -30.9 | 30.9 | 1004 | 0.11 | 10.3 | 41 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X456 | 2017-10-09 15:56 | 64 | 39.1 | 0 | 0 | 0.9 | -0.9 | 1004 | 0.81 | 4 | 27 | 20 | 20 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X461 | 2017-10-09 15:52 | 0.2 | 0.9 | 19.3 | 79.6 | -32.1 | 32.1 | 1003 | 0.07 | 7.8 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BLW2X460 | 2017-10-09 15:46 | 0.3 | 0.4 | 19.5 | 79.8 | -31.1 | 31.1 | 1003 | 0.04 | 5.7 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-10-09 12:32 | 61 | 41.2 | 0 | 0 | -8.6 | 8.6 | 1002 | 4.31 | 18.5 | 118 | 30 | 24.3 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-10-09 10:38 | 61.2 | 42.5 | 0 | 0 | -31.6 | 31.6 | 1002 | 14.29 | 113.5 | 728 | 99 | 43 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-10-09 10:37 | 62.8 | 41.2 | 0 | 0 | -5.4 | 5.4 | 1002 | 12.07 | 30.8 | 203 | 40 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-10-09 10:35 | 62.3 | 41.8 | 0 | 0 | -29.7 | 29.7 | 1002 | 18.95 | 81.8 | 534 | 99 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-10-09 10:34 | 62 | 41.9 | 0 | 0 | -16 | 16 | 1002 | 18.31 | 37.5 | 243 | 50 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-10-09 10:32 | 61.8 | 42.6 | 0 | 0 | -2.5 | 2.5 | 1002 | 2.86 | 14.9 | 96 | 25 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-10-09 10:31 | 60.3 | 42.3 | 0 | 0 | -4 | 4 | 1002 | 15.33 | 34.2 | 216 | 40 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-10-09 10:30 | 60 | 42.4 | 0 | 0 | -16 | 16 | 1002 | 22.92 | 88.7 | 557 | 90 | 41.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-10-09 10:28 | 58.5 | 42.3 | 0.4 | 0 | -42.8 | 42.8 | 1003 | 0.26 | 4.3 | 26 | 99 | 30.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-10-09 10:12 | 64.3 | 39 | 0 | 0 | -0.7 | 0.7 | 1003 | 2.32 | 13.8 | 93 | 50 | 22.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-10-09 10:08 | 64.7 | 41 | 0 | 0 | -0.7 | 0.7 | 1003 | 4.52 | 19.2 | 130 | 25 | 24 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-10-09 10:05 | 61.3 | 41.2 | 0 | 0 | -0.6 | 0.6 | 1003 | 3.25 | 15.8 | 101 | 25 | 36.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-10-09 10:04 | 57 | 36.4 | 1.1 | 5.5 | -5.7 | 5.7 | 1003 | 0.24 | 9.4 | 56 | 20 | 22.4 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-10-09 10:02 | 62.1 | 40 | 0 | 0 | -3.7 | 3.7 | 1002 | 14.55 | 34.4 | 223 | 40 | 23 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-10-09 10:00 | 54.2 | 35.1 | 1.9 | 8.8 | -13.4 | 13.4 | 1003 | 1.21 | 9.8 | 56 | 20 | 20.8 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-10-09 09:58 | 62 | 39.4 | 0 | 0 | -4 | 4 | 1002 | 7.71 | 25.1 | 163 | 40 | 20.8 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-10-09 09:53 | 59.9 | 42.3 | 0 | 0 | -2.3 | 2.3 | 1002 | 2.53 | 7 | 44 | 25 | 22 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-09-15 11:11 | 45.7 | 35 | 0 | 19.3 | -0.1 | 0.1 | 1007 | 0.099 | 2.8 |  | 20 | 20.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-09-15 11:07 | 50.4 | 38 | 0.1 | 11.5 | -3.9 | 3.9 | 1007 | 7.957 | 24.9 |  | 40 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-09-15 10:34 | 26.9 | 19.4 | 11.1 | 42.6 | -17.9 | 17.9 | 1005 | 0.251 | 4.3 |  | 0 | 26.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-09-15 10:33 | 58 | 41.6 | 0 | 0.4 | -50.4 | 50.4 | 1005 | 0.764 | 26.1 |  | 99 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-09-15 10:31 | 43.5 | 35.4 | 0.6 | 20.5 | -1.5 | 1.5 | 1005 | 12.851 | 30.9 |  | 30 | 33.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-09-15 10:29 | 46.8 | 37.2 | 0 | 16 | 0 | 0 | 1005 | 0.16 | 7.5 |  | 20 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-09-15 10:27 | 49.9 | 38.9 | 0.2 | 11 | -2.6 | 2.6 | 1005 | 13.927 | 8.3 |  | 20 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-09-15 10:25 | 51.7 | 40.4 | 0 | 7.9 | -39.8 | 39.8 | 1005 | 7.977 | 23.4 |  | 50 | 49.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-09-15 10:23 | 49.6 | 38 | 0.4 | 12 | -8.8 | 8.8 | 1005 | 0.977 | 18.4 |  | 20 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-09-15 10:21 | 53.2 | 39.8 | 0 | 7 | -14 | 14 | 1005 | 10.07 | 27 |  | 40 | 42.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-09-15 10:20 | 58.3 | 42.2 | 0.3 | 0 | -33.8 | 33.8 | 1005 | 6.07 | 5.4 |  | 20 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-09-15 10:18 | 19.9 | 25.5 | 1.4 | 53.2 | -2.1 | 2.1 | 1005 | 3.227 | 3.9 |  | 2 | 16.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-09-15 10:14 | 39.8 | 35 | 0.6 | 24.6 | -38.5 | 38.5 | 1005 | 0.137 | 11.2 |  | 5 | 21.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-09-15 10:12 | 44.9 | 36.7 | 0.5 | 17.9 | -4.1 | 4.1 | 1005 | 9.739 | 27 |  | 30 | 30.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-09-15 10:10 | 18.9 | 24.3 | 0.9 | 55.9 | -0.8 | 0.8 | 1005 | 0.038 | 3.6 |  | 0 | 24.5 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-09-15 10:07 | 50.3 | 39 | 0 | 10.7 | -40.4 | 40.4 | 1005 | 12.237 | 103.4 |  | 99 | 41.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-09-15 10:06 | 55.2 | 39.9 | 0 | 4.9 | -11.3 | 11.3 | 1005 | 8.442 | 54.7 |  | 50 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-09-15 10:04 | 58.2 | 41.6 | 0 | 0.2 | -24 | 24 | 1005 | 11.819 | 30.5 |  | 99 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-09-15 10:02 | 22.3 | 28.6 | 0 | 49.1 | -1.2 | 1.2 | 1005 | 1.376 | 21.7 |  | 1 | 22.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-09-15 10:00 | 49.8 | 36.9 | 0.7 | 12.6 | -23 | 23 | 1005 | 26.586 | 95.3 |  | 80 | 36.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-09-15 09:58 | 46.7 | 36.9 | 0.3 | 16.1 | -27.7 | 27.7 | 1005 | 1.406 | 34.6 |  | 42 | 51.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-09-15 09:56 | 0.4 | 5.7 | 14.6 | 79.3 | -1.2 | 1.2 | 1005 | -0.087 | 0 |  | 0 | 19.1
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-09-15 09:54 | 32.1 | 28 | 2.6 | 37.3 | -1.6 | 1.6 | 1005 | 0.415 | 5.7 |  | 5 | 15.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-09-15 09:52 | 60.6 | 42.9 | 0 | 0 | 0.2 | -0.2 | 1005 | 0.827 | 8.1 |  | 25 | 23.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-09-15 09:51 | 52.1 | 41.4 | 0 | 6.5 | -39.2 | 39.2 | 1005 | 3.641 | 4 |  | 99 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-09-15 09:49 | 35.7 | 33.5 | 0 | 30.8 | -4.6 | 4.6 | 1005 | 26.197 | 42.4 |  | 40 | 51.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-09-15 09:47 | 53.2 | 38.4 | 0 | 8.4 | -25.5 | 25.5 | 1005 | 13.617 | 109.5 |  | 80 | 49.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-09-15 09:45 | 45.8 | 37.4 | 0.4 | 16.4 | -0.8 | 0.8 | 1005 | 6.751 | 11 |  | 20 | 35.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-09-15 09:43 | 42.3 | 35.4 | 0 | 22.3 | -2.9 | 2.9 | 1005 | 2.284 | 28 |  | 30 | 34.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-09-15 09:41 | 32.4 | 27.8 | 6.3 | 33.5 | -0.2 | 0.2 | 1005 | 11.128 | 1.6 |  | 5 | 16.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-09-14 15:03 | 56.2 | 41.1 | 0 | 2.7 | -30 | 30 | 1003 | 20.395 | 82.1 |  | 99 | 46 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-09-14 15:02 | 58.2 | 42.4 | 0 | 0 | -38.1 | 38.1 | 1003 | 10.073 | 58 |  | 99 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-09-14 15:00 | 58.5 | 42 | 0 | 0 | -36.2 | 36.2 | 1003 | 13.744 | 111.1 |  | 99 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-09-14 14:59 | 44.1 | 34.8 | 0.9 | 20.2 | -4.5 | 4.5 | 1002 | -0.029 | 0 |  | 0 | 19.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-09-14 14:57 | 52.5 | 38.5 | 1.6 | 7.4 | -27.5 | 27.5 | 1003 | 20.015 | 82.1 |  | 99 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-09-14 14:55 | 60.7 | 42.4 | 0.2 | 0 | -11.8 | 11.8 | 1003 | 0.071 | 5 |  | 20 | 31.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-09-14 14:53 | 2.3 | 1.7 | 19.4 | 76.6 | -10.5 | 10.5 | 1002 | 0.07 | 2.3 |  | 0 | 17.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-09-14 14:52 | 49.5 | 37.6 | 0.4 | 12.5 | -3.2 | 3.2 | 1002 | 6.197 | 21.9 |  | 25 | 24.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-09-14 14:50 | 62 | 41.7 | 0 | 0 | -43.8 | 43.8 | 1002 | 0.055 | 2 |  | 5 | 20.6 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-09-14 14:43 | 58.7 | 41.1 | 0 | 0.2 | -14.1 | 14.1 | 1002 | 0.229 | 9 |  | 40 | 34.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-09-14 14:40 | 11.4 | 7.6 | 17.7 | 63.3 | -0.6 | 0.6 | 1002 | -0.264 | 0 |  | 0 | 17.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-09-14 14:38 | 13 | 8.1 | 16.2 | 62.7 | 0 | 0 | 1003 | -0.278 | 0 |  | 0 | 16.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-09-14 14:35 | 1.4 | 1.5 | 19.9 | 77.2 | -22.8 | 22.8 | 1002 | -0.22 | 0 |  | 0 | 21.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-09-14 14:33 | 60.1 | 41.5 | 0 | 0 | -48.4 | 48.4 | 1002 | 2.058 | 43 |  | 99 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-09-14 14:31 | 53.2 | 38.4 | 0.4 | 8 | -5.7 | 5.7 | 1002 | 10.856 | 29.3 |  | 40 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-09-14 14:29 | 56.7 | 39.7 | 0 | 3.6 | -6 | 6 | 1002 | 13.525 | 32.4 |  | 40 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-09-14 14:28 | 0.2 | 0.3 | 20.3 | 79.2 | 0.1 | -0.1 | 1002 | -0.107 | 0 |  | 0 | 17.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-09-14 14:26 | 0.5 | 0.4 | 20.2 | 78.9 | -1.3 | 1.3 | 1002 | -0.049 | 0 |  | 0 | 18.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-09-14 14:02 | 50.2 | 36.6 | 0 | 13.2 | -4.3 | 4.3 | 1004 | 10.172 | 27.9 |  | 40 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-09-14 14:00 | 47.1 | 36.1 | 0 | 16.8 | -11.5 | 11.5 | 1004 | 5.432 | 20.5 |  | 25 | 21.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-09-14 13:59 | 50.6 | 36.7 | 0 | 12.7 | -5.3 | 5.3 | 1004 | 5.025 | 19.9 |  | 25 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-09-14 13:55 | 57.3 | 39.6 | 0 | 3.1 | -5.2 | 5.2 | 1004 | 1.631 | 24.5 |  | 40 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-09-14 13:54 | 44.6 | 36.3 | 0 | 19.1 | -36.2 | 36.2 | 1003 | >>>> | 0 |  | 70 | 35.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-09-14 13:51 | 35.2 | 31.4 | 1.8 | 31.6 | -5.9 | 5.9 | 1003 | 4.701 | 18.5 |  | 20 | 34.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-09-14 13:49 | 19.8 | 19.7 | 7.9 | 52.6 | -3.8 | 3.8 | 1004 | 3.263 | 7.6 |  | 5 | 35.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-09-14 13:47 | 41.7 | 35 | 1.6 | 21.7 | -50.7 | 50.7 | 1004 | 11.221 | 59.5 |  | 50 | 44.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-09-14 13:34 | 60.5 | 40.3 | 0 | 0 | -66.2 | 66.2 | 1004 | 0.514 | 13.5 |  | 99 | 19.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-09-14 13:32 | 52.8 | 37.6 | 0 | 9.6 | -19.2 | 19.2 | 1004 | 2.977 | 15.2 |  | 40 | 24.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-09-14 13:31 | 56.9 | 37.9 | 0.8 | 4.4 | -68.7 | 68.7 | 1004 | 0.857 | 8 |  | 99 | 20.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-09-14 13:29 | 53.4 | 36.4 | 0 | 10.2 | -5.9 | 5.9 | 1004 | 3.789 | 17.5 |  | 40 | 16.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-09-14 13:27 | 59.6 | 41.4 | 0 | 0 | -0.8 | 0.8 | 1004 | 4.844 | 19.4 |  | 30 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-09-14 13:25 | 54.2 | 38.1 | 1.4 | 6.3 | -6.4 | 6.4 | 1004 | 1.331 | 10.3 |  | 20 | 17.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-09-14 13:24 | 47.4 | 35.8 | 1.4 | 15.4 | -2.5 | 2.5 | 1004 | 1.347 | 10.3 |  | 15 | 17.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-09-14 13:22 | 61.3 | 41 | 0 | 0 | -19.6 | 19.6 | 1004 | 29.457 | 102.9 |  | 80 | 30.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-09-14 13:21 | 58.8 | 41.4 | 0 | 0 | -0.1 | 0.1 | 1004 | 1.646 | 11.5 |  | 20 | 19.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-09-14 13:19 | 59 | 40.9 | 0 | 0.1 | -2.9 | 2.9 | 1004 | 1.161 | 20.8 |  | 25 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-09-14 13:17 | 55.8 | 38 | 0 | 6.2 | -16.3 | 16.3 | 1004 | 0.778 | 16.6 |  | 20 | 34.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-09-14 13:16 | 50.4 | 36 | 0 | 13.6 | -5.5 | 5.5 | 1004 | 4.552 | 40.6 |  | 40 | 26.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-09-14 13:14 | 52.1 | 37 | 0.2 | 10.7 | -53.2 | 53.2 | 1004 | 0.018 | 2.5 |  | 80 | 20.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-09-14 13:12 | 54.3 | 37.7 | 0 | 8 | 0.1 | -0.1 | 1004 | 0.089 | 5.8 |  | 10 | 18.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-09-14 13:10 | 52.8 | 38.1 | 0 | 9.1 | -52.2 | 52.2 | 1004 | 1.686 | 39.1 |  | 99 | 30.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-09-14 13:06 | 53 | 39.3 | 0.9 | 6.8 | -8.8 | 8.8 | 1005 | 0.774 | 16.1 |  | 50 | 43.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-09-14 11:57 | 5.2 | 10.8 | 11 | 73 | 0 | 0 | 1005 | 0.078 | 2.4 |  | 0 | 21.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-09-14 11:55 | 49.1 | 37.4 | 0 | 13.5 | -14.7 | 14.7 | 1005 | 7.047 | 49.5 |  | 50 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-09-14 11:53 | 40.6 | 33.4 | 0.4 | 25.6 | -5.9 | 5.9 | 1005 | 3.196 | 32.9 |  | 25 | 38.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-09-14 11:51 | 44.4 | 35.3 | 0 | 20.3 | -9.2 | 9.2 | 1005 | 4.954 | 41.3 |  |  | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-09-14 11:49 | 35.1 | 32.9 | 0 | 32 | -49.3 | 49.3 | 1005 | 3.375 | 33.3 |  | 40 | 28.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-09-14 11:46 | 46.2 | 36.1 | 0.2 | 17.5 | -7.9 | 7.9 | 1005 | 16.568 | 36 |  | 40 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-09-14 11:45 | 32.8 | 23.9 | 8 | 35.3 | -0.2 | 0.2 | 1005 | -0.008 | 0 |  | 5 | 15.9 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-09-14 11:43 | 49.5 | 37.9 | 0 | 12.6 | -3.2 | 3.2 | 1005 | 2.024 | 6.3 |  |  | 16.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-09-14 11:42 | 43.5 | 34.9 | 0.6 | 21 | -0.5 | 0.5 | 1005 | 3.111 | 3.9 |  | 7 | 18.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-09-14 11:37 | 48.1 | 36.9 | 0 | 15 | -16.3 | 16.3 | 1005 | 18.748 | 79.2 |  | 80 | 42.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-09-14 11:36 | 31.3 | 22.5 | 12.6 | 33.6 | -34.8 | 34.8 | 1005 | -0.182 | 0 |  | 99 | 21.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-09-14 11:34 | 50.4 | 37.2 | 0 | 12.4 | -0.8 | 0.8 | 1005 | 3.099 | 3.8 |  | 20 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-09-14 11:33 | 52.4 | 38.3 | 0 | 9.3 | -1.2 | 1.2 | 1005 | 0.974 | 18.8 |  | 40 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-09-14 11:31 | 50.1 | 37.6 | 0 | 12.3 | -6.4 | 6.4 | 1005 | 2.017 | 27 |  | 40 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-09-14 11:30 | 50 | 39.1 | 0.1 | 10.8 | -10.8 | 10.8 | 1004 | 16.481 | 77.4 |  | 80 | 18.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-09-14 11:28 | 0.4 | 0.3 | 19.4 | 79.9 | 0 | 0 | 1005 | -0.013 | 0 |  | 0 | 15.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-09-14 11:27 | 44 | 36.1 | 0 | 19.9 | -2 | 2 | 1004 | 0.257 | 9.6 |  | 20 | 18.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-09-14 11:25 | 61.9 | 40.7 | 0 | 0 | 0.6 | -0.6 | 1005 | 2.193 | 28.6 |  | 50 | 26.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-09-14 11:23 | 51.4 | 38.4 | 0.4 | 9.8 | -5.6 | 5.6 | 1004 | 2.645 | 30.5 |  | 40 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-09-14 11:22 | 50.1 | 38.8 | 0 | 11.1 | -0.4 | 0.4 | 1005 | 0.142 | 7.1 |  | 20 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-09-14 11:20 | 40.3 | 33.5 | 0.5 | 25.7 | -2.5 | 2.5 | 1005 | 9.409 | 26.9 |  | 40 | 21.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-09-14 11:07 | 54.6 | 40.2 | 0.3 | 4.9 | -9.8 | 9.8 | 1004 | 5.126 | 19.6 |  | 40 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-09-14 11:05 | 43.5 | 36.1 | 0 | 20.4 | -7.9 | 7.9 | 1004 | 10.058 | 27.9 |  | 40 | 18.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-09-14 11:04 | 36.6 | 30.7 | 3.4 | 29.3 | -2.5 | 2.5 | 1004 | 6.114 | 21.8 |  | 30 | 18.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-09-14 11:02 | 28.9 | 29.5 | 1.2 | 40.4 | -0.1 | 0.1 | 1004 | 1.569 | 10.9 |  | 15 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-09-14 11:00 | 58.2 | 40.8 | 0 | 1 | -3.6 | 3.6 | 1004 | 0.305 | 4.9 |  | 15 | 16.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-09-14 10:58 | 57.2 | 38.7 | 0.1 | 4 | -2.1 | 2.1 | 1004 | 1.286 | 35.7 |  | 50 | 24.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-09-14 10:55 | 58.9 | 41.5 | 0 | 0 | -0.8 | 0.8 | 1004 | 1.411 | 5.3 |  | 20 | 18.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-09-14 10:53 | 57.4 | 38.9 | 0.8 | 2.9 | -4.4 | 4.4 | 1004 | 6.466 | 22.5 |  | 40 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-09-14 10:18 | 50.5 | 38.8 | 0.1 | 10.6 | -3.1 | 3.1 | 1003 | 6.724 | 22.9 |  | 40 | 22.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-09-14 10:16 | 0.6 | 1.1 | 18.2 | 80.1 | -0.4 | 0.4 | 1003 | -0.054 | 0 |  | 0 | 16.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-09-14 10:14 | 37.4 | 20.1 | 19.1 | 23.4 | 0.3 | -0.3 | 1003 | -0.054 | 0 |  | 2 | 17 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-09-14 10:13 | 0.1 | 0.1 | 19.6 | 80.2 | -0.3 | 0.3 | 1003 | -0.052 | 0 |  | 0 | 15.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-09-14 10:12 | 58.2 | 41.6 | 0.1 | 0.1 | 1.2 | -1.2 | 1003 | -0.071 | 0 |  | 10 | 14.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-09-14 10:09 | 40.2 | 37.6 | 0.1 | 22.1 | -1.8 | 1.8 | 1003 | 0.094 | 5.7 |  | 15 | 19.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-09-14 10:07 | 50.3 | 37.4 | 0 | 12.3 | -24.6 | 24.6 | 1003 | 11.762 | 64.7 |  | 70 | 23.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-09-14 10:05 | 0.9 | 0.9 | 17.5 | 80.7 | -2.1 | 2.1 | 1003 | -0.144 | 0 |  | 0 | 18.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-09-14 10:04 | 51.6 | 40.8 | 0 | 7.6 | -0.8 | 0.8 | 1003 | 0.091 | 5.7 |  | 40 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-09-14 10:02 | 47.7 | 38 | 0 | 14.3 | -5.1 | 5.1 | 1003 | 1.148 | 20.4 |  | 40 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-09-14 10:00 | 53.3 | 39.7 | 0 | 7 | -4.7 | 4.7 | 1003 | 1.451 | 23.1 |  | 40 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-09-14 09:58 | 51.5 | 38.9 | 0.6 | 9 | -0.2 | 0.2 | 1003 | 0.032 | 3.4 |  | 20 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-09-14 09:56 | 58.4 | 42.3 | 0 | 0 | -0.1 | 0.1 | 1003 | 0.056 | 4.5 |  | 25 | 21 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-09-14 09:54 | 33.8 | 33.6 | 0.4 | 32.2 | -1.1 | 1.1 | 1003 | 1.26 | 9.7 |  | 10 | 21.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-09-14 09:51 | 28 | 24.3 | 6.3 | 41.4 | -4.6 | 4.6 | 1003 | 8.998 | 26.3 |  | 25 | 18.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-09-14 09:04 | 59 | 42.2 | 0 | 0 | -0.1 | 0.1 | 1003 | 0.578 | 3.4 |  | 5 | 12.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-09-14 09:02 | 54.3 | 39.4 | 0 | 6.3 | -27.5 | 27.5 | 1003 | 0.048 | 4.2 |  | 10 | 11.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-09-14 09:00 | 58.1 | 41.4 | 0 | 0.5 | -1.2 | 1.2 | 1003 | 0.348 | 11.5 |  | 20 | 11.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-09-14 08:58 | 56.5 | 39.2 | 0 | 4.3 | -3.3 | 3.3 | 1003 | 1.173 | 9.8 |  | 15 | 12.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-09-14 08:55 | 51.2 | 36.8 | 0 | 12 | -4.2 | 4.2 | 1003 | 6.863 | 23 |  | 25 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-09-14 08:53 | 49.3 | 38 | 1.4 | 11.3 | -38.2 | 38.2 | 1003 | 9.378 | 90.1 |  | 80 | 44.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-09-14 08:51 | 44.7 | 35.8 | 0 | 19.5 | -2.2 | 2.2 | 1003 | 2.527 | 14 |  | 20 | 22 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-09-14 08:49 | 60 | 44.6 | 0 | 0 | 0 | 0 | 1002 | -0.04 | 0 |  | 5 | 13.2 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-09-14 08:47 | 56.1 | 40.2 | 0 | 3.7 | -50.7 | 50.7 | 1002 | 0.81 | 27.7 |  | 70 | 18.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-09-14 08:45 | 60.9 | 43.6 | 0 | 0 | 0.1 | -0.1 | 1002 | 0.434 | 5.8 |  | 25 | 22.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-09-14 08:32 | 62.1 | 42.8 | 0 | 0 | -51.6 | 51.6 | 1002 | 3.531 | 58 |  | 99 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-09-14 08:30 | 47.1 | 36 | 7 | 9.9 | -55.4 | 55.4 | 1002 | -0.065 | 0 |  | 99 | 14.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-09-14 08:29 | 0.2 | 0.7 | 17.3 | 81.8 | 0 | 0 | 1002 | -0.01 | 0 |  | 0 | 15.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-09-14 08:26 | 38 | 34 | 0.7 | 27.3 | -1.3 | 1.3 | 1001 | -0.102 | 0 |  | 20 | 27.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-09-14 08:25 | 30.3 | 24.7 | 7.4 | 37.6 | -8.1 | 8.1 | 1001 | 5.556 | 43.3 |  | 20 | 37.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-09-14 08:22 | 61.3 | 43.5 | 0 | 0 | -53.1 | 53.1 | 1001 | 0.215 | 8.5 |  | 99 | 37.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-09-14 08:20 | 44.7 | 34.7 | 5.2 | 15.4 | -53.5 | 53.5 | 1004 | -0.082 | 0 |  | 25 | 9.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-09-13 11:44 | 45.3 | 34.2 | 1.8 | 18.7 | 0 | 0 | 995 | 4.464 | 18.5 |  | 15 | 26.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-09-13 11:42 | 54.3 | 36.8 | 1.3 | 7.6 | -2.8 | 2.8 | 995 | 6.873 | 49.9 |  | 50 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-09-13 11:41 | 61.7 | 39.8 | 0 | 0 | -20.7 | 20.7 | 995 | 0.008 | 0.8 |  | 0 | 18.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-09-13 11:40 | 61.7 | 39.8 | 0 | 0 | -20.7 | 20.7 | 995 | 0.008 | 0.8 |  | 0 | 18.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-09-13 11:39 | 61.2 | 40.7 | 0 | 0 | -38 | 38 | 995 | 1.008 | 19 |  | 50 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-09-13 11:37 | 57.8 | 39.7 | 0.4 | 2.1 | -21.1 | 21.1 | 995 | 12.692 | 31.4 |  | 40 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-09-13 11:35 | 24.2 | 19.8 | 7.6 | 48.4 | -0.6 | 0.6 | 995 | 1.128 | 4.6 |  | 5 | 19.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-09-13 11:34 | 47.7 | 37.1 | 0 | 15.2 | -1.9 | 1.9 | 995 | 1.308 | 5 |  | 10 | 22.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-09-13 11:32 | 57.8 | 38.9 | 0 | 3.3 | -36 | 36 | 995 | 8.471 | 90 |  | 99 | 25.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-09-13 11:30 | 41.6 | 27.1 | 4.4 | 26.9 | 0.2 | -0.2 | 995 | -0.043 | 0 |  | 0 | 15.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-09-13 11:28 | 50.7 | 36.3 | 0 | 13 | -0.9 | 0.9 | 995 | 0.983 | 8.8 |  | 15 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-09-13 11:27 | 49 | 35.5 | 0.3 | 15.2 | -6.4 | 6.4 | 995 | 3.134 | 33.5 |  | 50 | 27.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-09-13 11:26 | 48 | 37.7 | 0.1 | 14.2 | -0.2 | 0.2 | 995 | 2.949 | 14.8 |  | 25 | 33.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-09-13 11:24 | 51.6 | 37.7 | 0 | 10.7 | -32 | 32 | 995 | 20.038 | 83.5 |  | 99 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-09-13 10:38 | 61.6 | 41.8 | 0 | 0 | -3.3 | 3.3 | 995 | 5.657 | 10.6 |  | 20 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-09-13 10:37 | 59.7 | 41.3 | 0 | 0 | -2.2 | 2.2 | 995 | 3.227 | 15.7 |  | 25 | 36.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-09-13 10:36 | 57.7 | 41.6 | 0 | 0.7 | -32.4 | 32.4 | 995 | 21.974 | 139.6 |  | 99 | 44.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-09-13 10:35 | 51.2 | 39 | 0 | 9.8 | -2.3 | 2.3 | 995 | 0.158 | 3.5 |  | 5 | 17.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-09-13 10:33 | 50 | 37.2 | 2.5 | 10.3 | -1.4 | 1.4 | 995 | 1.142 | 20.3 |  | 25 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-09-13 10:31 | 51 | 39 | 0 | 10 | -2.1 | 2.1 | 995 | 1.39 | 21.9 |  | 25 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-09-13 10:30 | 44.8 | 36.1 | 0 | 19.1 | -7.6 | 7.6 | 995 | 7.414 | 50.3 |  | 40 | 37.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-09-13 10:28 | 55.7 | 40.5 | 0.7 | 3.1 | 0.1 | -0.1 | 995 | 4.618 | 9.5 |  | 5 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-09-13 10:25 | 53.5 | 38.2 | 0 | 8.3 | -6.6 | 6.6 | 995 | 20.662 | 40.4 |  | 50 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-09-13 10:24 | 51.6 | 38.1 | 0 | 10.3 | -33.1 | 33.1 | 995 | 0.421 | 12.1 |  | 20 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-09-13 10:23 | 48.5 | 34.6 | 1.2 | 15.7 | -4.8 | 4.8 | 995 | 2.044 | 27.5 |  | 20 | 18.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-09-13 10:20 | 55.2 | 38.2 | 1.9 | 4.7 | 0 | 0 | 995 | 0.884 | 2.1 |  | 3 | 19.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-09-13 10:19 | 46.8 | 38.9 | 0 | 14.3 | 0 | 0 | 994 | 6.354 | 5.5 |  | 5 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-09-13 10:15 | 57.5 | 41.6 | 0.4 | 0.5 | -43 | 43 | 994 | 2.857 | 50.5 |  | 99 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-09-13 10:13 | 58.2 | 34.2 | 0 | 7.6 | 0 | 0 | 994 | -0.111 | 0 |  | 0 | 16.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-09-13 10:12 | 59.2 | 44.2 | 0 | 0 | -45 | 45 | 994 | 0.72 | 7.4 |  | 99 | 16.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-09-13 10:10 | 57.5 | 41.7 | 0.6 | 0.2 | -47.6 | 47.6 | 994 | -0.214 | 0 |  | 99 | 16.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-09-13 10:09 | 49.7 | 38.2 | 0 | 12.1 | -18.2 | 18.2 | 994 | 12.6 | 67.3 |  | 70 | 20.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-09-13 10:07 | 59.9 | 43.1 | 0 | 0 | -38.2 | 38.2 | 994 | 0.411 | 5.6 |  | 20 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-09-13 10:05 | 0.3 | 3.7 | 17 | 79 | -4.4 | 4.4 | 994 | -0.059 | 0 |  | 0 | 22.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-09-13 10:04 | 50.6 | 38.3 | 0 | 11.1 | -23 | 23 | 994 | 5.345 | 42.3 |  | 50 | 40.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-09-13 10:02 | 51.8 | 38.6 | 0 | 9.6 | -46.1 | 46.1 | 994 | 2.527 | 47.4 |  | 99 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-09-13 10:01 | 58.7 | 44.3 | 0 | 0 | 0.3 | -0.3 | 994 | -0.109 | 0 |  | 25 | 20.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-08-31 10:34 | 44.1 | 35.9 | 0 | 20 | -94.18 | 94.2 | 1025.1 | 1.73 | 11.12 |  | 30 | 15.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-08-31 10:33 | 1.3 | 1.8 | 19.6 | 77.3 | -5.15 | 5.2 | 1025.3 | 1.162 | 0.85 |  | 0 | 16.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-08-31 10:31 | 25.4 | 20.2 | 11.2 | 43.2 | -98.85 | 98.9 | 1025.3 | 0.946 | 8.2 |  | 20 | 15.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-08-31 10:29 | 54.1 | 37.4 | 0 | 8.5 | -62.75 | 62.8 | 1025.3 | 28.722 | 11.28 |  | 100 | 15.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-08-31 10:26 | 0 | 0 | 21 | 79 | -10.76 | 10.8 | 1025.3 | 4.38 | 4.56 |  | 10 | 15.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2017-08-31 10:24 | 0.5 | 0.5 | 20.5 | 78.5 | -1.31 | 1.3 | 1025.3 | 0.028 | 1.49 |  | 0 | 18.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-08-31 10:22 | 32.3 | 32 | 0.5 | 35.2 | -17.31 | 17.3 | 1025.3 | 0.26 | 4.49 |  | 10 | 15.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-08-31 10:21 | 40 | 33.7 | 0 | 26.3 | -92.59 | 92.6 | 1025.3 | 6.397 | 5.28 |  | 20 | 15.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-08-31 10:17 | 52.9 | 39 | 0 | 8.1 | -87.6 | 87.6 | 1025.1 | 2.015 | 25.5 |  | 100 | 16 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-08-31 10:15 | 46.6 | 36.8 | 0 | 16.6 | -10.8 | 10.8 | 1025.1 | 2.508 | 3.45 |  | 10 | 15.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-08-31 10:13 | 38.6 | 33.4 | 0 | 28 | -18.79 | 18.8 | 1025.1 | 0.817 | 7.93 |  | 10 | 16.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-08-31 10:07 | 45.2 | 35.9 | 0 | 18.9 | -81.44 | 81.4 | 1025.3 | 0.123 | 2.98 |  | 10 | 16.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-08-31 10:05 | 0.1 | 0.1 | 21 | 78.8 | 0 | 0 | 1025.3 | 0.013 | 0.09 |  | 0 | 17.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-08-31 10:03 | 44.6 | 35.7 | 0 | 19.7 | -29.09 | 29.1 | 1025.1 | 10.62 | 28.19 |  | 20 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-08-31 10:02 | 5.5 | 3.8 | 19.5 | 71.2 | -95.13 | 95.1 | 1025.1 | 0.351 | 4.99 |  | 20 | 17.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-08-31 09:59 | 52.2 | 37.7 | 0 | 10.1 | -93.43 | 93.4 | 1025.1 | 1.272 | 9.56 |  | 100 | 14.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-08-31 09:57 | 38.5 | 31.5 | 3.6 | 26.4 | -0.3 | 0.3 | 1025.3 | 0.476 | 1.51 |  | 10 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-08-31 09:55 | 50.4 | 37.9 | 0 | 11.7 | -2.87 | 2.9 | 1025.3 | 0.04 | 1.77 |  | 10 | 15.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-08-31 09:54 | 14.8 | 12.9 | 15.3 | 57 | -4.88 | 4.9 | 1025.3 | 0.017 | 0.1 |  | 0 | 19.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-08-31 09:51 | 14.7 | 13.9 | 13.7 | 57.7 | -96.3 | 96.3 | 1025.1 | 0.87 | 7.87 |  | 20 | 16.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-08-31 09:49 | 34.1 | 27.4 | 8.1 | 30.4 | -95.98 | 96 | 1025.3 | 0.332 | 4.86 |  | 20 | 16.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-08-31 09:48 | 49.4 | 36.6 | 0 | 14 | -36.52 | 36.5 | 1025.1 | 1.981 | 12.22 |  | 20 | 17.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-08-31 09:45 | 41 | 35.3 | 0.1 | 23.6 | -1.73 | 1.7 | 1025.1 | 0.745 | 7.63 |  | 10 | 17 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-08-31 08:50 | 61.6 | 38.7 | 0 | 0 | -2.9 | 2.9 | 1021 | 1.538 | 5.5 |  | 99 | 25.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-08-31 08:48 | 58 | 39.1 | 0 | 2.9 | -2.1 | 2.1 | 1021 | 2.128 | 12.8 |  | 99 | 32.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-08-31 08:45 | 57.6 | 39.4 | 0 | 3 | -2.9 | 2.9 | 1020 | 1.424 | 22.2 |  | 99 | 45.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-08-31 08:41 | 58.6 | 40.1 | 0 | 1.3 | -58.9 | 58.9 | 1020 | 0.779 | 1.9 |  | 99 | 16.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-08-31 08:39 | 44.8 | 32.4 | 1.9 | 20.9 | -5.2 | 5.2 | 1020 | 3.982 | 17.5 |  | 15 | 28 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-08-31 08:36 | 42.2 | 34.7 | 0 | 23.1 | -1.4 | 1.4 | 1020 | 1.992 | 3.1 |  | 5 | 16.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-08-31 08:34 | 29 | 28 | 1.6 | 41.4 | -0.7 | 0.7 | 1020 | -0.065 | 0 |  | 2 | 14.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-08-31 08:32 | 42.2 | 32.9 | 2.6 | 22.3 | -44.7 | 44.7 | 1020 | 0.235 | 4.2 |  | 5 | 17.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-08-31 08:30 | 45 | 33.2 | 2.1 | 19.7 | -9.9 | 9.9 | 1020 | 2.154 | 45 |  | 40 | 30.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-08-31 08:26 | 47.7 | 35.9 | 1 | 15.4 | -1.7 | 1.7 | 1020 | 7.061 | 23.3 |  | 35 | 26.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-08-31 08:23 | 62.1 | 41.4 | 0 | 0 | -46.8 | 46.8 | 1020 | 9.421 | 26.3 |  | 99 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-08-31 08:22 | 34.8 | 25.1 | 7.8 | 32.3 | -11.9 | 11.9 | 1020 | 0.454 | 12.8 |  | 10 | 19.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-08-31 08:19 | 53 | 36.1 | 2.7 | 8.2 | -0.2 | 0.2 | 1020 | -0.075 | 0 |  | 10 | 16.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-08-31 08:17 | 0.1 | 0.8 | 14.5 | 84.6 | -0.1 | 0.1 | 1020 | -0.068 | 0 |  | 0 | 16.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-08-31 08:15 | 55.6 | 38.7 | 0 | 5.7 | -5.1 | 5.1 | 1020 | 3.591 | 36.8 |  | 40 | 16.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-08-31 08:14 | 52.4 | 35.2 | 0 | 12.4 | -0.6 | 0.6 | 1020 | -0.033 | 0 |  | 5 | 14.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-08-31 08:12 | 6.1 | 11.1 | 14.4 | 68.4 | 0 | 0 | 1020 | -0.029 | 0 |  | 0 | 12 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-08-31 08:10 | 49.1 | 35.6 | 0 | 15.3 | -39.5 | 39.5 | 1020 | 0.026 | 1.4 |  | 15 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-08-31 08:08 | 55.3 | 37.4 | 0 | 7.3 | -15.5 | 15.5 | 1020 | 4.922 | 42.7 |  | 50 | 20.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-08-31 08:06 | 60.8 | 36.3 | 0.3 | 2.6 | -1.7 | 1.7 | 1020 | 1.944 | 6.3 |  | 22 | 16.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-08-31 08:04 | 57.2 | 33.7 | 1.7 | 7.4 | -0.5 | 0.5 | 1019 | -0.039 | 0 |  | 0 | 17.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-08-31 08:02 | 44.9 | 34.9 | 0 | 20.2 | -54.3 | 54.3 | 1019 | 7.816 | 51.8 |  | 80 | 22.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-08-30 14:12 | 58.1 | 41.4 | 0 | 0.5 | -54.15 | 54.2 | 1020.2 | 3.144 | 48.13 |  | 100 | 14.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-08-30 14:11 | 48.1 | 36.9 | 2.5 | 12.5 | -57.87 | 57.9 | 1020.2 | 1.215 | 20.04 |  | 20 | 16.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-08-30 14:09 | 3.5 | 4.4 | 19.6 | 72.5 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 17.8 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-08-30 14:06 | 29.9 | 26.8 | 10.3 | 33 | -56.7 | 56.7 | 1020.2 | 0.021 | 1.25 |  | 10 | 13.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-08-30 13:55 | 41.7 | 36 | 1.2 | 21.1 | -1.31 | 1.3 | 1021.3 | 0.73 | 3.67 |  | 10 | 15.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-08-30 13:53 | 40.2 | 37.3 | 0 | 22.5 | -1.54 | 1.5 | 1021.3 | 0.195 | 8.28 |  | 10 | 16.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-08-30 13:50 | 43.3 | 37.9 | 0 | 18.8 | -1.82 | 1.8 | 1021.1 | 0.085 | 5.44 |  | 10 | 18.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-08-30 13:46 | 34.5 | 34.4 | 0 | 31.1 | -6.26 | 6.3 | 1020.5 | 0.267 | 4.56 |  | 10 | 16.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-08-30 13:39 | 31.2 | 33.6 | 0 | 35.2 | -2.92 | 2.9 | 1020.2 | 2.488 | 13.64 |  | 10 | 28.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-08-30 13:38 | 35.2 | 35.7 | 0 | 29.1 | 0.1 | -0.1 | 1020.2 | 0.139 | 3.29 |  | 10 | 16.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-08-30 13:36 | 46.6 | 38.4 | 0 | 15 | -54.15 | 54.2 | 1020.2 | 0.218 | 4 |  | 20 | 17.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-08-30 13:34 | 23.6 | 30.7 | 0.1 | 45.6 | 0.09 | -0.1 | 1020.2 | 0.525 | 6.14 |  | 10 | 41.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-08-30 13:31 | 52.8 | 39.6 | 0.5 | 7.1 | -38.65 | 38.7 | 1020.2 | 3.773 | 50.73 |  | 30 | 42 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-08-30 13:29 | 33.3 | 33.8 | 0 | 32.9 | -5.6 | 5.6 | 1020 | 5.858 | 20.74 |  | 10 | 32.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-08-30 12:17 | 48.7 | 38 | 2 | 11.3 | -22.83 | 22.8 | 1019.4 | 25.888 | 42.49 |  | 100 | 38.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-08-30 12:14 | 39.7 | 32.9 | 2.5 | 24.9 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 38.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-08-30 12:12 | 54.7 | 41.5 | 0 | 3.8 | -35.57 | 35.6 | 1020 | 14.584 | 100.02 |  | 100 | 38.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-08-30 12:10 | 54.1 | 41.9 | 0 | 4 | -36.31 | 36.3 | 1020.2 | 8.986 | 53 |  | 100 | 38.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-08-30 12:08 | 52.5 | 40.5 | 0.3 | 6.7 | -30.37 | 30.4 | 1020.2 | 20.991 | 80.23 |  | 100 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-08-30 12:06 | 44.3 | 34.5 | 0 | 21.2 | -9.9 | 9.9 | 1016 | 1.056 | 19.4 |  | 15 | 23.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-08-30 12:05 | 57.9 | 41.6 | 0.1 | 0.4 | -10.84 | 10.8 | 1020 | 0.598 | 14.17 |  | 10 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-08-30 12:04 | 62.6 | 40.2 | 0 | 0 | 0 | 0 | 1016 | 0.151 | 7.7 |  | 15 | 14.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-08-30 12:02 | 58.8 | 40.3 | 0.4 | 0.5 | -54.1 | 54.1 | 1016 | 0.473 | 6 |  | 70 | 21.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-08-30 12:02 | 7.3 | 5.6 | 20.2 | 66.9 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 24.9 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-08-30 12:00 | 33.5 | 33.8 | 1.5 | 31.2 | -4.03 | 4 | 1020.2 | 5.376 | 20.08 |  | 10 | 26.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-08-30 11:59 | 19.3 | 14.4 | 15.5 | 50.8 | -55 | 55 | 1016 | 0.035 | 5.7 |  | 99 | 12.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-08-30 11:58 | 0.2 | 0.1 | 22.3 | 77.4 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 12.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-08-30 11:57 | 49.8 | 33.4 | 3.1 | 13.7 | -0.5 | 0.5 | 1016 | -0.184 | 0 |  | 20 | 15.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-08-30 11:56 | 16.9 | 14.4 | 16.6 | 52.1 | 0 | 0 | 1020 | 0 | 0 |  | 0 | 16 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-08-30 11:55 | 47.9 | 36.7 | 0 | 15.4 | -5.6 | 5.6 | 1016 | 0.204 | 8.6 |  | 12 | 20.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-08-30 11:54 | 4.2 | 2.9 | 21.2 | 71.7 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 14.2 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-08-30 11:53 | 47.2 | 36.6 | 0 | 16.2 | -1.5 | 1.5 | 1016 | 1.261 | 9.9 |  | 15 | 19.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-08-30 11:51 | 0.1 | 0.2 | 18 | 81.7 | -0.7 | 0.7 | 1016 | -0.408 | 0 |  | 0 | 13.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-08-30 11:51 | 56.4 | 43 | 0 | 0.6 | -45.12 | 45.1 | 1020.2 | 2.792 | 29.61 |  | 30 | 35.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-08-30 11:50 | 62.4 | 38.8 | 0 | 0 | -55.2 | 55.2 | 1016 | 0.942 | 8.6 |  | 99 | 17.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-08-30 11:48 | 24.7 | 17.6 | 13 | 44.7 | -38 | 38 | 1016 | -0.509 | 0 |  | 10 | 15.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-08-30 11:47 | 49.2 | 39.3 | 0.7 | 10.8 | -7.77 | 7.8 | 1020.2 | 2.011 | 25.47 |  | 10 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-08-30 11:46 | 49.7 | 37.8 | 0.4 | 12.1 | -1.5 | 1.5 | 1017 | 1.69 | 11.4 |  | 12 | 27.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-08-30 11:45 | 57.2 | 41 | 0 | 1.8 | -50.96 | 51 | 1020.2 | 0.051 | 5.94 |  | 100 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-08-30 11:42 | 48.9 | 36.5 | 0 | 14.6 | -4 | 4 | 1017 | 10.126 | 27.5 |  | 40 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-08-30 11:42 | 45.9 | 38.2 | 0 | 15.9 | -8 | 8 | 1020 | 10.744 | 28.44 |  | 20 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-08-30 11:40 | 45 | 37.5 | 0.1 | 17.4 | -6.9 | 6.9 | 1020 | 13.199 | 31.23 |  | 10 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-08-30 11:39 | 61.7 | 41.2 | 0.2 | 0 | -3.7 | 3.7 | 1016 | 0.21 | 4.1 |  | 99 | 14.2 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-08-30 11:38 | 46.8 | 38.2 | 0.8 | 14.2 | -7.64 | 7.6 | 1020.2 | 1.635 | 23.72 |  | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-08-30 11:36 | 48.3 | 37.2 | 0 | 14.5 | -0.7 | 0.7 | 1016 | 0.337 | 10.8 |  | 25 | 33.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-08-30 11:36 | 5.1 | 4 | 20.8 | 70.1 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 14.2 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-08-30 11:30 | 39.4 | 31.9 | 3.4 | 25.3 | -10.4 | 10.4 | 1015 | 0.618 | 14.8 |  | 50 | 21.5 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-08-30 11:26 | 58.6 | 39.9 | 0 | 1.5 | -68.4 | 68.4 | 1015 | 0.332 | 10.8 |  | 99 | 17.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-08-30 11:24 | 42.5 | 34.9 | 0 | 22.6 | -37.5 | 37.5 | 1015 | 7.739 | 23.8 |  | 40 | 27.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-08-30 11:20 | 59.1 | 39.8 | 0 | 1.1 | -66.4 | 66.4 | 1015 | 0.27 | 4.5 |  | 99 | 17.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-08-30 11:18 | 51.9 | 36 | 0 | 12.1 | -6.5 | 6.5 | 1015 | 3.663 | 17.2 |  | 40 | 15.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-08-30 11:17 | 45.9 | 36.8 | 0 | 17.3 | -2.6 | 2.6 | 1015 | 8.557 | 25.2 |  | 40 | 34.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-08-30 11:14 | 58.5 | 40.5 | 0 | 1 | -7.9 | 7.9 | 1015 | 0.939 | 8.7 |  | 25 | 16.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-08-30 11:12 | 38.3 | 32.8 | 0.8 | 28.1 | -5.7 | 5.7 | 1015 | 3.955 | 17.5 |  | 10 | 18.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-08-30 11:12 | 49.4 | 38.3 | 0.1 | 12.2 | -17.63 | 17.6 | 1021.4 | 0.381 | 11.54 |  | 10 | 13 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-08-30 11:09 | 49 | 35.6 | 1.3 | 14.1 | -114.6 | 114.6 | 1015 | 30.505 | 98.2 |  | 80 | 31.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-08-30 11:06 | 38.3 | 34 | 0 | 27.7 | -0.9 | 0.9 | 1015 | 3.268 | 15.8 |  | 15 | 22.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-08-30 11:04 | 44 | 36.2 | 0 | 19.8 | -3.6 | 3.6 | 1015 | 1.723 | 24.8 |  | 22 | 22.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-08-30 11:01 | 47.1 | 35.6 | 0 | 17.3 | -23 | 23 | 1015 | 1.13 | 19.6 |  | 20 | 35.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-08-30 10:59 | 41.1 | 32.8 | 0 | 26.1 | -10.8 | 10.8 | 1015 | 9.013 | 56.1 |  | 40 | 29.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-08-30 10:59 | 0.1 | 0.1 | 22.1 | 77.7 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 13.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-08-30 10:58 | 43.8 | 30.8 | 6.2 | 19.2 | 0 | 0 | 1020.5 | 0 | 0 |  | 0 | 13.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-08-30 10:56 | 36.2 | 29.7 | 2.9 | 31.2 | -57.1 | 57.1 | 1015 | 0.038 | 3.6 |  | 80 | 17.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-08-30 10:56 | 0.3 | 0.3 | 21.9 | 77.5 | 0 | 0 | 1021.3 | 0 | 0 |  | 0 | 13.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-08-30 10:54 | 20.4 | 20.4 | 5.8 | 53.4 | -1.3 | 1.3 | 1015 | 0.613 | 14.7 |  | 10 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-08-30 10:54 | 41 | 34.1 | 3 | 21.9 | -22.83 | 22.8 | 1020.2 | 3.516 | 16.42 |  | 10 | 14.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-08-30 10:52 | 47 | 36.9 | 0 | 16.1 | -57 | 57 | 1015 | 0.509 | 21.3 |  | 99 | 29.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-08-30 10:51 | 28.9 | 33.7 | 1.3 | 36.1 | -0.68 | 0.7 | 1020.2 | 0.016 | 2.38 |  | 10 | 18.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-08-30 10:49 | 49.5 | 37.3 | 0.1 | 13.1 | -27.07 | 27.1 | 1020 | 12.424 | 63.98 |  | 20 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-08-30 10:47 | 9.8 | 8.3 | 18.3 | 63.6 | 0 | 0 | 1020.2 | 0 | 0 |  | 0 | 11.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-08-30 10:45 | 47 | 39.1 | 0 | 13.9 | -1.39 | 1.4 | 1021.3 | 0.237 | 9.07 |  | 20 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-08-30 10:42 | 50.6 | 39.4 | 0 | 10 | -3.66 | 3.7 | 1020.8 | 6.673 | 22.55 |  | 20 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-08-30 10:40 | 52.4 | 39.6 | 0 | 8 | -5.75 | 5.8 | 1021.4 | 1.469 | 22.53 |  | 10 | 19.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-08-30 10:38 | 47.7 | 38.5 | 0 | 13.8 | -5.86 | 5.9 | 1020.2 | 1.365 | 21.76 |  | 10 | 18.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-08-30 10:35 | 49.5 | 38.5 | 0.8 | 11.2 | -0.86 | 0.9 | 1020.2 | 0.176 | 7.82 |  | 10 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-08-30 10:32 | 53.2 | 40.4 | 0 | 6.4 | -0.86 | 0.9 | 1020.2 | 0.042 | 1.79 |  | 10 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-08-30 10:29 | 57.6 | 41.5 | 0 | 0.9 | -1.28 | 1.3 | 1020.2 | 1.484 | 10.71 |  | 10 | 19 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-08-30 10:26 | 39.5 | 35.2 | 3.4 | 21.9 | -5.58 | 5.6 | 1020.2 | 10.46 | 28.52 |  | 10 | 14.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-08-30 09:46 | 16.7 | 23.5 | 6.5 | 53.3 | -0.56 | 0.6 | 1019.5 | 0.282 | 4.62 |  | 10 | 25.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-08-29 13:46 | 49.7 | 38.4 | 0 | 11.9 | -67.95 | 68 | 1015.7 | 0.601 | 13.76 |  | 20 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-08-29 13:44 | 48.5 | 37.9 | 0 | 13.6 | -8.37 | 8.4 | 1016.2 | 5.783 | 43.47 |  | 10 | 33 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-08-29 13:42 | 48.3 | 37.6 | 0.4 | 13.7 | -4.51 | 4.5 | 1016.2 | 3.459 | 33.52 |  | 10 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-08-29 13:39 | 45.4 | 32.3 | 14.9 | 7.4 | -13.91 | 13.9 | 1016.2 | 7.928 | 51.15 |  | 20 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-08-29 13:37 | 58.5 | 41.5 | 0 | 0 | 0.26 | -0.3 | 1016.3 | 0.028 | 1.48 |  | 10 | 21.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-08-29 13:34 | 52.4 | 39 | 0.3 | 8.3 | -5.85 | 5.9 | 1016.3 | 19.399 | 38.55 |  | 20 | 15.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-08-29 13:33 | 58 | 42 | 0 | 0 | 0.49 | -0.5 | 1016.2 | 0.172 | 0.9 |  | 10 | 17.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-08-29 13:31 | 53.9 | 40.3 | 0 | 5.8 | -1.65 | 1.7 | 1016.2 | 0.707 | 3.61 |  | 10 | 14.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-08-29 13:28 | 52.4 | 39.9 | 0 | 7.7 | 0.35 | -0.4 | 1016.2 | 2.462 | 3.43 |  | 10 | 14.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-08-29 13:19 | 47.4 | 38.2 | 0 | 14.4 | -1.73 | 1.7 | 1016.3 | 0.389 | 11.61 |  | 10 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-08-29 13:17 | 50 | 37.8 | 0.3 | 11.9 | -1.68 | 1.7 | 1016.2 | 2.386 | 27.86 |  | 20 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-08-29 13:15 | 52.4 | 40.3 | 0.5 | 6.8 | -5.33 | 5.3 | 1016.3 | 2.387 | 28.07 |  | 20 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-08-29 13:13 | 55 | 41.3 | 0 | 3.7 | -0.15 | 0.2 | 1016 | 0.036 | 3.5 |  | 10 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-08-29 13:11 | 52.5 | 39.5 | 0.1 | 7.9 | -3.21 | 3.2 | 1015.7 | 9.361 | 26.73 |  | 10 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-08-29 13:09 | 2.2 | 1.1 | 20.7 | 76 | 0 | 0 | 1015.7 | 0 | 0 |  | 0 | 14.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-08-29 13:07 | 58.9 | 41.1 | 0 | 0 | -7.64 | 7.6 | 1016.3 | 20.092 | 82.67 |  | 50 | 18.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-08-29 13:05 | 51.3 | 39.5 | 0 | 9.2 | -6.26 | 6.3 | 1016.3 | 1.181 | 19.92 |  | 20 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-08-29 13:03 | 49.2 | 39.1 | 0.3 | 11.4 | -1.07 | 1.1 | 1016.2 | 1.435 | 21.91 |  | 20 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-08-29 13:00 | 49.3 | 38.6 | 0.1 | 12 | -16.14 | 16.1 | 1015.7 | 18.719 | 76.63 |  | 50 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-08-29 12:58 | 19.7 | 19.6 | 11.9 | 48.8 | -36.52 | 36.5 | 1016.3 | 0.389 | 17.01 |  | 50 | 15.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-08-29 12:55 | 50.4 | 38.9 | 0 | 10.7 | -1.29 | 1.3 | 1016.3 | 14.371 | 8.04 |  | 10 | 29.8 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-08-29 12:39 | 54.9 | 39.7 | 0.3 | 5.1 | -3.79 | 3.8 | 1015 | 3.887 | 16.95 |  | 20 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-08-29 12:35 | 48.9 | 38.5 | 0.9 | 11.7 | -0.53 | 0.5 | 1015.5 | 2.667 | 6.94 |  | 10 | 20.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-08-29 12:32 | 41 | 36.1 | 0.7 | 22.2 | -3.4 | 3.4 | 1015.4 | 1.029 | 27.62 |  | 10 | 26.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-08-29 12:30 | 9.5 | 8.5 | 17.2 | 64.8 | 0 | 0 | 1015.7 | 0 | 0 |  | 0 | 14.9 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-08-29 12:26 | 58.1 | 41.9 | 0 | 0 | -0.08 | 0.1 | 1015.5 | 3.273 | 15.8 |  | 10 | 21.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-08-29 12:21 | 51.9 | 41 | 0.3 | 6.8 | -9.85 | 9.9 | 1016.2 | 6.829 | 22.31 |  | 10 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-08-29 12:19 | 57.6 | 42.1 | 0 | 0.3 | -1.97 | 2 | 1015.7 | 6.048 | 21.6 |  | 10 | 17.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-08-29 12:17 | 48.6 | 38.5 | 0 | 12.9 | -6.68 | 6.7 | 1016.3 | 11.635 | 29.86 |  | 10 | 17.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-08-29 11:56 | 49.4 | 40.3 | 0 | 10.3 | -3.61 | 3.6 | 1014.9 | 13.41 | 7.91 |  | 10 | 17.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-08-29 11:54 | 38.6 | 36.2 | 0 | 25.2 | 0 | 0 | 1015 | 0 | 0 |  | 0 | 28.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-08-29 11:52 | 41.6 | 36.6 | 0.8 | 21 | -1.15 | 1.2 | 1015.2 | 8.375 | 24.74 |  | 10 | 33.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-08-29 11:50 | 54.9 | 40.9 | 0 | 4.2 | -52.98 | 53 | 1015 | 0.859 | 24.25 |  | 100 | 35 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-08-29 11:47 | 44.8 | 35.4 | 4.4 | 15.4 | -26.44 | 26.4 | 1015 | 0.866 | 8.11 |  | 10 | 15.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-08-29 11:45 | 46.2 | 39.9 | 0.1 | 13.8 | -39.18 | 39.2 | 1015 | 6.48 | 20.97 |  | 20 | 44.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-08-29 11:43 | 43 | 37.1 | 1.9 | 18 | 0 | 0 | 1014.9 | 0 | 0 |  | 0 | 34.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-08-29 11:40 | 45.6 | 39.3 | 0 | 15.1 | -14.55 | 14.6 | 1015.5 | 7.405 | 22.78 |  | 20 | 42.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-08-29 11:38 | 56.1 | 42.2 | 0.4 | 1.3 | -12.1 | 12.1 | 1015.5 | 6.673 | 5.53 |  | 10 | 22.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-08-29 11:36 | 25.3 | 32.4 | 0.1 | 42.2 | -2.44 | 2.4 | 1015.7 | 0.836 | 1.99 |  | 10 | 16.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-08-29 11:21 | 39.3 | 37.4 | 0.1 | 23.2 | -2.55 | 2.6 | 1015.7 | 3.804 | 16.29 |  | 30 | 48.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-08-29 11:19 | 52.2 | 38.9 | 0.6 | 8.3 | -24.21 | 24.2 | 1014.9 | 2.792 | 43.49 |  | 50 | 47.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-08-29 11:17 | 49.3 | 39.3 | 0.8 | 10.6 | -0.47 | 0.5 | 1015.8 | 0.583 | 3.17 |  | 10 | 35 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-08-29 11:15 | 46.4 | 38.1 | 0.1 | 15.4 | -2.61 | 2.6 | 1016 | 2.716 | 14.1 |  | 10 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-08-29 11:12 | 33.3 | 31.9 | 5.3 | 29.5 | 0 | 0 | 1015.8 | 0 | 0 |  | 0 | 15.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-08-29 11:10 | 46 | 37.7 | 0.9 | 15.4 | -22.08 | 22.1 | 1015 | 22.769 | 123.15 |  | 20 | 49 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-08-29 11:08 | 17.1 | 21.3 | 9.3 | 52.3 | -1 | 1 | 1015.2 | 0.627 | 14.46 |  | 10 | 30.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-08-29 11:04 | 38.1 | 34.8 | 1.1 | 26 | -1.12 | 1.1 | 1015.5 | 1.711 | 11.54 |  | 10 | 16 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-08-29 11:02 | 43.4 | 37.7 | 0.8 | 18.1 | 0.03 | 0 | 1015 | 0.153 | 3.36 |  | 10 | 32 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-08-29 10:59 | 50.6 | 41.1 | 0.3 | 8 | -24.63 | 24.6 | 1015.2 | 18.17 | 8.96 |  | 100 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-08-29 10:56 | 50.7 | 38.7 | 0.9 | 9.7 | -19.64 | 19.6 | 1015.2 | 32.838 | 101.92 |  | 50 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-08-29 10:54 | 34.5 | 35.6 | 0 | 29.9 | -1.44 | 1.4 | 1015.7 | 1.628 | 23.57 |  | 10 | 22.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-08-29 10:52 | 54.6 | 41.1 | 0.3 | 4 | -27.29 | 27.3 | 1014.9 | 11.298 | 28.95 |  | 100 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-08-29 10:49 | 42.7 | 36.9 | 1.3 | 19.1 | -46.72 | 46.7 | 1015 | 0.089 | 8.06 |  | 10 | 18.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-08-29 10:46 | 49.8 | 39.5 | 0.6 | 10.1 | -3.61 | 3.6 | 1015.4 | 10.476 | 28.28 |  | 20 | 19 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-08-29 10:44 | 38.2 | 35.6 | 0.4 | 25.8 | -0.62 | 0.6 | 1015 | 0.199 | 8.17 |  | 10 | 28 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-08-29 10:42 | 50 | 39.1 | 0.5 | 10.4 | -43.53 | 43.5 | 1015.5 | 8.137 | 74.41 |  | 100 | 38.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-08-29 10:38 | 52 | 39.7 | 0.1 | 8.2 | -11.32 | 11.3 | 1015 | 7.636 | 49.98 |  | 20 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-08-29 10:17 | 53.8 | 39.1 | 0.3 | 6.8 | -6.97 | 7 | 1016.3 | 1.727 | 23.98 |  | 10 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-08-29 10:14 | 46 | 37.5 | 0.8 | 15.7 | -12.22 | 12.2 | 1016.3 | 73.434 | 71.11 |  | 100 | 35.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-08-29 10:11 | 48.5 | 38.5 | 0.5 | 12.5 | -10.91 | 10.9 | 1016.3 | 20.595 | 39.4 |  | 10 | 18.9 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-08-29 10:08 | 46.3 | 37.4 | 3.1 | 13.2 | -83.56 | 83.6 | 1016.3 | 0.821 | 15.96 |  | 10 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-08-29 10:05 | 27.8 | 27.7 | 3.6 | 40.9 | -2.96 | 3 | 1016.3 | 1.753 | 5.54 |  | 10 | 29 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-08-29 09:49 | 46.2 | 36.6 | 0.4 | 16.8 | -12.01 | 12 | 1016.3 | 6.241 | 21.63 |  | 10 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-08-29 09:48 | 48 | 37.3 | 0 | 14.7 | -5.16 | 5.2 | 1016.2 | 10.137 | 27.3 |  | 10 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-08-29 09:39 | 47.9 | 36.4 | 0.6 | 15.1 | -7.32 | 7.3 | 1016.2 | 4.388 | 18.05 |  | 10 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-07-28 15:26 | 53.4 | 36.3 | 0 | 10.3 | -0.7 | 0.7 | 1010 | 4.14 | 18.2 | 102 | 40 | 22.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-07-28 15:24 | 44 | 32.1 | 1.7 | 22.2 | 0 | 0 | 1010 | 1.39 | 10.5 | 48 | 15 | 21.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-07-28 15:22 | 49.5 | 35.9 | 0.4 | 14.2 | 0 | 0 | 1010 | 0.2 | 3.9 | 20 | 25 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-07-28 15:20 | 54.8 | 37.7 | 0 | 7.5 | -1.8 | 1.8 | 1010 | 3.49 | 16.9 | 97 | 40 | 14.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-07-28 15:17 | 58.2 | 38.4 | 0 | 3.4 | -0.6 | 0.6 | 1010 | 0.18 | 3.7 | 23 | 20 | 26.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-07-28 15:15 | 53.4 | 37.3 | 0 | 9.3 | -0.1 | 0.1 | 1010 | 1.18 | 9.6 | 54 | 20 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-07-28 15:13 | 59.6 | 38.6 | 0.5 | 1.3 | -0.5 | 0.5 | 1010 | 1.7 | 11.6 | 73 | 20 | 26 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-07-28 15:09 | 63.3 | 41.9 | 0 | 0 | -19.4 | 19.4 | 1010 | 21.04 | 87 | 577 | 99 | 31.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-07-28 15:07 | 62.9 | 42.5 | 0 | 0 | -36.8 | 36.8 | 1010 | -0.32 | 0 | 0 | 99 | 18.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-07-28 15:06 | 61.6 | 42.4 | 0 | 0 | -5.1 | 5.1 | 1010 | 13.33 | 32.7 | 211 | 70 | 22 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-07-28 15:04 | 61.9 | 42.4 | 0 | 0 | -1.2 | 1.2 | 1010 | 30.69 | 49.5 | 321 | 50 | 24.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-07-28 14:48 | 61.5 | 41.6 | 0 | 0 | -49.7 | 49.7 | 1007 | 4.54 | 66.2 | 427 | 99 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-07-28 14:46 | 30.3 | 21.7 | 13.1 | 34.9 | -53.1 | 53.1 | 1007 | -0.26 | 0 | 0 | 99 | 17.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-07-28 14:45 | 10.1 | 8.3 | 14.4 | 67.2 | -2.2 | 2.2 | 1007 | -0.12 | 0 | 0 | 0 | 20.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-07-28 14:44 | 41 | 34.3 | 0.2 | 24.5 | -1.2 | 1.2 | 1007 | 0.06 | 4.5 | 19 | 25 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-07-28 14:42 | 40.7 | 31.6 | 3.4 | 24.3 | -12.8 | 12.8 | 1007 | 7.82 | 51.2 | 218 | 45 | 41.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-07-28 14:40 | 60.7 | 41.5 | 0 | 0 | -53.5 | 53.5 | 1007 | 0.06 | 4.5 | 28 | 99 | 20.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-07-28 14:38 | 6.3 | 4.3 | 18.6 | 70.8 | -53 | 53 | 1009 | -0.07 | 0 | 0 | 99 | 18.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-07-28 14:34 | 51.3 | 37 | 0 | 11.7 | -4.1 | 4.1 | 1009 | 9.17 | 26.2 | 141 | 50 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-07-28 14:31 | 49.6 | 37.4 | 0 | 13 | -0.7 | 0.7 | 1008 | 0.45 | 12.5 | 65 | 20 | 36.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-07-28 13:51 | 39.3 | 31.2 | 2.7 | 26.8 | -0.7 | 0.7 | 1009 | 6.6 | 22.4 | 92 | 20 | 27.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-07-28 13:50 | 46 | 33.6 | 1.9 | 18.5 | -4.5 | 4.5 | 1009 | 8.65 | 55.5 | 267 | 45 | 29.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-07-28 13:48 | 45.2 | 32.8 | 1.7 | 20.3 | -3.2 | 3.2 | 1008 | 14.92 | 34.2 | 162 | 40 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-07-28 13:46 | 49.3 | 37.3 | 0 | 13.4 | -27.5 | 27.5 | 1008 | 2.61 | 30.2 | 156 | 50 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-07-28 13:45 | 55.4 | 38.8 | 0.4 | 5.4 | -24.7 | 24.7 | 1008 | 11.36 | 29.6 | 171 | 40 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-07-28 13:43 | 33.9 | 24.4 | 7.1 | 34.6 | -0.3 | 0.3 | 1008 | -0.03 | 0 | 0 | 5 | 18.4 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-07-28 13:42 | 47 | 36.7 | 0 | 16.3 | -2.3 | 2.3 | 1008 | 1.29 | 4.9 | 24 | 10 | 22.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-07-28 13:41 | 56.5 | 38.5 | 0 | 5 | -36 | 36 | 1008 | 9.67 | 96 | 568 | 99 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-07-28 13:39 | 42 | 29.6 | 3.1 | 25.3 | -0.2 | 0.2 | 1008 | 0.09 | 0.6 | 2 | 0 | 16.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-07-28 13:37 | 44.7 | 34.1 | 0 | 21.2 | -3.2 | 3.2 | 1009 | 4.08 | 17.9 | 83 | 22 | 20.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-07-28 13:35 | 48.6 | 35.7 | 0 | 15.7 | -6.5 | 6.5 | 1009 | 3.06 | 33.2 | 168 | 40 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-07-28 13:34 | 46.5 | 36.5 | 0.2 | 16.8 | -1.7 | 1.7 | 1009 | 3.37 | 15.8 | 77 | 25 | 34.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-07-28 13:32 | 50.8 | 37.1 | 0 | 12.1 | -32.2 | 32.2 | 1008 | 20.04 | 83.6 | 445 | 99 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-07-28 13:29 | 44.4 | 36.1 | 0 | 19.5 | -0.2 | 0.2 | 1008 | 7.66 | 12.1 | 56 | 20 | 18.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-07-28 13:27 | 46.4 | 36.8 | 0 | 16.8 | -4 | 4 | 1008 | 3.36 | 15.7 | 76 | 25 | 36 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-07-28 13:26 | 50.4 | 39.3 | 0 | 10.3 | -34.2 | 34.2 | 1008 | 21.07 | 135.5 | 715 | 99 | 44.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-07-28 13:25 | 37.3 | 33.7 | 0 | 29 | -3.3 | 3.3 | 1008 | 0.24 | 4.3 | 17 | 7 | 16.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-07-28 13:22 | 49 | 36.2 | 2.7 | 12.1 | -1.7 | 1.7 | 1008 | 1.07 | 19.7 | 101 | 25 | 22 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-07-28 13:21 | 46.7 | 37.5 | 0 | 15.8 | -3 | 3 | 1008 | 1.37 | 21.6 | 105 | 22 | 37.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-07-28 13:19 | 42 | 35 | 0 | 23 | -9.7 | 9.7 | 1008 | 9.79 | 57.5 | 253 | 45 | 37 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-07-28 13:17 | 53.8 | 38.9 | 1.1 | 6.2 | -0.1 | 0.1 | 1008 | 4.81 | 9.6 | 54 | 20 | 21.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-07-28 13:15 | 52.2 | 37.6 | 0 | 10.2 | -7.1 | 7.1 | 1008 | 21.21 | 40.9 | 224 | 50 | 22.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-07-28 13:14 | 47.5 | 36.8 | 0 | 15.7 | -33.5 | 33.5 | 1008 | 0.4 | 11.8 | 58 | 15 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-07-28 13:12 | 45.8 | 34.2 | 0.7 | 19.3 | -6.3 | 6.3 | 1008 | 2.76 | 31.9 | 153 | 20 | 17 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-07-28 13:11 | 53 | 37.2 | 1.9 | 7.9 | 0 | 0 | 1008 | 0.88 | 2.1 | 11 | 5 | 18.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-07-28 13:09 | 43.6 | 37 | 0 | 19.4 | -0.2 | 0.2 | 1008 | 7.57 | 6 | 27 | 5 | 24.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-07-28 12:39 | 54.7 | 40.5 | 0.2 | 4.6 | -44 | 44 | 1008 | 6.84 | 77.7 | 445 | 99 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-07-28 12:38 | 60 | 41.6 | 0 | 0 | 0.1 | -0.1 | 1008 | 0.04 | 0.4 | 2 | 2 | 23.3 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-07-28 12:36 | 59.7 | 43.7 | 0 | 0 | -47 | 47 | 1008 | 1.3 | 9.7 | 61 | 99 | 31 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-07-28 12:34 | 60.4 | 42.5 | 0 | 0 | -48.1 | 48.1 | 1008 | -0.14 | 0 | 0 | 99 | 14.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-07-28 12:32 | 44.9 | 36.2 | 0 | 18.9 | -23.1 | 23.1 | 1008 | 14.74 | 72.4 | 340 | 50 | 19.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-07-28 12:30 | 45.3 | 36.7 | 0 | 18 | -7.6 | 7.6 | 1008 | 2.92 | 14.7 | 69 | 20 | 33.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-07-28 12:28 | 0.2 | 2.3 | 18 | 79.5 | -4.3 | 4.3 | 1009 | -0.12 | 0 | 0 | 0 | 25.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-07-28 12:27 | 47.1 | 37.3 | 0 | 15.6 | -23.5 | 23.5 | 1009 | 5.15 | 41.4 | 204 | 50 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-07-28 12:25 | 48.3 | 37.6 | 0 | 14.1 | -45.6 | 45.6 | 1009 | 3.17 | 52.9 | 267 | 99 | 36.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-07-28 12:24 | 43.9 | 35.9 | 1.7 | 18.5 | -1.3 | 1.3 | 1010 | 2.59 | 13.6 | 62 | 20 | 45.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-07-28 12:19 | 47.9 | 35.3 | 0.1 | 16.7 | -10.1 | 10.1 | 1010 | 1.13 | 20.1 | 101 | 25 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-07-28 12:18 | 4.1 | 3 | 18.3 | 74.6 | -53.9 | 53.9 | 1010 | -0.22 | 0 | 0 | 99 | 22.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-07-28 12:17 | 57.3 | 40.2 | 0.8 | 1.7 | -45.7 | 45.7 | 1010 | 3.69 | 16.4 | 98 | 50 | 32.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-07-28 12:14 | 10.2 | 7 | 18.3 | 64.5 | -55 | 55 | 1010 | -0.14 | 0 | 0 | 99 | 13.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-07-28 12:13 | 42.7 | 29 | 5.3 | 23 | -1 | 1 | 1010 | 0.51 | 6.4 | 28 | 5 | 19.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-07-28 12:11 | 45.7 | 36.2 | 0 | 18.1 | -7.7 | 7.7 | 1010 | 1.03 | 19.1 | 91 | 20 | 22.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-07-28 12:09 | 48.3 | 36.8 | 0.1 | 14.8 | -1.5 | 1.5 | 1010 | 1.63 | 11.3 | 57 | 15 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-07-28 12:07 | 0.2 | 0.2 | 18.5 | 81.1 | -0.8 | 0.8 | 1010 | -0.12 | 0 | 0 | 0 | 16.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-07-28 12:06 | 62.5 | 39.1 | 0 | 0 | -53.4 | 53.4 | 1010 | 1.05 | 9.1 | 59 | 99 | 18.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-07-28 12:05 | 10.6 | 7 | 18.1 | 64.3 | -38.5 | 38.5 | 1010 | -0.05 | 0 | 0 | 5 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-07-28 12:03 | 49.9 | 37.8 | 0.7 | 11.6 | -1.6 | 1.6 | 1010 | 2.28 | 13.2 | 69 | 25 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-07-28 11:13 | 56.4 | 41.2 | 0 | 2.4 | -28.2 | 28.2 | 1008 | 21.25 | 84.4 | 498 | 99 | 42.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-07-28 11:12 | 58 | 42.6 | 0 | 0 | -35.9 | 35.9 | 1008 | 10.23 | 58.6 | 356 | 99 | 38.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-07-28 11:10 | 58.7 | 42 | 0 | 0 | -34.8 | 34.8 | 1008 | 13.19 | 109.4 | 673 | 99 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-07-28 11:09 | 36.7 | 29.6 | 5 | 28.7 | -4 | 4 | 1008 | -0.95 | 0 | 0 | 0 | 19.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-07-28 11:07 | 54.8 | 39.6 | 0.8 | 4.8 | -28.1 | 28.1 | 1008 | 15.62 | 73 | 419 | 99 | 37.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-07-28 11:06 | 61.3 | 42.4 | 0.8 | 0 | 0.7 | -0.7 | 1008 | -0.01 | 0 | 0 | 2 | 20.6 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-07-28 11:04 | 4.9 | 3.5 | 18.5 | 73.1 | -46.5 | 46.5 | 1008 | 0.42 | 5.5 | 2 | 99 | 27 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-07-28 11:02 | 48.2 | 37.2 | 0.8 | 13.8 | -4.2 | 4.2 | 1008 | 8.68 | 25.9 | 131 | 25 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-07-28 11:00 | 59.7 | 40.8 | 0 | 0 | -45.6 | 45.6 | 1008 | 1.48 | 22.5 | 141 | 50 | 33.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-07-28 10:58 | 61.7 | 42.9 | 0 | 0 | -27.9 | 27.9 | 1008 | 0.76 | 16.4 | 106 | 45 | 30 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-07-28 10:54 | 8 | 5.5 | 18.1 | 68.4 | -47.9 | 47.9 | 1008 | -0.18 | 0 | 0 | 99 | 16.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-07-28 10:52 | 12 | 7.7 | 17.5 | 62.8 | -47.8 | 47.8 | 1008 | -0.13 | 0 | 0 | 99 | 15.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-07-28 10:51 | 14 | 9.5 | 18.3 | 58.2 | -36.5 | 36.5 | 1008 | -0.23 | 0 | 0 | 0 | 19.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-07-28 10:49 | 59.9 | 40.9 | 0 | 0 | -43.4 | 43.4 | 1008 | 2.6 | 48.6 | 305 | 99 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-07-28 10:47 | 48.7 | 37.1 | 0.4 | 13.8 | -9.5 | 9.5 | 1008 | 17.95 | 37.3 | 190 | 40 | 22.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-07-28 10:46 | 50.2 | 37.5 | 0 | 12.3 | -6.4 | 6.4 | 1008 | 12.62 | 31.1 | 163 | 40 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-07-28 10:44 | 47.7 | 37 | 0.9 | 14.4 | -7.9 | 7.9 | 1007 | 2.37 | 29.3 | 146 | 25 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-07-28 10:43 | 23.7 | 17.9 | 12.7 | 45.7 | -48.8 | 48.8 | 1007 | -0.04 | 0 | 0 | 99 | 19.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-07-28 10:09 | 39.3 | 28.7 | 8.1 | 23.9 | -2 | 2 | 1009 | 0.03 | 1.6 | 6 | 99 | 14.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-07-28 10:07 | 62.2 | 39.3 | 0 | 0 | -2.8 | 2.8 | 1009 | 1.92 | 6.2 | 40 | 99 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-07-28 10:05 | 60.2 | 39.7 | 0 | 0.1 | -1.4 | 1.4 | 1009 | 1.87 | 12.2 | 77 | 99 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-07-28 10:02 | 56.4 | 39.5 | 0 | 4.1 | -2.7 | 2.7 | 1009 | 1.81 | 25 | 148 | 99 | 43.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-07-28 09:59 | 60.7 | 41.2 | 0 | 0 | -40.5 | 40.5 | 1009 | 0.34 | 1.2 | 8 | 99 | 16.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-07-28 09:57 | 50.4 | 34.5 | 1.5 | 13.6 | -4.6 | 4.6 | 1009 | 3.12 | 15.6 | 82 | 20 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-07-28 09:56 | 45.4 | 35.2 | 0.6 | 18.8 | -0.7 | 0.7 | 1009 | 1.99 | 3.1 | 15 | 5 | 16.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-07-28 09:54 | 31.7 | 28.5 | 1.7 | 38.1 | -1.2 | 1.2 | 1009 | 0.14 | 7.2 | 24 | 2 | 15.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-07-28 09:52 | 37.7 | 30.9 | 2.8 | 28.6 | -42.4 | 42.4 | 1009 | 0.1 | 2.7 | 10 | 5 | 22.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-07-28 09:50 | 43.6 | 32.7 | 2.6 | 21.1 | -17.4 | 17.4 | 1009 | 3.61 | 57.4 | 262 | 40 | 35.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-07-28 09:48 | 45.1 | 34.9 | 1.3 | 18.7 | -2.3 | 2.3 | 1009 | 13.56 | 32.2 | 152 | 27 | 27.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-07-28 09:46 | 60.6 | 41.3 | 0 | 0 | -40.3 | 40.3 | 1009 | 6.61 | 22 | 140 | 99 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-07-28 09:44 | 61.3 | 40.4 | 0 | 0 | -27.9 | 27.9 | 1009 | -0.06 | 0 | 0 | 10 | 16.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-07-28 09:41 | 50.8 | 36.3 | 2.9 | 10 | -1.6 | 1.6 | 1009 | -0.05 | 0 | 0 | 0 | 14.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-07-28 09:39 | 0.2 | 0.3 | 13.6 | 85.9 | -0.2 | 0.2 | 1009 | -0.05 | 0 | 0 | 0 | 15.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-07-28 09:38 | 51.7 | 37.8 | 0 | 10.5 | -4.9 | 4.9 | 1009 | 2.6 | 31.1 | 168 | 40 | 16.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-07-28 09:37 | 41.4 | 32.6 | 1.3 | 24.7 | -2.7 | 2.7 | 1009 | 0.08 | 1.2 | 5 | 2 | 15.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-07-28 09:35 | 0.9 | 2.1 | 18.7 | 78.3 | -0.2 | 0.2 | 1009 | -0.02 | 0 | 0 | 0 | 13.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-07-28 09:33 | 62.3 | 39.9 | 0 | 0 | -20.1 | 20.1 | 1009 | -0.01 | 0 | 0 | 8 | 15.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-07-28 09:31 | 57.1 | 38.2 | 0 | 4.7 | -14.9 | 14.9 | 1009 | 4.6 | 41.4 | 248 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-07-28 09:30 | 64.2 | 37 | 0 | 0 | -0.7 | 0.7 | 1009 | 0.9 | 4.3 | 29 | 8 | 15.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-07-28 09:28 | 52.1 | 32.2 | 3.8 | 11.9 | 0 | 0 | 1009 | -0.02 | 0 | 0 | 0 | 16.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-07-28 09:24 | 56.1 | 38.1 | 0 | 5.8 | -42.2 | 42.2 | 1009 | 2.74 | 31.3 | 184 | 99 | 21.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-07-27 15:43 | 60.6 | 41.8 | 0 | 0 | -0.4 | 0.4 | 1004 | 9.89 | 28.2 | 179 | 50 | 20.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-07-27 15:42 | 59.7 | 41.2 | 0.3 | 0 | -12.8 | 12.8 | 1004 | 0.95 | 8.8 | 55 | 99 | 13.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-07-27 15:40 | 58.3 | 38.7 | 0 | 3 | -2.5 | 2.5 | 1004 | 2.88 | 15.3 | 93 | 40 | 19 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-07-27 15:38 | 60.9 | 42.1 | 0 | 0 | -1.5 | 1.5 | 1004 | 11.14 | 29.5 | 188 | 60 | 30.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-07-27 15:35 | 53.8 | 38.3 | 0 | 7.9 | -4.2 | 4.2 | 1004 | 10.98 | 29.1 | 164 | 40 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-07-27 15:34 | 52 | 37.8 | 0 | 10.2 | -12.8 | 12.8 | 1004 | 7.08 | 23.5 | 128 | 25 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-07-27 15:32 | 52.9 | 37.3 | 0.3 | 9.5 | -11.9 | 11.9 | 1004 | 17.84 | 37.2 | 206 | 40 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-07-27 15:29 | 60.8 | 42.3 | 0 | 0 | 0.1 | -0.1 | 1003 | 0.6 | 6.9 | 44 | 10 | 21.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-07-27 15:26 | 53.5 | 39.1 | 0.1 | 7.3 | -37.9 | 37.9 | 1003 | 9.27 | 91 | 510 | 50 | 39.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2017-07-27 15:21 | 56.9 | 54.1 | 0 | 0 | 1.6 | -1.6 | 1003 | 0.09 | 5.6 | 33 | 40 | 19.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2017-07-27 15:18 | 51 | 58 | 0 | 0 | 0.9 | -0.9 | 1003 | -0.11 | 0 | 0 | 25 | 19.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2017-07-27 15:15 | 25.2 | 76.3 | 0.6 | 0 | 0.5 | -0.5 | 1003 | -0.1 | 0 | 0 | 10 | 19.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2017-07-27 15:12 | 10.9 | 46.5 | 10.1 | 32.5 | -0.1 | 0.1 | 1003 | -0.08 | 0 | 0 | 2 | 18.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2017-07-27 15:10 | 18.2 | 53 | 0 | 28.8 | -11.4 | 11.4 | 1003 | -0.06 | 0 | 0 | 3 | 18.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-07-27 14:37 | 59.9 | 41.9 | 0 | 0 | -30.8 | 30.8 | 1004 | 17.91 | 126.6 | 794 | 99 | 44.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-07-27 14:36 | 49.5 | 36.6 | 0.4 | 13.5 | -10 | 10 | 1004 | 13.48 | 31.8 | 165 | 40 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-07-27 14:34 | 50.6 | 38.7 | 0 | 10.7 | -24.8 | 24.8 | 1004 | 20.19 | 82.2 | 436 | 99 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-07-27 14:33 | 48.7 | 38.6 | 0 | 12.7 | -10.7 | 10.7 | 1003 | 20.44 | 38.7 | 198 | 50 | 36.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-07-27 14:31 | 59.5 | 42.6 | 0 | 0 | -33 | 33 | 1004 | 11.75 | 62.5 | 390 | 99 | 45 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-07-27 14:29 | 36 | 34.1 | 0 | 29.9 | -1.3 | 1.3 | 1004 | 5.29 | 19.6 | 73 | 25 | 34.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-07-27 14:28 | 47.5 | 38.3 | 0 | 14.2 | -3.6 | 3.6 | 1004 | 15.68 | 34.1 | 170 | 40 | 34.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-07-27 14:26 | 60.8 | 42.9 | 0 | 0 | -13.5 | 13.5 | 1004 | 16.81 | 76.2 | 485 | 80 | 40.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-07-27 14:23 | 21.7 | 16 | 16 | 46.3 | -44.1 | 44.1 | 1005 | -0.08 | 0 | 0 | 99 | 18.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-07-27 14:20 | 2.3 | 1.6 | 19.7 | 76.4 | -44.6 | 44.6 | 1005 | -0.05 | 0 | 0 | 99 | 20.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-07-27 14:18 | 54 | 37.5 | 0 | 8.5 | -6.8 | 6.8 | 1005 | 16.22 | 35.4 | 200 | 40 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-07-27 14:17 | 52.9 | 37.2 | 0 | 9.9 | -12.1 | 12.1 | 1005 | 26.17 | 95.9 | 531 | 70 | 35.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-07-27 14:15 | 48.3 | 37 | 0 | 14.7 | -1.9 | 1.9 | 1005 | 10.79 | 28.3 | 143 | 25 | 36.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-07-27 14:13 | 50.5 | 37.6 | 0 | 11.9 | -0.2 | 0.2 | 1005 | 3.71 | 16.6 | 88 | 25 | 39.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-07-27 14:11 | 61.1 | 38.8 | 0 | 0.1 | -42.8 | 42.8 | 1006 | 2.47 | 29.8 | 191 | 99 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-07-27 14:10 | 47.6 | 35.9 | 0 | 16.5 | -2.7 | 2.7 | 1006 | 23.96 | 42.6 | 212 | 50 | 32.8 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-07-27 14:09 | 54 | 35.2 | 2.2 | 8.6 | -38.5 | 38.5 | 1006 | 6.79 | 23.1 | 131 | 99 | 19.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-07-27 14:07 | 53.4 | 36.8 | 0 | 9.8 | -14.3 | 14.3 | 1006 | 24.64 | 44 | 246 | 55 | 23.6 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-07-27 14:05 | 45.1 | 35.3 | 0 | 19.6 | -0.8 | 0.8 | 1006 | 13.28 | 16 | 75 | 22 | 20.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-07-27 14:03 | 50.6 | 37.8 | 0 | 11.6 | -1.9 | 1.9 | 1006 | 11.54 | 29.7 | 157 | 25 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-07-27 12:54 | 58.3 | 39.7 | 0 | 2 | -69.1 | 69.1 | 1007 | 0.48 | 12.9 | 78 | 99 | 20.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-07-27 12:53 | 47.4 | 36.1 | 0 | 16.5 | -39 | 39 | 1007 | 8.2 | 24.6 | 122 | 50 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-07-27 12:51 | 60.7 | 40.1 | 0 | 0 | -68.1 | 68.1 | 1007 | 0.45 | 5.8 | 37 | 99 | 19.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-07-27 12:49 | 52 | 36.3 | 0 | 11.7 | -5.8 | 5.8 | 1007 | 3.79 | 17.5 | 95 | 25 | 16.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-07-27 12:48 | 49.3 | 38.4 | 0 | 12.3 | -2 | 2 | 1007 | 8.72 | 25.5 | 131 | 40 | 35.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-07-27 12:46 | 53.4 | 38.2 | 1.3 | 7.1 | -5.4 | 5.4 | 1007 | 1.24 | 9.9 | 55 | 20 | 17.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-07-27 12:45 | 40.4 | 34 | 0.5 | 25.1 | -4.9 | 4.9 | 1007 | 5.27 | 20.2 | 85 | 20 | 19.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-07-27 12:42 | 61.3 | 40.8 | 0 | 0 | -25.1 | 25.1 | 1007 | 21.28 | 87.4 | 561 | 99 | 29.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-07-27 12:40 | 42.2 | 35.6 | 0 | 22.2 | -0.9 | 0.9 | 1007 | 4.76 | 19 | 84 | 20 | 25.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-07-27 12:38 | 45.9 | 36.9 | 0 | 17.2 | -3.8 | 3.8 | 1007 | 2.38 | 29.1 | 140 | 20 | 24.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-07-27 12:36 | 48.1 | 36.1 | 0 | 15.8 | -21.6 | 21.6 | 1007 | 1.24 | 20.6 | 104 | 20 | 34.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-07-27 12:34 | 42.1 | 32.7 | 0 | 25.2 | -10.8 | 10.8 | 1007 | 11.23 | 62.6 | 276 | 45 | 31.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-07-27 12:31 | 18.9 | 13.9 | 14.5 | 52.7 | -52.1 | 52.1 | 1008 | -0.01 | 0 | 0 | 80 | 17.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-07-27 12:29 | 29.9 | 25.8 | 2.8 | 41.5 | -2.2 | 2.2 | 1008 | 1.24 | 21.1 | 66 | 20 | 21.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-07-27 12:28 | 49.9 | 37.6 | 0 | 12.5 | -51.2 | 51.2 | 1007 | 0.66 | 24.5 | 128 | 99 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-07-27 12:24 | 50.7 | 38.4 | 0.8 | 10.1 | -8.7 | 8.7 | 1007 | 1.29 | 20.9 | 111 | 50 | 41.3 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-07-27 12:21 | 49.1 | 38.1 | 0 | 12.8 | -1 | 1 | 1007 | 3.85 | 8.7 | 44 | 10 | 14.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-07-27 12:20 | 46.3 | 37.9 | 0 | 15.8 | -1.4 | 1.4 | 1007 | 0.53 | 13.9 | 67 | 15 | 15.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-07-27 12:19 | 50.4 | 39.2 | 0 | 10.4 | -3.2 | 3.2 | 1007 | 2.38 | 29.5 | 156 | 25 | 17.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-07-27 12:17 | 45.3 | 37.1 | 0 | 17.6 | -2.7 | 2.7 | 1007 | -0.11 | 0 | 0 | 5 | 15.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-07-27 12:15 | 44.6 | 36.5 | 0 | 18.9 | -5.9 | 5.9 | 1007 | 16.86 | 35.4 | 165 | 40 | 31.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-07-27 12:13 | 59.2 | 41.3 | 0 | 0 | -26.9 | 26.9 | 1007 | 4.62 | 64.7 | 401 | 75 | 42 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-07-27 12:11 | 40.5 | 34.8 | 0 | 24.7 | -4.2 | 4.2 | 1007 | 7.74 | 24.1 | 102 | 22 | 27 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-07-27 12:08 | 43 | 36.6 | 0 | 20.4 | 0.1 | -0.1 | 1007 | 0.82 | 8 | 36 | 5 | 15.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-07-27 12:07 | 55.8 | 39.5 | 0.4 | 4.3 | -52 | 52 | 1007 | -0.13 | 0 | 0 | 70 | 17.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-07-27 12:05 | 31.6 | 31.9 | 0 | 36.5 | -0.3 | 0.3 | 1007 | 5.91 | 20.4 | 67 | 25 | 42.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-07-27 11:29 | 35.9 | 27 | 7 | 30.1 | -0.8 | 0.8 | 1007 | 0 | 0.5 | 2 | 5 | 27.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-07-27 11:27 | 56.7 | 41.2 | 0 | 2.1 | -54.2 | 54.2 | 1007 | 0.49 | 20.8 | 123 | 99 | 37.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-07-27 11:26 | 44.9 | 36.5 | 0 | 18.6 | -1.6 | 1.6 | 1008 | 14.87 | 33.2 | 156 | 25 | 34 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-07-27 11:24 | 43.1 | 36.1 | 0 | 20.8 | -0.1 | 0.1 | 1008 | 0.68 | 15.5 | 70 | 15 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-07-27 11:23 | 50 | 40.1 | 0 | 9.9 | -4 | 4 | 1008 | 13.15 | 8 | 42 | 15 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-07-27 11:21 | 47.9 | 39.5 | 0 | 12.6 | -40.2 | 40.2 | 1008 | 7.34 | 22.3 | 112 | 55 | 49.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-07-27 11:20 | 46.1 | 37.1 | 0.7 | 16.1 | -8.2 | 8.2 | 1008 | 1.42 | 22 | 106 | 20 | 35.1 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-07-27 11:17 | 47.3 | 38.6 | 0 | 14.1 | -17.8 | 17.8 | 1008 | 15.75 | 33.4 | 165 | 45 | 44.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-07-27 11:16 | 57.8 | 42.3 | 0.2 | 0 | -4 | 4 | 1008 | 2.19 | 3.3 | 20 | 5 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-07-27 11:14 | 20.5 | 27.2 | 1.5 | 50.8 | -1.9 | 1.9 | 1008 | 2.65 | 3.5 | 7 | 2 | 15.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-07-27 11:10 | 51.6 | 38.6 | 0.1 | 9.7 | -48 | 48 | 1008 | -0.19 | 0 | 0 | 25 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-07-27 11:09 | 57.4 | 41.6 | 0 | 1 | 0.2 | -0.2 | 1008 | 1.14 | 9.6 | 57 | 20 | 16.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-07-27 11:07 | 42.1 | 35.7 | 0 | 22.2 | -0.9 | 0.9 | 1008 | 0.87 | 17.4 | 77 | 15 | 28.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-07-27 11:05 | 55.3 | 40.2 | 0 | 4.5 | -45.8 | 45.8 | 1008 | 5.74 | 71.2 | 412 | 99 | 40.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-07-27 11:03 | 57.1 | 40.3 | 0 | 2.6 | -9.2 | 9.2 | 1008 | 7.31 | 51.3 | 307 | 50 | 29 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-07-27 11:01 | 58.3 | 41.6 | 0 | 0.1 | -23.3 | 23.3 | 1008 | 12.13 | 30.9 | 189 | 99 | 18.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-07-27 11:00 | 42.2 | 36.7 | 0 | 21.1 | -0.1 | 0.1 | 1008 | 0.07 | 5.1 | 22 | 10 | 21.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-07-27 10:58 | 57.6 | 39.5 | 0 | 2.9 | -15.2 | 15.2 | 1008 | 19.31 | 82.8 | 499 | 75 | 33.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-07-27 10:56 | 49.3 | 37.8 | 0 | 12.9 | -22.8 | 22.8 | 1008 | 1.7 | 38.3 | 197 | 40 | 51.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-07-27 10:54 | 28.9 | 26 | 5.2 | 39.9 | -1.2 | 1.2 | 1008 | 0.7 | 15.5 | 47 | 10 | 29.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-07-27 10:52 | 44.8 | 35.5 | 0.3 | 19.4 | -0.7 | 0.7 | 1008 | 0.65 | 7.1 | 33 | 5 | 15.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-07-27 10:51 | 48.9 | 38.9 | 0 | 12.2 | -0.3 | 0.3 | 1008 | 2.23 | 12.9 | 66 | 20 | 31.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-07-27 10:49 | 58.6 | 43.4 | 0 | 0 | -52.8 | 52.8 | 1008 | 0.66 | 1.7 | 10 | 99 | 22.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-07-27 10:47 | 45.1 | 37.7 | 0 | 17.2 | -1.6 | 1.6 | 1008 | 10.66 | 27.4 | 129 | 20 | 49.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-07-27 10:45 | 58 | 39.4 | 0 | 2.6 | -19.3 | 19.3 | 1008 | 10.94 | 99.1 | 603 | 80 | 49.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-07-27 10:43 | 54.6 | 40.9 | 0 | 4.5 | -0.1 | 0.1 | 1008 | 6.05 | 10.5 | 60 | 25 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-07-27 10:41 | 50 | 38.6 | 0 | 11.4 | -1.6 | 1.6 | 1008 | 1.24 | 20.8 | 109 | 40 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-07-27 10:39 | 30.4 | 28.2 | 5.2 | 36.2 | -1 | 1 | 1008 | 28.12 | 2.5 | 8 | 5 | 14.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-07-26 16:14 | 24.1 | 27.7 | 0.3 | 47.9 | -2 | 2 | 1010 | 1.96 | 12.1 | 30 | 5 | 19.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-07-26 16:10 | 50.3 | 38.3 | 0.1 | 11.3 | -5.9 | 5.9 | 1011 | 8.8 | 26.2 | 138 | 40 | 21.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-07-26 14:44 | 8.5 | 19.1 | 2.1 | 70.3 | -0.5 | 0.5 | 1009 | 0.21 | 3.9 | 3 | 2 | 21.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-07-26 14:42 | 52.6 | 38.2 | 0 | 9.2 | -16.1 | 16.1 | 1009 | 7.91 | 52.6 | 290 | 50 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-07-26 14:40 | 45.2 | 35.4 | 0.1 | 19.3 | -4 | 4 | 1009 | 1.49 | 22.6 | 107 | 40 | 36.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-07-26 14:38 | 47.5 | 36.1 | 0 | 16.4 | -5.7 | 5.7 | 1009 | 2.4 | 29 | 144 | 40 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-07-26 14:37 | 45.6 | 37.1 | 0 | 17.3 | -62.9 | 62.9 | 1009 | 0.99 | 18.2 | 86 | 50 | 25.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-07-26 14:35 | 53.2 | 38.3 | 0 | 8.5 | -5.1 | 5.1 | 1009 | 4.65 | 19.4 | 108 | 25 | 14.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-07-26 14:34 | 40.9 | 34 | 1.3 | 23.8 | -0.6 | 0.6 | 1009 | 6.01 | 5.3 | 23 | 5 | 24.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-07-26 14:32 | 52.2 | 38.7 | 0 | 9.1 | -2.1 | 2.1 | 1009 | 1.89 | 6 | 33 | 5 | 19.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-07-26 14:30 | 44.7 | 35.5 | 0.8 | 19 | -1.4 | 1.4 | 1008 | 4.12 | 4.5 | 21 | 5 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-07-26 14:26 | 49.6 | 37.9 | 0 | 12.5 | -11.2 | 11.2 | 1008 | 9.03 | 55.2 | 287 | 60 | 41.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-07-26 14:25 | 21.1 | 16.7 | 13.2 | 49 | -36 | 36 | 1008 | -0.08 | 0 | 0 | 99 | 22.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-07-26 14:23 | 45 | 37.2 | 0 | 17.8 | -2.9 | 2.9 | 1008 | 12.84 | 7.7 | 36 | 15 | 34.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-07-26 14:21 | 45.5 | 36.1 | 0.4 | 18 | -3.6 | 3.6 | 1008 | 1.76 | 25 | 119 | 40 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-07-26 14:20 | 51.1 | 38 | 0 | 10.9 | -7 | 7 | 1008 | 2.01 | 26.9 | 144 | 30 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-07-26 14:18 | 60.8 | 40.8 | 0 | 0 | -1.9 | 1.9 | 1008 | 10.51 | 29.4 | 187 | 70 | 16.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-07-26 14:16 | 1.6 | 1.3 | 19.8 | 77.3 | -18.5 | 18.5 | 1008 | 0.02 | 0.5 | 0 | 0 | 16.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-07-26 14:15 | 56.2 | 38.7 | 0 | 5.1 | -2.3 | 2.3 | 1008 | 0.22 | 8.9 | 52 | 10 | 21.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-07-26 14:14 | 38.6 | 31.9 | 1.6 | 27.9 | -5 | 5 | 1008 | 7.8 | 51.4 | 208 | 50 | 37.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-07-26 14:12 | 50.2 | 38 | 0.4 | 11.4 | -9.1 | 9.1 | 1008 | 3.78 | 36.4 | 191 | 50 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-07-26 14:10 | 36.3 | 33.4 | 0 | 30.3 | -3.8 | 3.8 | 1008 | 1.2 | 20.5 | 78 | 20 | 24.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-07-26 14:08 | 40 | 33.5 | 0.2 | 26.3 | -1.9 | 1.9 | 1008 | 4.86 | 19.4 | 81 | 20 | 18.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-07-26 13:56 | 53 | 40.5 | 0 | 6.5 | -7.7 | 7.7 | 1007 | 3.1 | 15.3 | 85 | 25 | 31.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-07-26 13:54 | 41.9 | 35.3 | 0 | 22.8 | -6.5 | 6.5 | 1007 | 6.7 | 22.7 | 100 | 35 | 18.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-07-26 13:52 | 39.3 | 33.8 | 1.3 | 25.6 | -2.9 | 2.9 | 1007 | 5.87 | 21.3 | 87 | 20 | 19.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-07-26 13:50 | 36.7 | 34 | 0.1 | 29.2 | -0.1 | 0.1 | 1007 | 1.54 | 10.8 | 41 | 15 | 20.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-07-26 13:48 | 57.7 | 39.3 | 0.4 | 2.6 | -30.1 | 30.1 | 1007 | 8.33 | 25.7 | 155 | 99 | 17 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-07-26 13:47 | 46.3 | 35 | 0.4 | 18.3 | -5.2 | 5.2 | 1007 | 2 | 43.7 | 212 | 37 | 27.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-07-26 13:45 | 44.7 | 35.3 | 1.2 | 18.8 | -1.6 | 1.6 | 1007 | 3.82 | 8.5 | 40 | 15 | 21.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-07-26 13:42 | 55.7 | 38.2 | 0.8 | 5.3 | -4.6 | 4.6 | 1007 | 4.76 | 19.2 | 112 | 40 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-07-26 12:21 | 48.3 | 35.1 | 0 | 16.6 | -87.6 | 87.6 | 1008 | 0.02 | 1.1 | 6 | 50 | 14.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-07-26 12:20 | 0.6 | 0.5 | 18.8 | 80.1 | -4 | 4 | 1008 | -0.03 | 0 | 0 | 0 | 15.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-07-26 12:19 | 16.4 | 10 | 15.8 | 57.8 | -75.8 | 75.8 | 1008 | 0.04 | 1.7 | 2 | 50 | 16.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-07-26 12:17 | 58.2 | 36.2 | 0.3 | 5.3 | -75.6 | 75.6 | 1008 | 0.09 | 0.6 | 3 | 99 | 15.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-07-26 12:15 | 45.7 | 33.3 | 0 | 21 | -88.1 | 88.1 | 1008 | 0.35 | 1.2 | 6 | 50 | 13.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-07-26 12:14 | 36.1 | 31.1 | 0.3 | 32.5 | -35.3 | 35.3 | 1008 | 0.38 | 5.3 | 20 | 10 | 14 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-07-26 12:12 | 26.4 | 28.5 | 1.7 | 43.4 | 0 | 0 | 1008 | -0.03 | 0 | 0 | 10 | 14.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-07-26 12:10 | 55.3 | 38.5 | 0 | 6.2 | -92.1 | 92.1 | 1008 | 0.02 | 2.3 | 13 | 99 | 15.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2017-07-26 12:09 | 54.2 | 38.4 | 0 | 7.4 | 0.2 | -0.2 | 1008 | -0.05 | 0 | 0 | 15 | 14.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-07-26 12:07 | 48.5 | 36.1 | 0 | 15.4 | -10.1 | 10.1 | 1008 | 11.54 | 7.6 | 38 | 15 | 14.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-07-26 12:05 | 41.3 | 32.2 | 0 | 26.5 | -41 | 41 | 1008 | 1.79 | 11.7 | 50 | 15 | 15.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-07-26 11:57 | 36.2 | 30 | 3.5 | 30.3 | -92.3 | 92.3 | 1008 | -0.15 | 0 | 0 | 10 | 15.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-07-26 11:55 | 0.1 | 0.1 | 18 | 81.8 | -0.7 | 0.7 | 1008 | -0.19 | 0 | 0 | 0 | 19.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-07-26 11:54 | 45.6 | 35 | 0 | 19.4 | -21.9 | 21.9 | 1008 | 4.1 | 17.8 | 85 | 15 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-07-26 11:53 | 30.1 | 22.4 | 7.7 | 39.8 | -92.7 | 92.7 | 1008 | 0 | 0 | 0 | 25 | 15 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-07-26 11:51 | 1 | 0.8 | 19 | 79.2 | -7 | 7 | 1008 | -0.16 | 0 | 0 | 0 | 13.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-07-26 11:50 | 44.2 | 32.1 | 4.2 | 19.5 | -41.6 | 41.6 | 1008 | -0.31 | 0 | 0 | 10 | 13.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-07-26 11:48 | 32.6 | 26.1 | 5.4 | 35.9 | -0.6 | 0.6 | 1008 | 3.36 | 4.1 | 14 | 5 | 13.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-07-26 11:46 | 55.2 | 37.6 | 0 | 7.2 | -92.1 | 92.1 | 1008 | 0.38 | 4.8 | 27 | 99 | 14.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-07-26 11:45 | 34.9 | 23.4 | 9.8 | 31.9 | -92.3 | 92.3 | 1008 | -0.18 | 0 | 0 | 40 | 15.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-07-26 11:43 | 55 | 38.4 | 0 | 6.6 | -92.2 | 92.2 | 1008 | -0.18 | 0 | 0 | 25 | 15.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-07-26 11:41 | 48.1 | 35.4 | 0 | 16.5 | -37 | 37 | 1008 | 1.65 | 10.1 | 51 | 15 | 16.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-07-26 11:40 | 41.8 | 34.5 | 0.1 | 23.6 | -2.6 | 2.6 | 1007 | 1.33 | 10.2 | 44 | 10 | 16.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-07-26 10:54 | 51.3 | 38.9 | 0.1 | 9.7 | -3.6 | 3.6 | 1007 | 7.51 | 24.3 | 130 | 40 | 21 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-07-26 10:52 | 2.7 | 3.8 | 20.2 | 73.3 | -0.6 | 0.6 | 1007 | 0.02 | 1.1 | 0 | 0 | 15.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-07-26 10:50 | 12 | 9.2 | 17.8 | 61 | 0 | 0 | 1007 | 0.01 | 0.3 | 0 | 0 | 16.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-07-26 10:49 | 0.1 | 0.1 | 20.6 | 79.2 | -0.4 | 0.4 | 1007 | 0 | 0 | 0 | 0 | 17.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-07-26 10:48 | 42.3 | 32.2 | 4.9 | 20.6 | -70.4 | 70.4 | 1007 | 0.2 | 3.7 | 16 | 0 | 22.2 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-07-26 10:46 | 29.8 | 31.8 | 0 | 38.4 | -1.5 | 1.5 | 1007 | 0.02 | 2.6 | 8 | 0 | 17.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-07-26 10:44 | 50.6 | 37.5 | 0 | 11.9 | -28.3 | 28.3 | 1007 | 13.32 | 68.8 | 365 | 70 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-07-26 10:42 | 17.9 | 12.8 | 12.7 | 56.6 | -2.7 | 2.7 | 1007 | 0.04 | 3.8 | 7 | 0 | 14.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-07-26 10:40 | 48.7 | 39.2 | 0 | 12.1 | -1.3 | 1.3 | 1007 | 0.32 | 10.7 | 54 | 25 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-07-26 10:38 | 45.3 | 37 | 0 | 17.7 | -6 | 6 | 1007 | 1.22 | 21 | 99 | 22 | 18.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-07-26 10:36 | 52.3 | 39 | 0 | 8.7 | -5.2 | 5.2 | 1007 | 1.78 | 25.6 | 140 | 25 | 19.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-07-26 10:34 | 46.3 | 36.4 | 1.5 | 15.8 | -1.3 | 1.3 | 1007 | 0.28 | 10 | 48 | 13 | 21 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-07-26 10:32 | 49.5 | 39.4 | 0 | 11.1 | -1.4 | 1.4 | 1007 | 0.27 | 9.8 | 51 | 20 | 24.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-07-26 10:31 | 24.8 | 29.2 | 0.4 | 45.6 | -3.5 | 3.5 | 1007 | 3.64 | 16.2 | 42 | 10 | 26.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-07-26 10:29 | 30.3 | 26.8 | 5.6 | 37.3 | -1.4 | 1.4 | 1007 | 1.44 | 10.6 | 33 | 10 | 14.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-07-26 10:25 | 55.5 | 39.2 | 0 | 5.3 | -11.7 | 11.7 | 1007 | 5.47 | 44.4 | 258 | 40 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-07-26 10:23 | 48.5 | 38 | 0.2 | 13.3 | -33.2 | 33.2 | 1007 | >>>> | 0 | 0 | 99 | 35.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-07-26 10:21 | 38 | 32.2 | 3.1 | 26.7 | -2.3 | 2.3 | 1007 | -0.11 | 0 | 0 | 20 | 15.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-07-26 10:19 | 23.5 | 23.6 | 6.4 | 46.5 | -1 | 1 | 1007 | -0.12 | 0 | 0 | 10 | 21.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-07-26 10:18 | 38.3 | 33.7 | 3.7 | 24.3 | -70.5 | 70.5 | 1007 | 0.15 | 6.9 | 27 | 40 | 27.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-06-23 15:04 | 58.6 | 42.5 | 0 | 0 | -25.7 | 25.7 | 1001 | 22.47 | 87.1 | 535 | 99 | 41.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-06-23 15:02 | 58.5 | 43.5 | 0 | 0 | -33 | 33 | 1001 | 11.76 | 63.1 | 387 | 99 | 36.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-06-23 15:01 | 59.4 | 42.7 | 0 | 0 | -32 | 32 | 1001 | 15.66 | 119.5 | 744 | 99 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-06-23 15:00 | 44 | 35 | 3.8 | 17.2 | -1.1 | 1.1 | 1001 | -0.02 | 0 | 0 | 0 | 26.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-06-23 14:59 | 59.6 | 41.9 | 0 | 0 | -29.3 | 29.3 | 1001 | 16.58 | 75.6 | 472 | 99 | 36.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-06-23 14:57 | 59.6 | 42.4 | 0.1 | 0 | -45.1 | 45.1 | 1001 | 0.27 | 9.6 | 60 | 99 | 32.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-06-23 14:55 | 0.2 | 0.2 | 18.8 | 80.8 | -45.8 | 45.8 | 1001 | -0.16 | 0 | 0 | 99 | 14.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-06-23 14:54 | 56.9 | 41.3 | 0.2 | 1.6 | -2.7 | 2.7 | 1001 | 9.45 | 27.2 | 162 | 25 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-06-23 14:52 | 60.5 | 42 | 0 | 0 | -27.3 | 27.3 | 1002 | 1.54 | 23.2 | 147 | 50 | 33.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-06-23 14:50 | 12.4 | 8.4 | 17.3 | 61.9 | -47.1 | 47.1 | 1001 | -0.01 | 0 | 0 | 40 | 15.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-06-23 14:49 | 3.8 | 2.9 | 19.8 | 73.5 | -47.5 | 47.5 | 1001 | 0.11 | 6.2 | 2 | 99 | 15.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-06-23 14:47 | 30.4 | 19.8 | 16.1 | 33.7 | -47.1 | 47.1 | 1002 | 0.11 | 2.8 | 9 | 99 | 17.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-06-23 14:46 | 19.7 | 14.5 | 13.6 | 52.2 | -46.6 | 46.6 | 1001 | 0.08 | 2.4 | 5 | 0 | 19.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-06-23 14:44 | 59.6 | 41.3 | 0 | 0 | -44.4 | 44.4 | 1001 | 3.25 | 54.1 | 337 | 99 | 38.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-06-23 14:43 | 52.3 | 39 | 0.1 | 8.6 | -8.2 | 8.2 | 1001 | 18.5 | 37.9 | 207 | 40 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-06-23 14:41 | 50.9 | 38.1 | 0 | 11 | -4.8 | 4.8 | 1001 | 12.61 | 31.1 | 165 | 40 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-06-23 14:39 | 48.9 | 37.7 | 0.8 | 12.6 | -7 | 7 | 1001 | 2.31 | 28.9 | 148 | 40 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-06-23 14:38 | 25.5 | 19 | 13.1 | 42.4 | -46.5 | 46.5 | 1001 | 0.04 | 3.5 | 9 | 99 | 17.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-06-23 14:04 | 55.3 | 38.9 | 0.7 | 5.1 | 0 | 0 | 1001 | -0.1 | 0 | 0 | 0 | 25.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-06-23 14:02 | 57.4 | 41.2 | 0 | 1.4 | -53.9 | 53.9 | 1001 | 0.78 | 26.5 | 159 | 99 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-06-23 14:00 | 48.1 | 37.4 | 0 | 14.5 | -1.2 | 1.2 | 1001 | 12.91 | 31.1 | 157 | 40 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-06-23 13:59 | 47.3 | 37.3 | 0 | 15.4 | -0.1 | 0.1 | 1001 | 0.62 | 14.8 | 73 | 15 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-06-23 13:58 | 56.2 | 41.4 | 0.2 | 2.2 | -1.7 | 1.7 | 1001 | 13.32 | 8.1 | 48 | 15 | 20.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-06-23 13:56 | 52.7 | 40.4 | 0 | 6.9 | -38.3 | 38.3 | 1002 | 8.08 | 23.6 | 130 | 50 | 48.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-06-23 13:54 | 52.4 | 39.3 | 0.3 | 8 | -6.8 | 6.8 | 1002 | 0.84 | 17.1 | 93 | 25 | 36.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-06-23 13:53 | 51.6 | 39.5 | 0 | 8.9 | -16.7 | 16.7 | 1002 | 15.67 | 33.5 | 181 | 50 | 43.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-06-23 13:51 | 58.1 | 42.2 | 0.1 | 0 | -4.1 | 4.1 | 1002 | 2.66 | 3.6 | 22 | 5 | 22.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-06-23 13:50 | 35.5 | 33 | 0.1 | 31.4 | -1.3 | 1.3 | 1003 | 4.18 | 4.5 | 16 | 5 | 18.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-06-23 13:42 | 49 | 37.7 | 0 | 13.3 | -0.2 | 0.2 | 1003 | 7.36 | 11.9 | 61 | 20 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-06-23 13:41 | 47.9 | 37.7 | 0 | 14.4 | -4.3 | 4.3 | 1003 | 4.79 | 18.8 | 94 | 20 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-06-23 13:40 | 50.5 | 39.4 | 0 | 10.1 | -31.2 | 31.2 | 1003 | 20.12 | 132.5 | 701 | 99 | 44.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-06-23 13:38 | 38.7 | 34.7 | 0 | 26.6 | -2.8 | 2.8 | 1003 | 1.16 | 9.4 | 38 | 5 | 19.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-06-23 13:35 | 55.2 | 40.1 | 0.9 | 3.8 | -0.8 | 0.8 | 1003 | 1.02 | 19.2 | 111 | 25 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-06-23 13:34 | 46.6 | 37.9 | 0 | 15.5 | -2.6 | 2.6 | 1003 | 1.71 | 24.1 | 117 | 22 | 39.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-06-23 13:32 | 41 | 34.9 | 0 | 24.1 | -12.4 | 12.4 | 1003 | 14.23 | 69 | 296 | 50 | 38.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-06-23 13:29 | 56.2 | 40.3 | 0.3 | 3.2 | 0 | 0 | 1003 | 9.37 | 13.4 | 79 | 25 | 25.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-06-23 13:27 | 51.6 | 38 | 0 | 10.4 | -6.3 | 6.3 | 1003 | 20.57 | 40.1 | 216 | 50 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-06-23 13:26 | 47.6 | 37.3 | 0 | 15.1 | -25.3 | 25.3 | 1003 | 1.51 | 22.8 | 114 | 20 | 28.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-06-23 13:24 | 45.8 | 34.8 | 0.6 | 18.8 | -9.7 | 9.7 | 1004 | 5.12 | 43.2 | 207 | 40 | 19.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-06-23 13:22 | 43.9 | 33.6 | 2.3 | 20.2 | 0 | 0 | 1004 | 9.57 | 6.9 | 31 | 10 | 19.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-06-23 13:21 | 45.1 | 37.5 | 0 | 17.4 | -0.1 | 0.1 | 1003 | 17.62 | 9.2 | 43 | 10 | 24.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2017-06-23 10:43 | 4.6 | 2.7 | 17.8 | 74.9 | -50.7 | 50.7 | 1005 | -0.2 | 0 | 0 | 5 | 17 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-06-23 10:42 | 61.4 | 41.5 | 0 | 0 | -47.4 | 47.4 | 1005 | 6.16 | 77.7 | 500 | 99 | 14.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2017-06-23 10:40 | 6.4 | 4.4 | 15.5 | 73.7 | -52.4 | 52.4 | 1005 | -0.17 | 0 | 0 | 99 | 15.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-06-23 10:39 | 36.5 | 25.5 | 10.1 | 27.9 | -52.6 | 52.6 | 1005 | -0.16 | 0 | 0 | 99 | 15.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-06-23 10:38 | 57.8 | 42.1 | 1.5 | 0 | 0 | 0 | 1005 | -0.13 | 0 | 0 | 0 | 14.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-06-23 10:36 | 46.6 | 36.6 | 0 | 16.8 | -1.8 | 1.8 | 1005 | 0.33 | 10.8 | 52 | 10 | 30.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-06-23 10:34 | 60.4 | 41.8 | 0 | 0 | -9.9 | 9.9 | 1005 | 17.72 | 36.4 | 230 | 50 | 41.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-06-23 10:32 | 59.6 | 42.3 | 0 | 0 | -52.7 | 52.7 | 1005 | 0.03 | 3.2 | 20 | 99 | 29.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2017-06-23 10:31 | 60.5 | 41.2 | 0.1 | 0 | -53.3 | 53.3 | 1005 | -0.13 | 0 | 0 | 99 | 16 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-06-23 10:29 | 24.9 | 18.5 | 13.3 | 43.3 | -52.6 | 52.6 | 1006 | -0.06 | 0 | 0 | 99 | 14.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-06-23 10:25 | 54.9 | 40.9 | 0.3 | 3.9 | -40.6 | 40.6 | 1006 | 9.13 | 89.6 | 515 | 99 | 41.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-06-23 10:23 | 3.2 | 3.2 | 17.6 | 76 | -1.2 | 1.2 | 1006 | -0.31 | 0 | 0 | 0 | 22.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-06-23 10:21 | 59.6 | 43.8 | 0 | 0 | -45.2 | 45.2 | 1006 | 0.72 | 7.2 | 45 | 99 | 32.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-06-23 10:19 | 60.5 | 42.7 | 0 | 0 | -45.8 | 45.8 | 1006 | -0.17 | 0 | 0 | 50 | 17.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-06-23 10:18 | 47.7 | 37.7 | 0 | 14.6 | -20.5 | 20.5 | 1005 | 14.79 | 72.6 | 363 | 70 | 20.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-06-23 10:16 | 44.1 | 36.6 | 0 | 19.3 | -6.7 | 6.7 | 1005 | 4.04 | 17.2 | 79 | 20 | 36.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-06-23 10:14 | 0.5 | 3.5 | 15.8 | 80.2 | -4.8 | 4.8 | 1005 | -0.17 | 0 | 0 | 0 | 24.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-06-23 10:12 | 48.8 | 38.2 | 0 | 13 | -22.2 | 22.2 | 1005 | 5.23 | 41.7 | 213 | 50 | 41.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-06-23 10:10 | 50.8 | 38.8 | 0 | 10.4 | -43.2 | 43.2 | 1005 | 3.57 | 56.2 | 299 | 99 | 37.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-06-23 10:09 | 49.6 | 39.1 | 0.5 | 10.8 | -1.2 | 1.2 | 1005 | 2.09 | 12.2 | 63 | 40 | 46 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-06-22 15:00 | 41.7 | 33.1 | 1.9 | 23.3 | -0.1 | 0.1 | 1014 | 6.41 | 22.1 | 96 | 20 | 28.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-06-22 14:58 | 48 | 34.7 | 1.5 | 15.8 | -4 | 4 | 1014 | 8.23 | 54.1 | 272 | 50 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-06-22 14:57 | 46.4 | 33.4 | 1.4 | 18.8 | -3.4 | 3.4 | 1014 | 16.97 | 36.4 | 177 | 40 | 25.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-06-22 14:55 | 47.4 | 37.4 | 0.1 | 15.1 | -4.6 | 4.6 | 1014 | 4.1 | 38 | 189 | 50 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-06-22 14:53 | 55 | 39 | 0.4 | 5.6 | -17.9 | 17.9 | 1014 | 13.68 | 32.4 | 187 | 40 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-06-22 14:51 | 26 | 22.8 | 5.1 | 46.1 | -0.4 | 0.4 | 1014 | -0.11 | 0 | 0 | 5 | 19.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-06-22 14:49 | 44.3 | 35.7 | 0 | 20 | -1.2 | 1.2 | 1014 | 1.8 | 5.8 | 27 | 10 | 25.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-06-22 14:47 | 56.4 | 38.4 | 0.1 | 5.1 | -33.3 | 33.3 | 1014 | 10.56 | 100.2 | 592 | 99 | 26.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-06-22 13:34 | 34.5 | 28.4 | 1.4 | 35.7 | -1.8 | 1.8 | 1015 | 3.19 | 3.9 | 14 | 5 | 16.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-06-22 13:33 | 42.8 | 33.5 | 0.2 | 23.5 | -3.8 | 3.8 | 1015 | 5.36 | 20.4 | 91 | 20 | 22.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-06-22 13:30 | 44.4 | 34.2 | 0.4 | 21 | -7.6 | 7.6 | 1015 | 4.27 | 38.8 | 180 | 45 | 29.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-06-22 13:27 | 48.3 | 37.4 | 0.1 | 14.2 | -1.6 | 1.6 | 1015 | 2.73 | 14.3 | 72 | 25 | 35.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-06-22 13:25 | 48.9 | 36.8 | 0 | 14.3 | -30.6 | 30.6 | 1015 | 18.92 | 81 | 415 | 99 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-06-22 13:21 | 31.7 | 22.5 | 13.1 | 32.7 | -2.1 | 2.1 | 1015 | -0.33 | 0 | 0 | 99 | 15.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-06-22 13:19 | 51.2 | 38 | 0 | 10.8 | -0.4 | 0.4 | 1015 | 0.18 | 8 | 43 | 25 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-06-22 13:16 | 52.6 | 37.4 | 0.1 | 9.9 | -3.4 | 3.4 | 1015 | 8.63 | 25.4 | 140 | 50 | 39.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-06-22 12:32 | 59 | 41.6 | 0 | 0 | -26.5 | 26.5 | 1015 | 18.68 | 79.1 | 489 | 99 | 45.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-06-22 12:30 | 60.4 | 41.5 | 0 | 0 | -29 | 29 | 1015 | 16.83 | 123.1 | 779 | 99 | 44.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-06-22 12:29 | 46.3 | 34.9 | 0.9 | 17.9 | -4.6 | 4.6 | 1015 | 14.57 | 33.1 | 161 | 40 | 33.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-06-22 12:27 | 50.8 | 38.3 | 0 | 10.9 | -24.9 | 24.9 | 1015 | 18.38 | 78.6 | 418 | 99 | 40 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-06-22 12:25 | 48.5 | 37.6 | 0 | 13.9 | -18.6 | 18.6 | 1015 | 18.3 | 36.8 | 187 | 50 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-06-22 12:24 | 33.1 | 32.2 | 0 | 34.7 | -2.9 | 2.9 | 1015 | 10.95 | 28 | 97 | 30 | 36.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-06-22 12:22 | 45 | 36.9 | 0 | 18.1 | -4.4 | 4.4 | 1015 | 18.37 | 36.8 | 173 | 50 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-06-22 12:20 | 60.9 | 42.5 | 0 | 0 | -5.7 | 5.7 | 1015 | 10 | 60.4 | 385 | 55 | 27.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-06-22 12:18 | 29.5 | 22.4 | 12.4 | 35.7 | -44 | 44 | 1015 | 0.11 | 2.8 | 8 | 99 | 25.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-06-22 12:08 | 10.6 | 6.4 | 16.5 | 66.5 | -41.8 | 41.8 | 1016 | -0.21 | 0 | 0 | 99 | 24.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-06-22 12:06 | 51.2 | 36.2 | 0 | 12.6 | -7.9 | 7.9 | 1016 | 15.01 | 33.7 | 181 | 40 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-06-22 12:05 | 52.9 | 37.1 | 0 | 10 | -11.5 | 11.5 | 1016 | 25.87 | 95.5 | 529 | 70 | 34.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-06-22 12:04 | 47.6 | 36.6 | 0 | 15.8 | -2.3 | 2.3 | 1016 | 12.9 | 31 | 154 | 40 | 36.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-06-22 12:02 | 44.1 | 34.9 | 0.1 | 20.9 | -0.8 | 0.8 | 1016 | 6.23 | 21.4 | 99 | 20 | 39.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-06-22 12:00 | 60.5 | 38.2 | 0 | 1.3 | -42.4 | 42.4 | 1016 | 1.19 | 20.7 | 131 | 99 | 24.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-06-22 11:58 | 48.1 | 36 | 0 | 15.9 | -2.5 | 2.5 | 1016 | 23.73 | 42.5 | 214 | 50 | 31.6 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-06-22 11:57 | 52.4 | 34.6 | 2.5 | 10.5 | -37 | 37 | 1016 | 6.56 | 22.7 | 124 | 99 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-06-22 11:55 | 52 | 36.6 | 0.1 | 11.3 | -14.2 | 14.2 | 1016 | 22.81 | 42.4 | 231 | 55 | 21.9 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-06-22 11:17 | 42.3 | 34.3 | 0 | 23.4 | -1.5 | 1.5 | 1016 | 19.97 | 19.6 | 86 | 20 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-06-22 11:14 | 44 | 36.1 | 0.1 | 19.8 | -2.8 | 2.8 | 1015 | 16.85 | 35.5 | 164 | 40 | 31.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-06-22 10:28 | 56.5 | 40.7 | 0 | 2.8 | -4.7 | 4.7 | 1015 | 13.88 | 32.6 | 193 | 50 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-06-22 10:26 | 13.9 | 6.8 | 1 | 78.3 | -15.2 | 15.2 | 1015 | -0.07 | 0 | 0 | 0 | 21.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-06-22 10:23 | 42.6 | 35.9 | 0 | 21.5 | -6.1 | 6.1 | 1015 | 12.47 | 30.4 | 136 | 40 | 30.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-06-22 10:21 | 29.1 | 31.1 | 0 | 39.8 | -0.6 | 0.6 | 1015 | 3.02 | 15.2 | 46 | 10 | 14.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-06-22 10:19 | 57.5 | 41 | 0 | 1.5 | -51 | 51 | 1015 | 0.08 | 8.6 | 52 | 70 | 19.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-06-22 10:17 | 45 | 38.4 | 0 | 16.6 | -0.2 | 0.2 | 1015 | 5.87 | 20.5 | 96 | 25 | 42.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-06-22 10:06 | 50.4 | 37.1 | 0.1 | 12.4 | -9.4 | 9.4 | 1016 | 0.96 | 18.5 | 98 | 25 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-06-22 10:04 | 8 | 5.9 | 17.1 | 69 | -51.4 | 51.4 | 1016 | -0.37 | 0 | 0 | 99 | 19.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-06-22 10:03 | 56.8 | 40.1 | 0.8 | 2.3 | -38.9 | 38.9 | 1016 | 2.73 | 14.2 | 84 | 50 | 32.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-06-22 10:01 | 37.8 | 29.1 | 6.2 | 26.9 | -50.6 | 50.6 | 1016 | -0.17 | 0 | 0 | 99 | 15.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-06-22 09:59 | 31.6 | 22.3 | 8.8 | 37.3 | -4.3 | 4.3 | 1016 | 1.51 | 11 | 36 | 10 | 14.1 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-06-22 09:57 | 48.9 | 37.8 | 0 | 13.3 | -7.4 | 7.4 | 1016 | 0.62 | 14.9 | 76 | 25 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-06-22 09:56 | 47.7 | 37.1 | 0.5 | 14.7 | -1.9 | 1.9 | 1016 | 2.66 | 14.4 | 72 | 15 | 21.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-06-22 09:53 | 0.1 | 0.1 | 19.3 | 80.5 | -0.7 | 0.7 | 1016 | -0.11 | 0 | 0 | 0 | 18.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-06-22 09:52 | 62 | 39.6 | 0 | 0 | -50.5 | 50.5 | 1016 | 1.18 | 9.6 | 62 | 99 | 18.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-06-22 09:50 | 47.7 | 33 | 5.1 | 14.2 | 0.7 | -0.7 | 1016 | -0.07 | 0 | 0 | 3 | 14.9 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-06-22 09:47 | 50.6 | 38.3 | 0.7 | 10.4 | -1.8 | 1.8 | 1016 | 2.33 | 13.4 | 71 | 25 | 26.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-06-22 09:41 | 33.4 | 31.6 | 0.4 | 34.6 | -1.1 | 1.1 | 1016 | 1.67 | 11.3 | 39 | 20 | 19.3 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-06-22 09:38 | 52.2 | 39 | 0.4 | 8.4 | -4.4 | 4.4 | 1016 | 7.83 | 25.1 | 137 | 40 | 15.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-06-21 14:43 | 59.6 | 40.3 | 0 | 0.1 | -4 | 4 | 1017 | 29.01 | 48.1 | 300 | 50 | 24.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-06-21 14:41 | 23.7 | 17.5 | 12.4 | 46.4 | -78.5 | 78.5 | 1017 | 0 | 0 | 0 | 99 | 14.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-06-21 14:39 | 56.8 | 38 | 0 | 5.2 | -7.8 | 7.8 | 1017 | 22.98 | 43 | 255 | 50 | 21.8 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-06-21 14:37 | 59.5 | 41.3 | 0 | 0 | -3.5 | 3.5 | 1017 | 19.11 | 38.4 | 239 | 55 | 33.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-06-21 14:34 | 37.5 | 33.9 | 0 | 28.6 | -0.2 | 0.2 | 1017 | 0.94 | 8.4 | 33 | 10 | 26.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-06-21 14:31 | 49 | 38.5 | 0.5 | 12 | -32.8 | 32.8 | 1019 | 8.18 | 85.3 | 438 | 50 | 37.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-06-21 14:26 | 61.1 | 39.3 | 0 | 0 | -2.2 | 2.2 | 1019 | 1.15 | 4.8 | 30 | 99 | 21.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-06-21 14:24 | 58.7 | 39.2 | 0 | 2.1 | -1.2 | 1.2 | 1019 | 1.19 | 9.7 | 59 | 99 | 29.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-06-21 14:22 | 52.3 | 37.8 | 0 | 9.9 | -2.3 | 2.3 | 1018 | 0.75 | 15.9 | 87 | 99 | 45 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-06-21 14:14 | 60.6 | 40.8 | 0 | 0 | -36.9 | 36.9 | 1018 | 0.42 | 1.4 | 9 | 25 | 17.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-06-21 14:12 | 50.1 | 34.6 | 1.3 | 14 | -4.5 | 4.5 | 1018 | 3.16 | 15.7 | 82 | 25 | 27.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-06-21 14:11 | 32.6 | 29.2 | 1.3 | 36.9 | -0.6 | 0.6 | 1018 | 6.79 | 5.7 | 19 | 10 | 16.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-06-21 14:09 | 38.1 | 32 | 1 | 28.9 | -1.9 | 1.9 | 1018 | 1.11 | 20 | 80 | 20 | 18.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-06-21 14:06 | 37.3 | 31.8 | 0.4 | 30.5 | -16.6 | 16.6 | 1018 | 2.65 | 14 | 54 | 20 | 28.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-06-21 14:04 | 43.9 | 33.5 | 1.4 | 21.2 | -27.4 | 27.4 | 1019 | 5.15 | 67.9 | 312 | 70 | 38.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-06-21 14:02 | 43.9 | 34.3 | 1.2 | 20.6 | -3.2 | 3.2 | 1019 | 17.31 | 36.2 | 166 | 40 | 30.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-06-21 14:00 | 60 | 40.7 | 0 | 0 | -35.8 | 35.8 | 1019 | 6.98 | 22.7 | 143 | 99 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-06-21 13:58 | 53.6 | 37.1 | 1.1 | 8.2 | -14.2 | 14.2 | 1019 | 0.02 | 2.5 | 14 | 25 | 15.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-06-21 13:56 | 45.4 | 34.7 | 0.9 | 19 | -3.6 | 3.6 | 1019 | 0.18 | 3.8 | 18 | 7 | 17.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-06-21 13:54 | 0.1 | 0.1 | 19.6 | 80.2 | -0.2 | 0.2 | 1019 | -0.14 | 0 | 0 | 0 | 18.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-06-21 13:53 | 51.4 | 37.1 | 0 | 11.5 | -4.8 | 4.8 | 1019 | 2.63 | 31.2 | 168 | 40 | 18.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-06-21 13:52 | 28.3 | 23 | 5.9 | 42.8 | -3.2 | 3.2 | 1019 | -0.04 | 0 | 0 | 5 | 15.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-06-21 13:50 | 8.4 | 12.9 | 8 | 70.7 | -9.9 | 9.9 | 1019 | 2.02 | 26.6 | 23 | 5 | 18.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-06-21 13:48 | 60.9 | 39.6 | 0 | 0 | -12.6 | 12.6 | 1019 | -0.19 | 0 | 0 | 5 | 16.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-06-21 13:46 | 53.9 | 35.9 | 0 | 10.2 | -13.5 | 13.5 | 1019 | 4.09 | 39 | 220 | 50 | 21.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-06-21 13:45 | 56.8 | 31.8 | 0 | 11.4 | -1 | 1 | 1019 | 0.48 | 3.1 | 18 | 10 | 17.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-06-21 13:44 | 47.3 | 27.7 | 4 | 21 | -0.4 | 0.4 | 1019 | -0.14 | 0 | 0 | 0 | 18 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-06-21 13:43 | 61.1 | 38.4 | 0 | 0.5 | -42.8 | 42.8 | 1018 | 1.45 | 23 | 147 | 99 | 23.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2017-06-21 12:29 | 18.9 | 85.5 | 0 | 0 | -0.6 | 0.6 | 1017 | 0.02 | 2 | 4 | 5 | 13.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2017-06-21 12:27 | 31.5 | 75.3 | 0 | 0 | 0 | 0 | 1017 | -0.04 | 0 | 0 | 3 | 13.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2017-06-21 12:26 | 24.2 | 77.1 | 0.6 | 0 | 0 | 0 | 1017 | -0.04 | 0 | 0 | 0 | 17.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2017-06-21 12:24 | 4.7 | 24.1 | 15 | 56.2 | -0.5 | 0.5 | 1017 | 0.13 | 6.4 | 3 | 3 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2017-06-21 12:22 | 9.5 | 62.2 | 2.3 | 26 | -14.9 | 14.9 | 1016 | -0.02 | 0 | 0 | 3 | 20.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-06-21 12:12 | 54.6 | 38.6 | 0.1 | 6.7 | -38.6 | 38.6 | 1016 | -0.03 | 0 | 0 | 25 | 24 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-06-21 12:09 | 49.7 | 38.1 | 0 | 12.2 | -1.4 | 1.4 | 1016 | 0.97 | 8.7 | 45 | 15 | 18.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-06-21 12:08 | 35.9 | 32.4 | 0 | 31.7 | -2.9 | 2.9 | 1016 | 1.59 | 23.3 | 87 | 20 | 31.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-06-21 12:05 | 55 | 39.7 | 0 | 5.3 | -31.4 | 31.4 | 1016 | 19.66 | 132.3 | 762 | 99 | 43.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-06-21 12:04 | 59.6 | 40.6 | 0 | 0 | -6.8 | 6.8 | 1016 | 17.88 | 37.6 | 235 | 50 | 25.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-06-21 12:01 | 57.4 | 41 | 0 | 1.6 | -22.1 | 22.1 | 1016 | 9.18 | 26.8 | 161 | 99 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-06-21 12:00 | 37.4 | 33.9 | 0 | 28.7 | -0.4 | 0.4 | 1016 | 0.67 | 15.4 | 60 | 10 | 24 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-06-21 11:58 | 59.8 | 39.6 | 0 | 0.6 | -8.7 | 8.7 | 1016 | 11.4 | 64.3 | 403 | 60 | 31.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-06-21 11:56 | 50.6 | 37.6 | 0 | 11.8 | -19.9 | 19.9 | 1016 | 1.64 | 39.3 | 208 | 40 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-06-21 11:54 | 32.6 | 28.3 | 3.7 | 35.4 | -2.1 | 2.1 | 1016 | 1.67 | 23.7 | 81 | 20 | 37 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-06-21 11:52 | 40.5 | 34 | 0.7 | 24.8 | -2.1 | 2.1 | 1016 | 1.76 | 11.7 | 49 | 10 | 17.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-06-21 11:50 | 40.9 | 35.7 | 0.3 | 23.1 | -0.3 | 0.3 | 1016 | 2.28 | 12.9 | 55 | 15 | 33.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-06-21 11:48 | 52.5 | 41 | 0 | 6.5 | -29.5 | 29.5 | 1016 | 2.36 | 3.3 | 18 | 99 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-06-21 11:46 | 44.3 | 36.6 | 0 | 19.1 | -2.1 | 2.1 | 1016 | 13.21 | 30.5 | 141 | 25 | 49.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-06-21 11:44 | 59.2 | 39.2 | 0 | 1.6 | -11.7 | 11.7 | 1016 | 6.44 | 76.6 | 475 | 75 | 49 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-06-21 11:42 | 44.3 | 36.6 | 0.8 | 18.3 | -0.8 | 0.8 | 1016 | 7.36 | 11.5 | 53 | 15 | 38.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-06-21 11:40 | 48.9 | 37.3 | 0 | 13.8 | -1.7 | 1.7 | 1016 | 1.11 | 19.7 | 101 | 40 | 34.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-06-21 11:38 | 40.6 | 35.2 | 1.5 | 22.7 | -1 | 1 | 1017 | 15.64 | 1.9 | 8 | 5 | 16.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-06-21 11:34 | 51.9 | 37.7 | 0 | 10.4 | -4.4 | 4.4 | 1017 | 10.5 | 28.4 | 154 | 40 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-06-21 11:33 | 48.9 | 36.5 | 0.2 | 14.4 | -15 | 15 | 1017 | 8.44 | 25.5 | 130 | 20 | 24.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-06-21 11:30 | 52.1 | 37.2 | 0.4 | 10.3 | -11.6 | 11.6 | 1017 | 16.3 | 35.4 | 193 | 40 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-06-21 10:25 | 52.8 | 39.2 | 0.2 | 7.8 | -2.7 | 2.7 | 1017 | 7.19 | 23.8 | 131 | 40 | 21.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-06-21 10:23 | 4.8 | 4.9 | 17.1 | 73.2 | -0.8 | 0.8 | 1017 | 0.09 | 2.6 | 1 | 0 | 12.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-06-21 10:22 | 30.3 | 21.9 | 11.4 | 36.4 | 0 | 0 | 1017 | 0.01 | 0.4 | 1 | 0 | 15.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-06-21 10:20 | 0.1 | 0.1 | 20 | 79.8 | -0.2 | 0.2 | 1017 | -0.05 | 0 | 0 | 0 | 17.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-06-21 10:18 | 40.3 | 31.5 | 4.2 | 24 | -48.7 | 48.7 | 1017 | 5.57 | 19.7 | 83 | 25 | 40.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-06-21 10:16 | 39.6 | 35.1 | 0 | 25.3 | -0.8 | 0.8 | 1017 | 0.06 | 4.6 | 19 | 15 | 19 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-06-21 10:14 | 52.3 | 37.6 | 0 | 10.1 | -26 | 26 | 1017 | 11.66 | 64.6 | 354 | 50 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-06-21 10:12 | 34.9 | 31.3 | 0 | 33.8 | -2.6 | 2.6 | 1017 | -0.01 | 0 | 0 | 15 | 15 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-06-21 10:10 | 53.1 | 40.3 | 0 | 6.6 | -1 | 1 | 1017 | 0.21 | 8.6 | 48 | 20 | 20.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-06-21 10:08 | 45.4 | 36.9 | 0 | 17.7 | -6.6 | 6.6 | 1017 | 1.45 | 22.8 | 108 | 22 | 20.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-06-21 10:06 | 54 | 39.3 | 0 | 6.7 | -4.2 | 4.2 | 1017 | 1.54 | 23.8 | 135 | 40 | 19.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-06-21 10:04 | 49.4 | 37.8 | 0.8 | 12 | -0.7 | 0.7 | 1017 | 0.05 | 4.3 | 22 | 5 | 21.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-06-21 10:01 | 51.3 | 39.5 | 0.3 | 8.9 | -0.9 | 0.9 | 1017 | 0.13 | 6.8 | 36 | 25 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-06-21 09:59 | 58.6 | 42.3 | 0 | 0 | 0 | 0 | 1017 | 0.13 | 3.2 | 20 | 8 | 19.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-06-21 09:57 | 39.1 | 32.2 | 3.3 | 25.4 | -0.6 | 0.6 | 1017 | 1.19 | 9.6 | 39 | 10 | 16.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-06-21 09:52 | 48.5 | 38.5 | 1.1 | 11.9 | -70.2 | 70.2 | 1018 | 0.31 | 10 | 50 | 50 | 35.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-06-20 15:17 | 48.8 | 36.7 | 0.7 | 13.8 | -1.2 | 1.2 | 1014 | 3.7 | 8.5 | 43 | 10 | 17.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-06-20 15:15 | 48.5 | 38.2 | 0 | 13.3 | -1.6 | 1.6 | 1014 | 0.41 | 12.2 | 62 | 15 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-06-20 15:14 | 51.1 | 38.9 | 0 | 10 | -3.3 | 3.3 | 1014 | 1.89 | 26.3 | 140 | 25 | 20.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-06-20 15:12 | 45.9 | 36.9 | 0 | 17.2 | -1.6 | 1.6 | 1014 | 0.18 | 3.8 | 18 | 10 | 18.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-06-20 15:09 | 49.7 | 37.5 | 1 | 11.8 | -6.1 | 6.1 | 1014 | -0.52 | 0 | 0 | 50 | 42.3 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-06-20 15:06 | 55.2 | 38.5 | 0 | 6.3 | -64.9 | 64.9 | 1014 | 0.9 | 17.7 | 102 | 99 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-06-20 15:04 | 53.7 | 37.8 | 0 | 8.5 | -35.2 | 35.2 | 1014 | 8.09 | 24.7 | 139 | 60 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-06-20 15:02 | 55.8 | 37.1 | 0.9 | 6.2 | -63.6 | 63.6 | 1014 | 0.75 | 7.5 | 44 | 50 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-06-20 15:00 | 55.4 | 37 | 0 | 7.6 | -5.8 | 5.8 | 1014 | 3.66 | 17.2 | 100 | 25 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-06-20 14:59 | 43.5 | 35.3 | 0 | 21.2 | -3.8 | 3.8 | 1014 | 11.65 | 29.2 | 133 | 45 | 37.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-06-20 14:56 | 53 | 37 | 1.6 | 8.4 | -5.1 | 5.1 | 1014 | 0.85 | 8.2 | 45 | 15 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-06-20 14:54 | 38.2 | 27.7 | 6.7 | 27.4 | -1.3 | 1.3 | 1014 | -0.14 | 0 | 0 | 5 | 21.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-06-20 14:52 | 60.2 | 39.7 | 0 | 0.1 | -19 | 19 | 1014 | 10.62 | 62.1 | 391 | 75 | 28.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-06-20 14:51 | 34.7 | 32.1 | 0 | 33.2 | -1.6 | 1.6 | 1014 | 9.32 | 26.2 | 95 | 20 | 31.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-06-20 14:49 | 41.9 | 34.6 | 0 | 23.5 | -6.3 | 6.3 | 1014 | 3.71 | 36 | 158 | 20 | 28.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-06-20 14:47 | 46 | 35.1 | 0 | 18.9 | -28.2 | 28.2 | 1014 | 1.41 | 21.8 | 105 | 20 | 36.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-06-20 14:45 | 44.7 | 33.5 | 0 | 21.8 | -13.7 | 13.7 | 1015 | 15.52 | 73.4 | 344 | 50 | 34.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-06-20 14:43 | 37.3 | 28.1 | 4.6 | 30 | -49 | 49 | 1014 | -0.09 | 0 | 0 | 80 | 23 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-06-20 14:41 | 36 | 27.6 | 3.3 | 33.1 | -6.4 | 6.4 | 1014 | 5.19 | 43 | 162 | 30 | 26.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-06-20 14:39 | 53.5 | 38.2 | 0.1 | 8.2 | -48.2 | 48.2 | 1014 | 0.94 | 29.2 | 164 | 99 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-06-20 13:41 | 62 | 38.7 | 0 | 0 | -0.4 | 0.4 | 1016 | 5.31 | 20.8 | 135 | 99 | 25.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-06-20 13:39 | 53.4 | 35.6 | 0 | 11 | 0 | 0 | 1016 | 3.39 | 16.4 | 92 | 99 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-06-20 13:37 | 55.3 | 36.7 | 0 | 8 | 0.2 | -0.2 | 1016 | 0.47 | 6.1 | 35 | 99 | 26 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-06-20 13:35 | 62.6 | 39.2 | 0 | 0 | -0.1 | 0.1 | 1016 | 1.19 | 9.8 | 64 | 99 | 25.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-06-20 13:33 | 60.4 | 38.4 | 0 | 1.2 | 0.2 | -0.2 | 1017 | 1.53 | 11.1 | 70 | 99 | 26.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-06-20 13:31 | 58.5 | 38.1 | 0 | 3.4 | 0.1 | -0.1 | 1017 | 2.21 | 13.3 | 81 | 99 | 25.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-06-20 13:28 | 60.2 | 38.2 | 0.9 | 0.7 | -0.7 | 0.7 | 1016 | 1.44 | 10.8 | 68 | 99 | 24.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-06-20 13:25 | 62.8 | 41.2 | 0 | 0 | 1.8 | -1.8 | 1016 | 2.76 | 32.1 | 211 | 99 | 26.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-06-20 13:23 | 61.7 | 41.5 | 0 | 0 | 1.8 | -1.8 | 1016 | 1.24 | 10 | 64 | 99 | 23.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-06-20 13:22 | 60.4 | 41.8 | 0 | 0 | 1.5 | -1.5 | 1016 | 1.55 | 11.1 | 70 | 99 | 23.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-06-20 13:21 | 60 | 41.7 | 0.2 | 0 | 2.7 | -2.7 | 1016 | 4.01 | 17.8 | 112 | 99 | 24.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-06-20 11:58 | 57.3 | 33.9 | 1.2 | 7.6 | -95 | 95 | 1016 | -0.3 | 0 | 0 | 50 | 17.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-06-20 11:56 | 60.6 | 36.7 | 0 | 2.7 | -91.7 | 91.7 | 1016 | 0.13 | 0.8 | 5 | 50 | 16.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-06-20 11:54 | 46.8 | 33.3 | 0 | 19.9 | -44.2 | 44.2 | 1016 | 1.62 | 11.2 | 55 | 15 | 17 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-06-20 11:53 | 51.9 | 36.2 | 0 | 11.9 | -10.6 | 10.6 | 1016 | 11.72 | 7.7 | 42 | 10 | 16.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-06-20 11:51 | 40.7 | 31.8 | 0 | 27.5 | -35.6 | 35.6 | 1016 | 0.23 | 4.2 | 18 | 10 | 15.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-06-20 11:49 | 60.8 | 36 | 0 | 3.2 | -92.2 | 92.2 | 1016 | 0.57 | 1.6 | 10 | 99 | 15.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-06-20 11:48 | 44.6 | 30 | 4 | 21.4 | -12.5 | 12.5 | 1016 | 0.63 | 0.3 | 1 | 0 | 16.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-06-20 11:46 | 58.2 | 36.2 | 0 | 5.6 | 0.1 | -0.1 | 1016 | -0.11 | 0 | 0 | 10 | 16.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-06-20 11:43 | 54.8 | 34.7 | 0.7 | 9.8 | -94.8 | 94.8 | 1016 | -0.2 | 0 | 0 | 50 | 16.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2017-06-20 11:41 | 60.6 | 38.8 | 0 | 0.6 | 0.3 | -0.3 | 1016 | -0.15 | 0 | 0 | 20 | 16.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-06-20 11:36 | 55.9 | 37.8 | 0 | 6.3 | -95.3 | 95.3 | 1016 | 0.04 | 3.5 | 20 | 99 | 16.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-06-20 11:30 | 43.8 | 31.2 | 2.4 | 22.6 | -96.3 | 96.3 | 1016 | -0.48 | 0 | 0 | 20 | 16.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-06-20 11:28 | 8.8 | 5 | 18.8 | 67.4 | -12 | 12 | 1016 | -0.44 | 0 | 0 | 0 | 14.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-06-20 11:27 | 44.1 | 31.7 | 2.3 | 21.9 | -0.2 | 0.2 | 1016 | 3.15 | 4 | 18 | 10 | 14.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-06-20 11:26 | 57.5 | 37.6 | 0.3 | 4.6 | -24.7 | 24.7 | 1016 | -0.37 | 0 | 0 | 5 | 15.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-06-20 11:24 | 49.2 | 35 | 0.1 | 15.7 | -21.5 | 21.5 | 1016 | 4.02 | 17.7 | 91 | 25 | 21.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-06-20 11:22 | 0.1 | 0.2 | 15.7 | 84 | -1.1 | 1.1 | 1016 | -0.72 | 0 | 0 | 0 | 15.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-06-20 11:21 | 37.8 | 27 | 5.8 | 29.4 | -88.4 | 88.4 | 1016 | -0.37 | 0 | 0 | 5 | 16.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-06-20 11:20 | 52.3 | 35.9 | 2 | 9.8 | -94.5 | 94.5 | 1016 | -0.31 | 0 | 0 | 25 | 15.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-06-20 11:18 | 46.7 | 35.5 | 0 | 17.8 | -2 | 2 | 1016 | 0.77 | 7.8 | 38 | 15 | 17.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-06-20 11:16 | 51.2 | 35.6 | 0 | 13.2 | -37 | 37 | 1016 | 1.11 | 8.3 | 44 | 20 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-06-20 11:15 | 48.9 | 34.3 | 1.1 | 15.7 | -97.7 | 97.7 | 1015 | -0.03 | 0 | 0 | 50 | 16 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-06-20 11:13 | 56.8 | 37.2 | 0.2 | 5.8 | -93.3 | 93.3 | 1015 | 0.31 | 4.3 | 25 | 99 | 15.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-06-20 10:22 | 41.4 | 34.2 | 0.4 | 24 | 0 | 0 | 1016 | 0.01 | 0.6 | 2 | 20 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-06-20 10:20 | 55.1 | 38.7 | 0 | 6.2 | -14.9 | 14.9 | 1016 | 7.66 | 51.9 | 299 | 50 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-06-20 10:18 | 48.1 | 35.9 | 0.2 | 15.8 | -2.4 | 2.4 | 1016 | 1.71 | 24.3 | 122 | 40 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-06-20 10:16 | 50 | 36.6 | 0 | 13.4 | -4.4 | 4.4 | 1016 | 1.93 | 26.1 | 136 | 40 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-06-20 10:15 | 56 | 38.5 | 0 | 5.5 | -58.1 | 58.1 | 1016 | 0.49 | 13 | 76 | 50 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-06-20 10:13 | 54.4 | 38.6 | 0 | 7 | -3.6 | 3.6 | 1016 | 4.07 | 18.1 | 103 | 25 | 15.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-06-20 10:11 | 60 | 41.6 | 0 | 0 | 0.4 | -0.4 | 1016 | -0.03 | 0 | 0 | 15 | 17.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-06-20 10:09 | 55.9 | 39.3 | 0 | 4.8 | 0.1 | -0.1 | 1016 | 2.53 | 7 | 41 | 15 | 20.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-06-20 10:07 | 51.1 | 37.8 | 0 | 11.1 | -0.8 | 0.8 | 1015 | 1.4 | 2.6 | 14 | 10 | 20.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-06-20 10:01 | 57.1 | 39.3 | 0 | 3.6 | -8.3 | 8.3 | 1015 | 24.68 | 43.9 | 263 | 50 | 27.8 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-06-20 09:59 | 49.7 | 38.1 | 0.1 | 12.1 | -19.5 | 19.5 | 1015 | >>>> | 0 | 0 | 99 | 35.7 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-06-20 09:57 | 51 | 38.4 | 0.2 | 10.4 | -1.3 | 1.3 | 1015 | 0.1 | 2.8 | 15 | 15 | 18.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-06-20 09:53 | 46.5 | 35.1 | 1.3 | 17.1 | -0.3 | 0.3 | 1015 | 0.04 | 0.8 | 4 | 20 | 28.8 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-06-20 09:51 | 55.2 | 40.8 | 0.7 | 3.3 | -70.2 | 70.2 | 1015 | -0.03 | 0 | 0 | 50 | 33.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-06-19 15:06 | 51.2 | 38.1 | 0 | 10.7 | -9.1 | 9.1 | 1020 | 8.86 | 54.9 | 294 | 70 | 42 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-06-19 15:05 | 15.3 | 11.2 | 15.4 | 58.1 | -32.8 | 32.8 | 1020 | -0.03 | 0 | 0 | 99 | 23.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-06-19 15:04 | 48.5 | 38.3 | 0 | 13.2 | -2.1 | 2.1 | 1020 | 12.42 | 7.6 | 38 | 25 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-06-19 15:02 | 49.8 | 37.9 | 0.1 | 12.2 | -3 | 3 | 1020 | 2.09 | 27.3 | 142 | 50 | 27.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-06-19 15:01 | 52.3 | 38.2 | 0 | 9.5 | -5.6 | 5.6 | 1020 | 1.63 | 24.3 | 133 | 40 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-06-19 14:59 | 57.4 | 39 | 0.2 | 3.4 | -0.6 | 0.6 | 1020 | 0.44 | 6 | 36 | 25 | 18.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-06-19 14:58 | 0.3 | 0.2 | 18.7 | 80.8 | -0.1 | 0.1 | 1020 | -0.01 | 0 | 0 | 0 | 17.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-06-19 14:56 | 52.1 | 37.2 | 0 | 10.7 | -1.7 | 1.7 | 1020 | 0.14 | 7.2 | 39 | 20 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-06-19 14:55 | 60.9 | 41.1 | 0 | 0 | -6.7 | 6.7 | 1020 | 29.41 | 48.2 | 307 | 99 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-06-19 14:54 | 51.6 | 38.8 | 0.2 | 9.4 | -6.8 | 6.8 | 1020 | 3.3 | 34 | 184 | 50 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-06-19 14:52 | 37.9 | 34.8 | 0 | 27.3 | -5.8 | 5.8 | 1020 | 1.44 | 22.3 | 88 | 50 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-06-19 14:51 | 54.8 | 38.7 | 0 | 6.5 | -1 | 1 | 1019 | 4.18 | 18.3 | 105 | 40 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-06-19 14:48 | 56.2 | 41.5 | 0 | 2.3 | -4.9 | 4.9 | 1019 | 3.24 | 15.7 | 92 | 25 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-06-19 14:46 | 41.4 | 36.4 | 0 | 22.2 | -8.4 | 8.4 | 1019 | 11.24 | 29.2 | 127 | 45 | 20.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-06-19 14:44 | 43 | 36.2 | 0.5 | 20.3 | -4.7 | 4.7 | 1019 | 10.1 | 27.8 | 125 | 42 | 22.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-06-19 14:42 | 60 | 41.6 | 0 | 0 | 0.1 | -0.1 | 1019 | 0.96 | 8.8 | 55 | 25 | 20 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-06-19 14:40 | 58.7 | 40 | 0 | 1.3 | -24.7 | 24.7 | 1019 | 5.54 | 21 | 129 | 99 | 18.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-06-19 14:38 | 55.1 | 38.4 | 0.3 | 6.2 | -4.2 | 4.2 | 1019 | 2.03 | 44.4 | 256 | 60 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-06-19 14:37 | 53.9 | 39.5 | 0 | 6.6 | -1 | 1 | 1019 | 3.44 | 8.1 | 46 | 20 | 22.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-06-19 14:35 | 56.9 | 39.1 | 0.2 | 3.8 | -4.1 | 4.1 | 1019 | 5.65 | 20.9 | 125 | 40 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-05-25 11:51 | 59 | 39.6 | 0 | 1.4 | -2.8 | 2.8 | 1035 | 21.1 | 40.9 | 253.2 | 40 | 32.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-05-25 11:44 | 59 | 39.4 | 0 | 1.6 | -5.4 | 5.4 | 1007 | 8.88 | 57.8 | 358.1 | 60 | 22.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-05-25 11:40 | 60.6 | 40.8 | 0 | 0 | -17.3 | 17.3 | 1007 | 3.51 | 35.5 | 225.5 | 45 | 38.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-05-25 11:35 | 61.7 | 39.3 | 0 | 0 | -1.5 | 1.5 | 1008 | 14.78 | 34.6 | 223.9 | 50 | 30 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-05-25 11:33 | 58.5 | 38.3 | 0 | 3.2 | -12.8 | 12.8 | 1008 | 18.58 | 38.8 | 238.2 | 55 | 22.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-05-25 11:30 | 51.4 | 37.3 | 0 | 11.3 | -7.9 | 7.9 | 1008 | 14.2 | 33.3 | 179.4 | 40 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-05-25 11:29 | 52.2 | 37.4 | 0 | 10.4 | -11.3 | 11.3 | 1008 | 24.27 | 93.2 | 510.3 | 80 | 34.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-05-25 11:27 | 56.5 | 39.2 | 0 | 4.3 | -1.9 | 1.9 | 1008 | 10.29 | 28.3 | 168 | 40 | 35.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-05-25 11:25 | 54.8 | 38.7 | 0.1 | 6.4 | -0.4 | 0.4 | 1007 | 5.82 | 21.2 | 122 | 20 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-05-25 11:21 | 61.2 | 42.8 | 0 | 0 | -4.4 | 4.4 | 1009 | 6.71 | 49.3 | 316.4 | 50 | 36.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-05-25 11:12 | 62.6 | 42.5 | 0 | 0 | 1.9 | -1.9 | 1007 | 1.82 | 12.2 | 80.1 | 99 | 22.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-05-23 13:50 | 58.3 | 39.1 | 0 | 2.6 | -9.3 | 9.3 | 1006 | 19.64 | 84 | 512 | 80 | 33.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-05-23 13:48 | 59.8 | 40.5 | 0 | 0 | -1.4 | 1.4 | 1006 | 7.01 | 23.3 | 146 | 25 | 33.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-05-23 13:46 | 59.9 | 40.7 | 0 | 0 | -0.5 | 0.5 | 1006 | 3.56 | 16.5 | 103 | 30 | 36.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-05-23 13:44 | 63.2 | 40.2 | 0 | 0 | -0.4 | 0.4 | 1006 | 7.66 | 24.8 | 164 | 35 | 27.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-05-23 13:41 | 59.6 | 39 | 0 | 1.4 | -10 | 10 | 1006 | 13.94 | 33.5 | 209 | 50 | 21.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-05-23 13:38 | 57.7 | 40 | 0 | 2.3 | -0.6 | 0.6 | 1005 | 14.68 | 34.4 | 208 | 25 | 20.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-05-23 13:33 | 56.3 | 40.1 | 0 | 3.6 | 0 | 0 | 1005 | 4.01 | 17.7 | 104 | 25 | 27.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-05-23 13:28 | 53.3 | 36.6 | 0.4 | 9.7 | -3.9 | 3.9 | 1005 | 15.31 | 34.7 | 194 | 40 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-05-23 13:26 | 55.1 | 40.2 | 0 | 4.7 | -3.2 | 3.2 | 1005 | 3.58 | 35.8 | 207 | 42 | 28.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-05-23 13:25 | 58.9 | 40.8 | 0 | 0.3 | -1.2 | 1.2 | 1006 | 15.94 | 35.4 | 218 | 40 | 28.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-05-23 13:20 | 50.2 | 38.7 | 0 | 11.1 | -0.2 | 0.2 | 1005 | 6.81 | 11.4 | 60 | 20 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-05-23 13:19 | 53.7 | 40.4 | 0 | 5.9 | -3.3 | 3.3 | 1005 | 4.04 | 17.3 | 97 | 20 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-05-23 13:16 | 59.7 | 41.3 | 0 | 0 | -11.9 | 11.9 | 1004 | 8.79 | 56.8 | 355 | 50 | 23.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-05-23 13:13 | 61.1 | 42.4 | 0 | 0 | -10.5 | 10.5 | 1004 | 1.29 | 21.3 | 137 | 45 | 35.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-05-23 13:09 | 59 | 41.4 | 0.2 | 0 | -5.9 | 5.9 | 1004 | 12.96 | 32 | 198 | 45 | 23.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-05-23 13:06 | 59.3 | 43.3 | 0 | 0 | -2.8 | 2.8 | 1004 | 0.03 | 3.3 | 20 | 25 | 22.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-05-23 13:03 | 56.9 | 39.6 | 0.7 | 2.8 | 0 | 0 | 1004 | -0.16 | 0 | 0 | 2 | 21.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-05-23 13:01 | 59.2 | 41.4 | 0 | 0 | -6 | 6 | 1006 | 11.55 | 29.5 | 183 | 40 | 38.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-05-23 11:55 | 57.4 | 40.3 | 0 | 2.3 | -12.2 | 12.2 | 1005 | 6.07 | 46.4 | 279 | 45 | 32.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-05-23 11:50 | 51.7 | 36.9 | 2 | 9.4 | -1.3 | 1.3 | 1005 | 16.86 | 9 | 48 | 20 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-05-23 11:49 | 62.7 | 40.9 | 0 | 0 | -0.1 | 0.1 | 1006 | 0.31 | 5 | 32 | 10 | 19.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-05-23 11:45 | 56.1 | 41.3 | 0 | 2.6 | -0.9 | 0.9 | 1006 | 0.33 | 11 | 64 | 18 | 24.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-05-23 11:43 | 60.7 | 42.3 | 0 | 0 | -0.8 | 0.8 | 1005 | 1.08 | 19.8 | 126 | 25 | 27.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-05-23 11:39 | 61.8 | 41.8 | 0 | 0 | -34.7 | 34.7 | 1004 | 2.33 | 13.5 | 87 | 60 | 19.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-05-23 11:36 | 50.1 | 38.3 | 0 | 11.6 | -0.1 | 0.1 | 1004 | 0.61 | 14.7 | 77 | 20 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-05-23 11:34 | 31.1 | 31.2 | 0 | 37.7 | -0.8 | 0.8 | 1004 | 0.8 | 1.9 | 6 | 5 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-05-23 11:30 | 46.3 | 37.4 | 0 | 16.3 | -1.6 | 1.6 | 1004 | 1.56 | 23.3 | 113 | 25 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-05-23 11:29 | 60.4 | 42.3 | 0 | 0 | -24.8 | 24.8 | 1004 | 13.99 | 33 | 209 | 99 | 22.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-05-23 11:26 | 62.7 | 41.1 | 0 | 0 | -5.5 | 5.5 | 1004 | 8.7 | 56.5 | 371 | 55 | 30.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-05-23 11:24 | 49.3 | 37 | 0.5 | 13.2 | -1.8 | 1.8 | 1004 | 2.42 | 28.9 | 149 | 25 | 38 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-05-23 11:21 | 62.9 | 41.1 | 0 | 0 | -6 | 6 | 1005 | 4.29 | 63 | 415 | 55 | 47.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-05-23 11:16 | 26 | 19.5 | 8.2 | 46.3 | 0 | 0 | 1005 | 1.28 | 10 | 27 | 20 | 19.7 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-05-23 11:15 | 42.4 | 38.4 | 0 | 19.2 | 0.5 | -0.5 | 1005 | -0.02 | 0 | 0 | 8 | 17.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-05-23 11:12 | 59.3 | 41.5 | 0 | 0 | -1.2 | 1.2 | 1006 | 1.02 | 19.5 | 121 | 25 | 19.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-05-23 11:08 | 53 | 40.3 | 0.1 | 6.6 | -0.7 | 0.7 | 1006 | 0.54 | 13.8 | 77 | 20 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-05-23 11:06 | 56.4 | 40.7 | 0.1 | 2.8 | 0 | 0 | 1006 | 1.86 | 12.2 | 72 | 25 | 18.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-05-23 11:01 | 58.4 | 40.2 | 0 | 1.4 | -6.1 | 6.1 | 1006 | 15.98 | 35.5 | 217 | 45 | 26.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-05-23 10:59 | 58.4 | 42.1 | 0 | 0 | -0.7 | 0.7 | 1006 | -0.07 | 0 | 0 | 20 | 18.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-05-23 10:56 | 61 | 41.3 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 10 | 23.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-05-23 10:35 | 44.5 | 39.1 | 0 | 16.4 | -0.3 | 0.3 | 1006 | 4.36 | 17.7 | 82 | 22 | 40.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-05-23 10:32 | 55.6 | 41 | 0 | 3.4 | -5 | 5 | 1007 | 10.05 | 27.8 | 162 | 45 | 29.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-05-23 10:28 | 56.8 | 39.6 | 0 | 3.6 | -6.8 | 6.8 | 1007 | 0.53 | 13.9 | 83 | 23 | 24.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-05-23 10:24 | 39.1 | 27.5 | 5.6 | 27.8 | -12.3 | 12.3 | 1007 | 3.78 | 17.3 | 71 | 40 | 16.7 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-05-23 10:22 | 56.7 | 41.7 | 0 | 1.6 | -1.3 | 1.3 | 1007 | 2.25 | 13.2 | 78 | 25 | 27.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-05-23 10:12 | 60.1 | 40.8 | 0 | 0 | -27 | 27 | 1007 | 6.11 | 21.7 | 137 | 60 | 26.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-05-23 10:09 | 60.8 | 41.5 | 0 | 0 | -17.3 | 17.3 | 1007 | 0.48 | 13.2 | 84 | 25 | 24.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-05-23 10:07 | 60.1 | 40.2 | 0 | 0 | -2.7 | 2.7 | 1008 | 2.93 | 33.1 | 208 | 45 | 23.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-05-23 10:01 | 55.6 | 37.7 | 0.4 | 6.3 | -3.7 | 3.7 | 1008 | 2.85 | 15 | 87 | 20 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-05-23 09:58 | 57.7 | 38.3 | 0 | 4 | -12.2 | 12.2 | 1008 | 3 | 33.4 | 202 | 50 | 21.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-05-23 09:56 | 55.6 | 32.5 | 0.1 | 11.8 | -1.8 | 1.8 | 1009 | 0.28 | 2.4 | 14 | 7 | 17.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-05-16 15:33 | 50.9 | 31.8 | 2.9 | 14.4 | -95.3 | 95.3 | 1008 | -0.15 | 0 | 0 | 40 | 17.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-05-16 15:31 | 61.2 | 37.2 | 0 | 1.6 | -93.4 | 93.4 | 1007 | 0.31 | 1.2 | 7 | 25 | 16.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-05-16 15:29 | 57 | 34.7 | 0 | 8.3 | -49.3 | 49.3 | 1008 | 0.94 | 8.6 | 51 | 15 | 17.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-05-16 15:27 | 54.8 | 37 | 0 | 8.2 | -10.2 | 10.2 | 1008 | 12.93 | 8.1 | 46 | 20 | 17.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-05-16 15:25 | 43.4 | 32.7 | 0 | 23.9 | -34.5 | 34.5 | 1008 | 0.4 | 5.5 | 25 | 10 | 16.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-05-16 15:24 | 60.8 | 37.1 | 0 | 2.1 | -94.2 | 94.2 | 1008 | 6.8 | 5.7 | 36 | 99 | 16.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-05-16 15:22 | 41 | 28 | 5.2 | 25.8 | -5.9 | 5.9 | 1008 | 0.6 | 0.3 | 1 | 0 | 17.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-05-16 15:20 | 4.7 | 3.5 | 15.7 | 76.1 | 0 | 0 | 1008 | 0.03 | 0.3 | 0 | 5 | 20.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-05-16 15:17 | 58.7 | 36.1 | 0 | 5.2 | -100.3 | 100.3 | 1008 | 0.14 | 3.2 | 19 | 50 | 18 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-05-16 15:14 | 58.6 | 38.4 | 0 | 3 | -101.8 | 101.8 | 1008 | 0.17 | 7.3 | 45 | 99 | 19.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-05-16 15:06 | 48.5 | 32.8 | 1.3 | 17.4 | -101.8 | 101.8 | 1008 | -0.03 | 0 | 0 | 25 | 19.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-05-16 15:04 | 0.2 | 0.2 | 16.8 | 82.8 | -2.8 | 2.8 | 1008 | -0.74 | 0 | 0 | 0 | 18.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-05-16 15:02 | 61.5 | 38.7 | 0 | 0 | 0.1 | -0.1 | 1008 | -0.04 | 0 | 0 | 10 | 21 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-05-16 15:00 | 51.4 | 33.3 | 2.4 | 12.9 | -33.8 | 33.8 | 1008 | -0.02 | 0 | 0 | 5 | 18.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-05-16 14:58 | 51 | 35.3 | 0.1 | 13.6 | -22.8 | 22.8 | 1008 | 4.9 | 19.5 | 104 | 10 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-05-16 14:57 | 0.1 | 0.2 | 15.8 | 83.9 | 0 | 0 | 1008 | 0 | 0 | 0 | 0 | 20.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-05-16 14:55 | 53.2 | 33.6 | 2.5 | 10.7 | -105.2 | 105.2 | 1008 | -0.21 | 0 | 0 | 5 | 20.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-05-16 14:54 | 45.9 | 31.9 | 3.6 | 18.6 | -100.5 | 100.5 | 1008 | -0.3 | 0 | 0 | 20 | 22.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-05-16 14:52 | 54.7 | 36.7 | 0 | 8.6 | -2 | 2 | 1008 | 1.21 | 9.9 | 56 | 10 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-05-16 14:51 | 55.7 | 37 | 0 | 7.3 | -37.7 | 37.7 | 1008 | 1.19 | 8.7 | 50 | 18 | 20.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-05-16 14:49 | 45.8 | 31.1 | 2.9 | 20.2 | -101.9 | 101.9 | 1008 | -0.13 | 0 | 0 | 40 | 21.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-05-16 14:47 | 60.2 | 37.9 | 0.1 | 1.8 | -99.6 | 99.6 | 1007 | 0.31 | 4.3 | 27 | 99 | 18.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-05-11 15:31 | 60.8 | 39.6 | 0 | 0 | -0.1 | 0.1 | 1017 | 0.28 | 4.7 | 30 | 99 | 24.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-05-11 15:29 | 64.4 | 39.7 | 0 | 0 | 0 | 0 | 1018 | -0.27 | 0 | 0 | 99 | 24.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-05-11 15:27 | 63.1 | 39.5 | 0 | 0 | -0.1 | 0.1 | 1018 | 0.05 | 2 | 13 | 99 | 25.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-05-11 15:25 | 64.7 | 39.7 | 0 | 0 | -0.1 | 0.1 | 1018 | 0.72 | 7.6 | 52 | 99 | 25.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-05-11 15:23 | 63.5 | 39.4 | 0 | 0 | -0.4 | 0.4 | 1018 | 0.59 | 6.9 | 46 | 99 | 23.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-05-11 15:21 | 61 | 39.1 | 0 | 0 | -0.1 | 0.1 | 1018 | 1.65 | 11.6 | 74 | 99 | 19.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-05-11 15:19 | 58.9 | 37.5 | 1.1 | 2.5 | -0.5 | 0.5 | 1017 | 0.14 | 3.2 | 20 | 99 | 27.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-05-11 15:15 | 64.8 | 41.6 | 0 | 0 | 1.8 | -1.8 | 1017 | 2.24 | 29.2 | 198 | 99 | 23.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-05-11 15:14 | 64.5 | 41.9 | 0 | 0 | 0.1 | -0.1 | 1017 | 0.81 | 8.1 | 55 | 99 | 21 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-05-11 15:13 | 62.8 | 42.4 | 0 | 0 | 0.4 | -0.4 | 1017 | -5.82 | 0 | 0 | 99 | 20.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-05-11 15:11 | 62.7 | 42.3 | 0 | 0 | 2.1 | -2.1 | 1017 | 2.89 | 15.3 | 100 | 99 | 22.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-05-11 14:57 | 62.3 | 42.1 | 0 | 0 | -25.4 | 25.4 | 1015 | 16.34 | 74.6 | 487 | 99 | 44.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-05-11 14:56 | 62.7 | 41.9 | 0 | 0 | -24.2 | 24.2 | 1015 | 11.71 | 105.7 | 695 | 99 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-05-11 14:55 | 57.4 | 39.4 | 0 | 3.2 | -7.9 | 7.9 | 1015 | 11.76 | 30 | 181 | 50 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-05-11 14:54 | 59.6 | 40.6 | 0 | 0 | -21.3 | 21.3 | 1015 | 11.3 | 62.7 | 391 | 99 | 38 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-05-11 14:51 | 58.4 | 40.6 | 0 | 1 | -18.9 | 18.9 | 1015 | 15.1 | 33.6 | 205 | 40 | 37.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-05-11 14:50 | 55.9 | 40.7 | 0 | 3.4 | -1.6 | 1.6 | 1015 | 9.78 | 27.2 | 159 | 40 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-05-11 14:48 | 55 | 40 | 0 | 5 | -4 | 4 | 1016 | 15.95 | 34.7 | 200 | 40 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-05-11 14:47 | 61.5 | 41.9 | 0 | 0 | -33.3 | 33.3 | 1016 | -0.06 | 0 | 0 | 99 | 27.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-05-11 14:46 | 51.5 | 36.6 | 1.4 | 10.5 | -36.5 | 36.5 | 1016 | 0.2 | 3.8 | 20 | 99 | 31.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-05-11 14:43 | 64.1 | 39.7 | 0 | 0 | -35.2 | 35.2 | 1016 | -0.11 | 0 | 0 | 99 | 20.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-05-11 14:41 | 54.5 | 38.2 | 0 | 7.3 | -7.6 | 7.6 | 1016 | 13.23 | 32.1 | 183 | 40 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-05-11 14:40 | 60.5 | 39.3 | 0 | 0.2 | -6.8 | 6.8 | 1016 | 14.56 | 72.8 | 462 | 75 | 32.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-05-11 14:38 | 63.1 | 40.7 | 0 | 0 | -0.7 | 0.7 | 1016 | 3.73 | 17.2 | 113 | 25 | 30.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-05-11 14:36 | 61.6 | 40.3 | 0 | 0 | -0.2 | 0.2 | 1016 | 2.77 | 14.7 | 94 | 25 | 35.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-05-11 14:35 | 62.8 | 39.2 | 0 | 0 | -35.3 | 35.3 | 1016 | 0.8 | 17.2 | 113 | 99 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-05-11 14:34 | 63.5 | 39.4 | 0 | 0 | -0.1 | 0.1 | 1016 | 4.44 | 19 | 126 | 25 | 25.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-05-11 14:32 | 59.3 | 38.2 | 0.4 | 2.1 | -34.3 | 34.3 | 1016 | 4.33 | 18.5 | 115 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-05-11 14:30 | 62.9 | 39.3 | 0 | 0 | -7.3 | 7.3 | 1016 | 7.85 | 25.4 | 167 | 40 | 20.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-05-11 14:29 | 63.5 | 39.7 | 0 | 0 | -0.3 | 0.3 | 1016 | 6.27 | 22.8 | 151 | 25 | 20.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-05-11 14:27 | 57.7 | 39.5 | 0 | 2.8 | -2.2 | 2.2 | 1016 | 14.24 | 33.3 | 201 | 25 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-05-11 13:50 | 61 | 40.7 | 0 | 0 | 0 | 0 | 1016 | 2.28 | 13.4 | 85 | 15 | 30 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-05-11 13:48 | 57.8 | 37.7 | 0.3 | 4.2 | -3.4 | 3.4 | 1016 | 6.53 | 49 | 296 | 50 | 29.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-05-11 13:47 | 61 | 37.7 | 0.1 | 1.2 | -3 | 3 | 1016 | 10.9 | 29.8 | 191 | 45 | 24.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-05-11 13:44 | 60.7 | 39.9 | 0 | 0 | -2.6 | 2.6 | 1016 | 2.1 | 27.8 | 177 | 50 | 28.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-05-11 13:41 | 60.9 | 40.3 | 0 | 0 | -0.9 | 0.9 | 1016 | 10.93 | 29.5 | 188 | 30 | 27.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-05-11 13:38 | 56.5 | 37.7 | 0 | 5.8 | 0 | 0 | 1016 | -0.07 | 0 | 0 | 5 | 22.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-05-11 13:37 | 52.1 | 37.9 | 0 | 10 | -1.3 | 1.3 | 1016 | 0.99 | 4.3 | 23 | 15 | 24.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-05-11 13:35 | 61.9 | 39.2 | 0 | 0 | -22.2 | 22.2 | 1016 | 6.2 | 78.2 | 507 | 99 | 25.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-05-11 13:33 | 48.3 | 32.8 | 1 | 17.9 | -2.2 | 2.2 | 1016 | 4.42 | 4.7 | 24 | 5 | 18.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-05-11 13:32 | 56.2 | 37.2 | 0 | 6.6 | -3 | 3 | 1016 | 4.61 | 19.2 | 113 | 25 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-05-11 13:30 | 54.4 | 37.5 | 0 | 8.1 | -5.1 | 5.1 | 1016 | 3.87 | 37.4 | 213 | 40 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-05-11 13:29 | 54.4 | 38.7 | 0 | 6.9 | -0.9 | 0.9 | 1016 | 2.62 | 14.1 | 80 | 25 | 34 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-05-11 13:28 | 54.2 | 37.7 | 0 | 8.1 | -25 | 25 | 1016 | 15.67 | 74.6 | 423 | 99 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-05-11 13:25 | 60.6 | 40.3 | 0 | 0 | 0.1 | -0.1 | 1016 | 2.27 | 6.7 | 42 | 10 | 22 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-05-11 13:23 | 57.8 | 40.3 | 0 | 1.9 | -1.9 | 1.9 | 1016 | 2.56 | 13.9 | 84 | 25 | 36.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-05-11 13:22 | 56.5 | 40.6 | 0 | 2.9 | -23.7 | 23.7 | 1016 | 18.79 | 130.2 | 771 | 99 | 42.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-05-11 13:21 | 50.6 | 38.7 | 0 | 10.7 | -2.2 | 2.2 | 1016 | 1 | 8.8 | 47 | 15 | 20.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-05-11 13:19 | 56.5 | 39.5 | 0.8 | 3.2 | -1.1 | 1.1 | 1016 | 1.08 | 19.9 | 118 | 20 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-05-11 13:18 | 52.6 | 39 | 0 | 8.4 | -2.7 | 2.7 | 1016 | 1.69 | 24.1 | 133 | 25 | 38.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-05-11 13:17 | 48.2 | 36.7 | 0 | 15.1 | -10.3 | 10.3 | 1016 | 12.4 | 65.3 | 330 | 50 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-05-11 13:15 | 55.6 | 39 | 0.6 | 4.8 | -0.3 | 0.3 | 1016 | 7.87 | 12.3 | 71 | 15 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-05-11 13:14 | 56.9 | 38.6 | 0 | 4.5 | -5.3 | 5.3 | 1016 | 17.51 | 37.3 | 222 | 50 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-05-11 13:12 | 56.9 | 39.4 | 0 | 3.7 | -31.4 | 31.4 | 1016 | 0.48 | 13 | 77 | 25 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-05-11 13:11 | 53.5 | 36.7 | 0 | 9.8 | -8.2 | 8.2 | 1016 | 4.55 | 40.9 | 229 | 40 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-05-11 13:10 | 53.8 | 37.7 | 0.3 | 8.2 | 0 | 0 | 1016 | 7.94 | 6.3 | 35 | 10 | 20.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-05-11 13:09 | 58.1 | 41 | 0 | 0.9 | 0 | 0 | 1016 | 14.95 | 8.5 | 52 | 15 | 30.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-05-11 12:58 | 57.3 | 40.7 | 0 | 2 | -32.1 | 32.1 | 1015 | 11.05 | 99.6 | 598 | 99 | 41.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-05-11 12:57 | 20.4 | 14.4 | 3.2 | 62 | -36.4 | 36.4 | 1015 | 0.83 | 1.9 | 4 | 0 | 22.9 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-05-11 12:56 | 60.3 | 43.1 | 0 | 0 | -36.7 | 36.7 | 1015 | 0.23 | 4.1 | 26 | 99 | 30 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-05-11 12:54 | 60.8 | 41.4 | 0 | 0 | -38.9 | 38.9 | 1015 | -0.13 | 0 | 0 | 50 | 21.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-05-11 12:52 | 60.7 | 40.5 | 0 | 0 | -12.4 | 12.4 | 1015 | 7.59 | 53 | 337 | 50 | 23.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-05-11 12:50 | 56.1 | 39.7 | 0 | 4.2 | -1 | 1 | 1015 | 3.78 | 17 | 100 | 20 | 34.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-05-11 12:49 | 3 | 3.4 | 16.7 | 76.9 | -6 | 6 | 1015 | -0.16 | 0 | 0 | 0 | 22.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-05-11 12:48 | 19.9 | 14 | 13 | 53.1 | -38.4 | 38.4 | 1015 | -0.09 | 0 | 0 | 99 | 26.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-05-11 12:47 | 56.7 | 39.2 | 0 | 4.1 | -33.3 | 33.3 | 1015 | 5.26 | 69.2 | 411 | 99 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-05-11 12:45 | 56.9 | 41 | 0 | 2.1 | -0.5 | 0.5 | 1015 | 2.26 | 12.9 | 77 | 25 | 43.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-05-11 11:52 | 59.8 | 42.2 | 0 | 0 | -22.5 | 22.5 | 1015 | 19.12 | 81.1 | 508 | 99 | 39 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-05-11 11:50 | 59.9 | 43.4 | 0 | 0 | -29.3 | 29.3 | 1015 | 11.77 | 63.5 | 398 | 99 | 35.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-05-11 11:49 | 61.1 | 42.1 | 0 | 0 | -18.8 | 18.8 | 1015 | 8.4 | 88.8 | 568 | 99 | 34.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-05-11 11:48 | 8.8 | 6.4 | 14.9 | 69.9 | -2.8 | 2.8 | 1015 | -0.19 | 0 | 0 | 0 | 34.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-05-11 11:47 | 62.3 | 41.4 | 0 | 0 | -23 | 23 | 1015 | 12.99 | 67.8 | 442 | 99 | 34.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-05-11 11:45 | 61.9 | 42 | 0 | 0 | -38.9 | 38.9 | 1015 | 0.15 | 7.1 | 46 | 99 | 32 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-05-11 11:43 | 4.7 | 3.1 | 14.5 | 77.7 | -41 | 41 | 1015 | -0.18 | 0 | 0 | 99 | 20.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-05-11 11:42 | 57.6 | 40.2 | 0.2 | 2 | -2.8 | 2.8 | 1015 | 9 | 26.6 | 160 | 25 | 25.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-05-11 11:40 | 63.4 | 41.4 | 0 | 0 | -0.7 | 0.7 | 1015 | 1.32 | 21.9 | 145 | 30 | 35.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-05-11 11:38 | 57 | 48.6 | 0 | 0 | -17.8 | 17.8 | 1015 | 1 | 18.3 | 109 | 25 | 32.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-05-11 11:36 | 10.8 | 7 | 15.9 | 66.3 | -42.4 | 42.4 | 1015 | 0.01 | 2.2 | 2 | 99 | 18.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-05-11 11:35 | 19.5 | 12.8 | 13.4 | 54.3 | -41.8 | 41.8 | 1015 | 0.03 | 1.5 | 3 | 99 | 19.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-05-11 11:34 | 45.5 | 33.6 | 4.4 | 16.5 | -41.9 | 41.9 | 1015 | -0.11 | 0 | 0 | 99 | 20.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-05-11 11:32 | 61.5 | 41.2 | 0 | 0 | -39.3 | 39.3 | 1015 | 3.47 | 56.3 | 362 | 99 | 38.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-05-11 11:31 | 61.8 | 41.5 | 0 | 0 | -7.3 | 7.3 | 1015 | 12.73 | 32 | 207 | 40 | 22.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-05-11 11:29 | 5.1 | 3.5 | 15.6 | 75.8 | -5.6 | 5.6 | 1015 | -0.06 | 0 | 0 | 0 | 19.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-05-11 11:28 | 56.3 | 39.2 | 0.3 | 4.2 | -6.6 | 6.6 | 1015 | 2.19 | 28.5 | 168 | 25 | 21 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-05-11 11:27 | 60.9 | 42.6 | 0 | 0 | -4.8 | 4.8 | 1015 | 0.44 | 12.7 | 81 | 15 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2017-05-11 11:15 | 0.2 | 0.2 | 15.4 | 84.2 | -38.5 | 38.5 | 1015 | -0.27 | 0 | 0 | 0 | 15.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-05-11 11:14 | 62.4 | 41.7 | 0 | 0 | -42.4 | 42.4 | 1015 | 7.58 | 86.5 | 565 | 99 | 15.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2017-05-11 11:13 | 48.7 | 34.4 | 3.8 | 13.1 | -45.8 | 45.8 | 1015 | -0.22 | 0 | 0 | 99 | 21.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-05-11 11:12 | 62.3 | 41 | 0 | 0 | -47.9 | 47.9 | 1015 | -0.21 | 0 | 0 | 99 | 17 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-05-11 11:10 | 64.2 | 40.3 | 0 | 0 | 0.2 | -0.2 | 1014 | -0.19 | 0 | 0 | 2 | 16.9 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-05-11 11:08 | 46.7 | 36.2 | 0 | 17.1 | -1.8 | 1.8 | 1014 | 0.25 | 9.4 | 46 | 15 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-05-11 11:07 | 62.8 | 41.2 | 0 | 0 | -5.9 | 5.9 | 1015 | 8.14 | 25 | 164 | 25 | 37.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-05-11 11:04 | 62.5 | 41.6 | 0 | 0 | -47.8 | 47.8 | 1014 | 0.09 | 5.6 | 37 | 99 | 38.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2017-05-11 11:03 | 30.2 | 21.5 | 10.1 | 38.2 | -47.2 | 47.2 | 1014 | -0.06 | 0 | 0 | 99 | 20.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-05-11 11:01 | 55.8 | 38.3 | 1.9 | 4 | -48.2 | 48.2 | 1014 | -0.06 | 0 | 0 | 99 | 20.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-05-11 10:40 | 41.6 | 34.3 | 0 | 24.1 | -0.3 | 0.3 | 1016 | 1.54 | 10.8 | 47 | 15 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-05-11 10:38 | 58.5 | 39.4 | 0 | 2.1 | -11.1 | 11.1 | 1016 | 4.87 | 41.8 | 256 | 48 | 32.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-05-11 10:36 | 46.6 | 35.5 | 0 | 17.9 | -4.2 | 4.2 | 1016 | 2.32 | 28.6 | 139 | 25 | 31.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-05-11 10:35 | 50.8 | 36.8 | 0 | 12.4 | -5.7 | 5.7 | 1016 | 2.98 | 32.4 | 172 | 25 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-05-11 10:33 | 41.6 | 33.7 | 0 | 24.7 | -76.1 | 76.1 | 1016 | 1.61 | 22.9 | 99 | 99 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-05-11 10:32 | 54.9 | 38.5 | 0 | 6.6 | -4.3 | 4.3 | 1016 | 5.34 | 20.8 | 119 | 20 | 17.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-05-11 10:30 | 48.4 | 36.5 | 0.4 | 14.7 | -0.2 | 0.2 | 1016 | 8.35 | 6.3 | 32 | 15 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-05-11 10:29 | 54.1 | 38.8 | 0 | 7.1 | -2.1 | 2.1 | 1016 | 2.15 | 6.4 | 36 |  | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-05-11 10:27 | 45 | 35.2 | 0.6 | 19.2 | -1.9 | 1.9 | 1016 | 10.96 | 7.2 | 34 |  | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-05-11 10:17 | 42.9 | 35.1 | 2.5 | 19.5 | -0.8 | 0.8 | 1014 | -0.23 | 0 | 0 |  | 25 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-05-11 10:16 | 58.9 | 41.2 | 0 | 0 | -44.3 | 44.3 | 1014 | 0.86 | 27.9 | 172 |  | 37.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-05-11 10:14 | 47.5 | 36.9 | 0 | 15.6 | -1.2 | 1.2 | 1014 | 11.72 | 29.6 | 147 |  | 35.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-05-11 10:13 | 45.7 | 36.3 | 0 | 18 | -0.4 | 0.4 | 1014 | 0.53 | 13.5 | 65 | 10 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-05-11 10:11 | 56.5 | 40 | 0.5 | 3 | -2.8 | 2.8 | 1014 | 12.48 | 7.9 | 46 | 5 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-05-11 10:10 | 52.6 | 40.1 | 0 | 7.3 | -37.5 | 37.5 | 1014 | 7.76 | 23.2 | 128 | 50 | 48.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-05-11 10:08 | 50.9 | 38.1 | 0.8 | 10.2 | -7.9 | 7.9 | 1014 | 1.38 | 21.9 | 117 | 15 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-05-11 10:07 | 53.4 | 40.1 | 0 | 6.5 | -17.1 | 17.1 | 1014 | 14.43 | 32.3 | 180 | 40 | 43 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-05-11 10:05 | 59.5 | 41.6 | 0.3 | 0 | -4.3 | 4.3 | 1014 | 2.55 | 3.5 | 22 | 5 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-05-11 10:04 | 25.2 | 28.1 | 0.6 | 46.1 | -1.8 | 1.8 | 1014 | 2.66 | 3.5 | 9 | 5 | 19.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-05-11 09:58 | 56.7 | 39.5 | 0.1 | 3.7 | -44.2 | 44.2 | 1014 | -0.01 | 0 | 0 | 25 | 24.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-05-11 09:56 | 55.6 | 40.8 | 0 | 3.6 | -1.5 | 1.5 | 1014 | 1.27 | 10 | 58 | 10 | 19.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-05-11 09:55 | 41.5 | 35.1 | 0 | 23.4 | -3.1 | 3.1 | 1014 | 1.84 | 25.1 | 109 | 20 | 34 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-05-11 09:53 | 58.6 | 40.7 | 0 | 0.7 | -40.9 | 40.9 | 1014 | 6.96 | 79 | 485 | 90 | 41.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-05-11 09:51 | 60.3 | 41 | 0 | 0 | -6.8 | 6.8 | 1014 | 19.26 | 39 | 246 | 40 | 26 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-05-11 09:50 | 60.5 | 41.8 | 0 | 0 | -25.8 | 25.8 | 1014 | 13.98 | 33.1 | 209 | 50 | 22.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-05-11 09:48 | 45.3 | 35.9 | 0 | 18.8 | -0.6 | 0.6 | 1013 | 0.76 | 16.4 | 78 | 10 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-05-11 09:47 | 64.2 | 40.6 | 0 | 0 | -5.9 | 5.9 | 1013 | 7.43 | 52.5 | 353 | 55 | 29.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-05-11 09:44 | 55 | 39 | 0 | 6 | -19.2 | 19.2 | 1013 | 1.29 | 34.8 | 200 | 40 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-05-11 09:43 | 41.8 | 33.8 | 1 | 23.4 | -4.1 | 4.1 | 1013 | 4.67 | 39.7 | 173 | 20 | 40.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-05-11 09:40 | 49.6 | 37.2 | 0.2 | 13 | -1.9 | 1.9 | 1013 | 1.71 | 11.6 | 60 | 10 | 18.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-05-11 09:38 | 46.1 | 37.7 | 0 | 16.2 | -0.2 | 0.2 | 1013 | 2 | 12.2 | 59 | 15 | 33.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-05-11 09:37 | 57.2 | 42.1 | 0 | 0.7 | -24.8 | 24.8 | 1013 | 1.43 | 2.6 | 15 | 99 | 28.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-05-11 09:35 | 49.4 | 38.3 | 0 | 12.3 | -1.9 | 1.9 | 1013 | 13.73 | 31.3 | 162 | 25 | 48.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-05-11 09:34 | 64.9 | 40.6 | 0 | 0 | -5.7 | 5.7 | 1013 | 3.14 | 54.3 | 369 | 45 | 47.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-05-11 09:32 | 49.3 | 38.7 | 0 | 12 | -0.8 | 0.8 | 1013 | 7.63 | 11.7 | 60 | 15 | 39.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-05-11 09:30 | 53.4 | 38.5 | 0 | 8.1 | -1.5 | 1.5 | 1013 | 1.18 | 20.4 | 114 | 25 | 35.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-05-11 09:29 | 44.1 | 36.9 | 0.7 | 18.3 | -1.1 | 1.1 | 1013 | 16.82 | 2 | 9 | 5 | 17 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-05-10 14:23 | 55.2 | 38.1 | 0 | 6.7 | -13 | 13 | 1015 | 13.34 | 67.9 | 392 | 50 | 41.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-05-10 14:22 | 61.1 | 40.4 | 0 | 0 | -40.4 | 40.4 | 1015 | -0.04 | 0 | 0 | 99 | 29.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-05-10 14:20 | 60.9 | 40.5 | 0 | 0 | -0.1 | 0.1 | 1015 | 2.92 | 3.7 | 24 | 20 | 33.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-05-10 14:18 | 54.5 | 38.2 | 0 | 7.3 | -3.5 | 3.5 | 1015 | 3.09 | 33.2 | 190 | 40 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-05-10 14:17 | 50.7 | 37.7 | 0 | 11.6 | -9.4 | 9.4 | 1015 | 4.11 | 38.2 | 203 | 40 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-05-10 14:15 | 62.4 | 39.2 | 0 | 0 | 0.1 | -0.1 | 1015 | 0.27 | 4.6 | 30 | 7 | 21.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-05-10 14:14 | 2.9 | 1.9 | 17.5 | 77.7 | 1.8 | -1.8 | 1015 | -0.04 | 0 | 0 | 0 | 22.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-05-10 14:11 | 58 | 37.2 | 0 | 4.8 | -1 | 1 | 1015 | 0.11 | 6.4 | 39 | 5 | 24.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-05-10 14:10 | 55.7 | 37.9 | 0 | 6.4 | -2 | 2 | 1015 | 4.52 | 18.6 | 108 | 50 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-05-10 14:09 | 60.3 | 40.6 | 0 | 0 | -0.5 | 0.5 | 1015 | 0.39 | 11.9 | 75 | 15 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-05-10 14:08 | 60.6 | 40.6 | 0 | 0 | -1.1 | 1.1 | 1015 | 0.96 | 18.7 | 119 | 25 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-05-10 14:07 | 51.8 | 37.8 | 0 | 10.4 | -1.1 | 1.1 | 1015 | 6.33 | 22.3 | 121 | 25 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-05-10 13:55 | 55.9 | 40.6 | 0 | 3.5 | -6.6 | 6.6 | 1015 | 4.35 | 18.1 | 106 | 25 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-05-10 13:54 | 1 | 0.9 | 16.2 | 81.9 | -44.5 | 44.5 | 1015 | -0.25 | 0 | 0 | 40 | 25 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-05-10 13:53 | 52.5 | 38.9 | 0 | 8.6 | -25.2 | 25.2 | 1015 | 13.49 | 32 | 176 | 50 | 25.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-05-10 13:51 | 54 | 38.9 | 0 | 7.1 | 0 | 0 | 1015 | 2.52 | 14 | 79 | 20 | 26.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-05-10 13:50 | 61.7 | 40 | 0 | 0 | -42.8 | 42.8 | 1015 | 2.31 | 13.4 | 86 | 50 | 22.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-05-10 13:49 | 57.9 | 38.7 | 0 | 3.4 | -5.1 | 5.1 | 1015 | 2.73 | 51.4 | 312 | 50 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-05-10 13:47 | 49.6 | 37.5 | 0.3 | 12.6 | -1.9 | 1.9 | 1015 | 10.34 | 14 | 72 | 25 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-05-10 13:46 | 57.1 | 38.3 | 0.4 | 4.2 | -4.8 | 4.8 | 1016 | 8.39 | 25.5 | 152 | 25 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-05-10 13:12 | 54.9 | 38.4 | 0 | 6.7 | -3.5 | 3.5 | 1016 | 10.45 | 28.5 | 163 | 40 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-05-10 13:11 | 53 | 37.5 | 0 | 9.5 | -16.3 | 16.3 | 1016 | 11.57 | 29.9 | 166 | 40 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-05-10 13:09 | 57.5 | 38.7 | 0 | 3.8 | -10.8 | 10.8 | 1015 | 18.87 | 38.4 | 231 | 40 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-05-10 13:06 | 58.1 | 38.6 | 0 | 3.3 | -5.5 | 5.5 | 1015 | 17.52 | 37.2 | 226 | 40 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-05-10 13:04 | 51.9 | 37.8 | 0 | 10.3 | -16.2 | 16.2 | 1015 | >>>> | 0 | 0 | 99 | 34.3 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-05-10 13:02 | 58.8 | 40.8 | 0 | 0.4 | 0.1 | -0.1 | 1015 | -0.03 | 0 | 0 | 10 | 20.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-05-10 13:00 | 61.6 | 40 | 0 | 0 | 0.5 | -0.5 | 1015 | -0.03 | 0 | 0 | 10 | 20.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-05-10 12:57 | 58.9 | 41.7 | 0 | 0 | -72.5 | 72.5 | 1015 | 0.04 | 3.6 | 22 | 50 | 22.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-05-10 12:46 | 56.5 | 39 | 0 | 4.5 | -1.1 | 1.1 | 1015 | 8.53 | 26 | 154 | 40 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-05-10 12:44 | 5.7 | 4.3 | 14.7 | 75.3 | 0.2 | -0.2 | 1015 | -0.05 | 0 | 0 | 10 | 22.9 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-05-10 12:42 | 56 | 37.4 | 0.7 | 5.9 | 1.2 | -1.2 | 1015 | -0.02 | 0 | 0 | 3 | 22.3 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-05-10 12:40 | 0.1 | 0.1 | 17.3 | 82.5 | 0.2 | -0.2 | 1015 | 0.01 | 0.6 | 0 | 0 | 21.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-05-10 12:37 | 41.1 | 32.2 | 2.1 | 24.6 | -65.2 | 65.2 | 1015 | 9.33 | 25.3 | 109 | 50 | 40.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-05-10 12:36 | 53.8 | 38.9 | 0 | 7.3 | 0 | 0 | 1015 | 0.02 | 2.5 | 14 | 20 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-05-10 12:34 | 54.1 | 37.3 | 0 | 8.6 | -26 | 26 | 1015 | 13.43 | 69.4 | 393 | 70 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-05-10 12:32 | 46.4 | 35.2 | 0 | 18.4 | -1.5 | 1.5 | 1015 | -0.03 | 0 | 0 | 15 | 21.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-05-10 12:31 | 56.1 | 39.8 | 0 | 4.1 | -0.3 | 0.3 | 1015 | 0.92 | 18.2 | 107 | 25 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-05-10 12:29 | 49.7 | 36.8 | 0 | 13.5 | -7.1 | 7.1 | 1015 | 2.3 | 28.8 | 150 | 40 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-05-10 12:28 | 59.7 | 39.9 | 0 | 0.4 | -1.1 | 1.1 | 1014 | 0.84 | 17.8 | 111 | 25 | 20.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-05-10 12:25 | 57.1 | 40 | 0 | 2.9 | 0 | 0 | 1014 | 0.25 | 9.6 | 57 | 25 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-05-10 12:24 | 60.5 | 41.3 | 0 | 0 | 0.2 | -0.2 | 1014 | 0.18 | 8.1 | 51 | 25 | 28.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-05-10 12:21 | 60.3 | 41.5 | 0 | 0 | 0.3 | -0.3 | 1014 | 0.19 | 3.8 | 24 | 25 | 25 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-05-10 12:20 | 60.1 | 40 | 0.2 | 0 | 0 | 0 | 1014 | 1.61 | 11.4 | 72 | 20 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A455 | 2017-05-10 09:34 | 45.1 | 64.6 | 0 | 0 | -0.2 | 0.2 | 1016 | -0.09 | 0 | 0 | 5 | 22.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2017-05-10 09:33 | 44.5 | 66.7 | 0 | >>>> | -0.2 | 0.2 | 1016 | -0.1 | 0 | 0 | 2 | 22.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A453 | 2017-05-10 09:31 | 33.8 | 78.1 | 0 | >>>> | -0.4 | 0.4 | 1017 | -0.09 | 0 | 0 | 2 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2017-05-10 09:30 | 2.5 | 16.1 | 14.4 | 67 | -0.5 | 0.5 | 1016 | -0.05 | 0 | 0 | 2 | 23.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2017-05-10 09:28 | 10.4 | 67.3 | 1.1 | 21.2 | -14.2 | 14.2 | 1017 | -0.03 | 0 | 0 | 5 | 22.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-05-10 09:24 | 62.2 | 38.6 | 0 | 0 | -4.3 | 4.3 | 1017 | 31.8 | 51 | 332 | 50 | 24 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-05-10 09:22 | 40.7 | 27.9 | 6.8 | 24.6 | -80.5 | 80.5 | 1017 | -0.57 | 0 | 0 | 99 | 17.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-05-10 09:21 | 58.5 | 38.8 | 0 | 2.7 | -7.1 | 7.1 | 1016 | 20.83 | 40.8 | 250 | 40 | 23.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-05-10 09:19 | 61.2 | 41.4 | 0 | 0 | -1 | 1 | 1016 | 4.6 | 18.9 | 121 | 40 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-05-10 09:16 | 45.4 | 36.7 | 0 | 17.9 | -0.3 | 0.3 | 1016 | 0.96 | 8.5 | 40 | 15 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-05-10 09:14 | 53.5 | 40 | 0.3 | 6.2 | -24.4 | 24.4 | 1016 | 9.89 | 94.8 | 531 | 50 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-05-10 09:08 | 61.2 | 40.9 | 0 | 0 | -3.2 | 3.2 | 1018 | 0.17 | 3.6 | 23 | 99 | 17.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-05-10 09:06 | 62.4 | 39.9 | 0 | 0 | -1.7 | 1.7 | 1018 | -0.1 | 0 | 0 | 99 | 27.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-05-10 09:03 | 62.6 | 40 | 0 | 0 | -1.2 | 1.2 | 1018 | 0.79 | 7.8 | 51 | 99 | 31.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-05-10 09:00 | 59.6 | 39.5 | 0.1 | 0.8 | -2.7 | 2.7 | 1016 | 2.94 | 32 | 200 | 99 | 44.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-05-10 08:43 | 55.5 | 38.9 | 0 | 5.6 | 0.2 | -0.2 | 1016 | 1.75 | 11.9 | 69 | 10 | 17.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-05-10 08:39 | 4.9 | 17.5 | 4.3 | 73.3 | 0.5 | -0.5 | 1017 | 5.1 | 19.5 | 10 | 40 | 12.2 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-05-09 14:56 | 57.5 | 39 | 0 | 3.5 | -3.5 | 3.5 | 1018 | 7.98 | 24.6 | 148 | 40 | 38.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-05-09 14:54 | 56.7 | 39.9 | 0 | 3.4 | -0.6 | 0.6 | 1017 | 0.39 | 12.2 | 72 | 25 | 13.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-05-09 14:52 | 57.7 | 38.6 | 0 | 3.7 | -5.9 | 5.9 | 1017 | 0.63 | 15.2 | 92 | 15 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-05-09 14:51 | 20.2 | 12.6 | 10.5 | 56.7 | -38 | 38 | 1018 | 0.03 | 3.1 | 6 | 99 | 16.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-05-09 14:49 | 57.1 | 39.9 | 0.6 | 2.4 | -35 | 35 | 1017 | 2.33 | 13.2 | 78 | 50 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-05-09 14:48 | 53.3 | 37.3 | 3.3 | 6.1 | -40.3 | 40.3 | 1017 | 0.08 | 8.5 | 47 | 99 | 19.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-05-09 14:46 | 62.1 | 40 | 0 | 0 | -1.2 | 1.2 | 1017 | 0.29 | 4.8 | 31 | 15 | 18.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-05-09 14:44 | 54.8 | 39.3 | 0 | 5.9 | -9 | 9 | 1018 | 1.22 | 20.9 | 120 | 25 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-05-09 14:43 | 56.2 | 39.5 | 0 | 4.3 | -1.6 | 1.6 | 1018 | 3.55 | 16.8 | 98 | 25 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-05-09 14:41 | 0.1 | 0.1 | 17.2 | 82.6 | -0.3 | 0.3 | 1018 | 0.02 | 1.2 | 0 | 0 | 15 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-05-09 14:40 | 24.7 | 16.3 | 12 | 47 | -39.6 | 39.6 | 1018 | 0.03 | 1.5 | 4 | 50 | 16.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-05-09 14:39 | 50.6 | 35.5 | 2.4 | 11.5 | -7 | 7 | 1018 | 0.2 | 1.9 | 10 | 5 | 17.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-05-09 14:38 | 56.8 | 40.3 | 0 | 2.9 | -1.2 | 1.2 | 1018 | 2.34 | 13.5 | 80 | 25 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-05-09 14:22 | 61.8 | 39.8 | 0 | 0 | -70.1 | 70.1 | 1017 | 0.22 | 8.7 | 56 | 99 | 25.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-05-09 14:21 | 60.6 | 39.7 | 0 | 0 | -27.7 | 27.7 | 1017 | 6.35 | 22.3 | 141 | 50 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-05-09 14:20 | 55.1 | 36.1 | 1.2 | 7.6 | -53.4 | 53.4 | 1017 | 2.77 | 14.4 | 83 | 40 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-05-09 14:18 | 58.9 | 38.3 | 0.6 | 2.2 | -68.9 | 68.9 | 1017 | 0.4 | 5.4 | 33 | 99 | 25.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-05-09 14:16 | 55.9 | 39.1 | 0.7 | 4.3 | -1.5 | 1.5 | 1017 | 7.62 | 24.2 | 141 | 40 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-05-09 14:15 | 54.6 | 37.5 | 1.1 | 6.8 | -5 | 5 | 1017 | 1 | 8.9 | 51 | 15 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-05-09 14:13 | 47.2 | 34 | 2.9 | 15.9 | -1.6 | 1.6 | 1017 | 0.31 | 4.9 | 24 | 10 | 21.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-05-09 14:11 | 61.8 | 40.3 | 0 | 0 | -14 | 14 | 1017 | 0.4 | 12.1 | 78 | 25 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-05-09 14:10 | 49.8 | 38 | 0 | 12.2 | -11 | 11 | 1017 | 17.18 | 35.8 | 186 | 50 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-05-09 14:09 | 55.7 | 40.8 | 0.3 | 3.2 | -42.5 | 42.5 | 1017 | -0.01 | 0 | 0 | 70 | 23 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-05-09 14:07 | 56.2 | 38.1 | 0 | 5.7 | -24 | 24 | 1017 | 1.64 | 24 | 141 | 25 | 33.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-05-09 14:06 | 62.2 | 39.6 | 0 | 0 | -34.6 | 34.6 | 1017 | 0.3 | 10.5 | 68 | 40 | 22.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-05-09 14:04 | 57.9 | 39.1 | 0 | 3 | -40.6 | 40.6 | 1017 | 0 | 1 | 6 | 80 | 24.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-05-09 14:03 | 61.5 | 39.5 | 0 | 0 | -2.3 | 2.3 | 1017 | 2.95 | 33.3 | 214 | 40 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-05-09 14:01 | 55 | 38.9 | 0 | 6.1 | -37.4 | 37.4 | 1017 | 1.98 | 42.7 | 246 | 99 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-05-09 13:57 | 53.2 | 38.9 | 0.6 | 7.3 | -6.1 | 6.1 | 1016 | 1.84 | 26 | 145 | 50 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-05-09 13:54 | 46.7 | 37.2 | 0.5 | 15.6 | -1.4 | 1.4 | 1016 | 3.79 | 8.5 | 42 | 10 | 16.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-05-09 13:53 | 49.9 | 39.1 | 0 | 11 | -1.5 | 1.5 | 1016 | 0.47 | 13 | 68 | 15 | 17.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-05-09 13:52 | 51.2 | 39.1 | 0 | 9.7 | -3.5 | 3.5 | 1016 | 2.17 | 28.2 | 151 | 25 | 19.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-05-09 13:50 | 49 | 38.4 | 0 | 12.6 | -2.7 | 2.7 | 1016 | 0.14 | 3.3 | 17 | 5 | 17.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-05-09 13:21 | 55.2 | 40.4 | 0 | 4.4 | -4.6 | 4.6 | 1016 | 13.03 | 31.5 | 182 | 40 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-05-09 13:20 | 0.2 | 0.2 | 17.7 | 81.9 | -13.5 | 13.5 | 1016 | -0.04 | 0 | 0 | 0 | 17.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-05-09 13:18 | 57.3 | 40.4 | 0 | 2.3 | -4.9 | 4.9 | 1016 | 10.54 | 28.6 | 172 | 25 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-05-09 13:17 | 46.5 | 38.1 | 0 | 15.4 | -0.1 | 0.1 | 1016 | 1.59 | 11.1 | 54 | 10 | 18.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-05-09 13:16 | 59.5 | 41.1 | 0.1 | 0 | -45.9 | 45.9 | 1016 | 0.09 | 9 | 56 | 70 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-05-09 13:14 | 44.1 | 38.3 | 0 | 17.6 | 0 | 0 | 1019 | 4.34 | 17.7 | 81 | 25 | 39.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-05-09 13:11 | 61 | 40.6 | 0 | 0 | -29.1 | 29.1 | 1019 | 0.33 | 1.2 | 8 | 25 | 19.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-05-09 13:09 | 60.6 | 38.1 | 0 | 1.3 | -3.4 | 3.4 | 1019 | 2.49 | 14.1 | 90 | 20 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-05-09 13:08 | 53.6 | 37.8 | 0 | 8.6 | -0.1 | 0.1 | 1019 | 5.67 | 5.3 | 30 | 10 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-05-09 13:07 | 60.5 | 40.4 | 0 | 0 | -2.9 | 2.9 | 1019 | 0.27 | 10 | 63 | 20 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-05-09 13:05 | 48.3 | 35.5 | 0 | 16.2 | -31.7 | 31.7 | 1019 | 0.59 | 6.6 | 33 | 20 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-05-09 13:04 | 50.4 | 36.1 | 0.5 | 13 | -21.6 | 21.6 | 1019 | 5.57 | 71.6 | 378 | 80 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-05-09 13:02 | 54.9 | 38.6 | 0.1 | 6.4 | -1.3 | 1.3 | 1019 | 12.84 | 31.6 | 182 | 50 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-05-09 13:00 | 60.6 | 40.5 | 0 | 0 | -35.4 | 35.4 | 1019 | 3.15 | 15.4 | 97 | 99 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-05-09 12:59 | 60.9 | 40 | 0 | 0 | -19.4 | 19.4 | 1019 | -0.01 | 0 | 0 | 25 | 15.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-05-09 12:57 | 52 | 35.4 | 2.4 | 10.2 | -13.1 | 13.1 | 1019 | 0.03 | 1.6 | 9 | 20 | 19.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-05-09 12:55 | 0.1 | 0.1 | 15.1 | 84.7 | 0.1 | -0.1 | 1019 | -0.17 | 0 | 0 | 0 | 18.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-05-09 12:54 | 54.6 | 37.9 | 0 | 7.5 | -3.6 | 3.6 | 1019 | 2.37 | 29.7 | 170 | 30 | 21 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-05-09 12:53 | 41.1 | 28.2 | 3.6 | 27.1 | -3.9 | 3.9 | 1019 | -0.05 | 0 | 0 | 0 | 20.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-05-09 12:50 | 2 | 5.1 | 15.5 | 77.4 | 0 | 0 | 1019 | -0.14 | 0 | 0 | 0 | 17.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-05-09 12:49 | 37.1 | 24.7 | 6.9 | 31.3 | -0.3 | 0.3 | 1019 | -0.13 | 0 | 0 | 0 | 20.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-05-09 12:48 | 61.1 | 37.9 | 0 | 1 | -11.5 | 11.5 | 1019 | 2.76 | 32.3 | 207 | 40 | 22.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-05-09 12:47 | 57.8 | 30.9 | 0 | 11.3 | -1.8 | 1.8 | 1019 | 0.14 | 1.7 | 10 | 5 | 20.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-05-09 12:45 | 43.5 | 25.9 | 4.4 | 26.2 | -0.3 | 0.3 | 1019 | -0.07 | 0 | 0 | 0 | 20.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-05-09 12:44 | 61.9 | 39.2 | 0 | 0 | -38.5 | 38.5 | 1019 | 0.72 | 16.3 | 105 | 99 | 22.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-04-20 12:48 | 53.7 | 39.1 | 0 | 7.2 | 0 | 0 | 1016 | 1.12 | 9.3 | 52 | 10 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-04-20 12:43 | 60.1 | 42 | 0 | 0 | -1.1 | 1.1 | 1016 | 0.87 | 17.8 | 112 | 22 | 27.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-04-20 12:41 | 60.2 | 41.5 | 0 | 0 | -0.5 | 0.5 | 1016 | 6.68 | 11.3 | 71 | 20 | 28.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-04-20 12:39 | 54.2 | 38.2 | 0.4 | 7.2 | -0.3 | 0.3 | 1016 | 8.56 | 6.5 | 37 | 10 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-04-20 12:38 | 49.2 | 39.5 | 0 | 11.3 | -0.5 | 0.5 | 1015 | 16.38 | 8.8 | 45 | 15 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-04-20 12:35 | 60 | 40.7 | 0 | 0 | -10.1 | 10.1 | 1015 | 7 | 50.5 | 318 | 55 | 27 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-04-20 12:32 | 60.1 | 41.1 | 0 | 0 | -1 | 1 | 1015 | 0.72 | 16 | 101 | 25 | 36 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-04-20 12:22 | 60.1 | 41.5 | 0 | 0 | -5.7 | 5.7 | 1015 | 9.77 | 27.8 | 175 | 45 | 25.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-04-20 12:20 | 58.7 | 42.2 | 0 | 0 | -2.2 | 2.2 | 1015 | 0.04 | 3.7 | 23 | 10 | 26.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-04-20 12:18 | 59 | 41 | 0 | 0 | -24.3 | 24.3 | 1015 | 13.75 | 69.3 | 429 | 80 | 34.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-04-20 12:16 | 57.4 | 42.1 | 0 | 0.5 | -20.6 | 20.6 | 1015 | 17.67 | 77.7 | 467 | 90 | 38.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-04-20 12:14 | 57.7 | 43.5 | 0 | 0 | -27 | 27 | 1015 | 10.81 | 60.7 | 367 | 99 | 35 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-04-20 12:12 | 59 | 42.1 | 0 | 0 | -21.7 | 21.7 | 1015 | 22.15 | 87.8 | 543 | 95 | 34.2 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-04-19 13:44 | 57.3 | 40.8 | 0 | 1.9 | -15.5 | 15.5 | 1017 | 13.3 | 31.4 | 188 | 55 | 38.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-04-19 13:39 | 62.8 | 39.2 | 0 | 0 | 0 | 0 | 1018 | 2.33 | 13.7 | 90 | 25 | 27.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-04-19 13:37 | 60.7 | 40.2 | 0 | 0 | -0.1 | 0.1 | 1017 | 2.32 | 13.4 | 85 | 25 | 36.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-04-19 13:35 | 61.3 | 39.7 | 0 | 0 | -37.9 | 37.9 | 1018 | 0.07 | 5.1 | 33 | 55 | 25.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-04-19 13:33 | 60.9 | 39.3 | 0 | 0 | -4.4 | 4.4 | 1017 | 5.24 | 20.5 | 131 | 25 | 25.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-04-19 13:27 | 57 | 38.3 | 0.1 | 4.6 | -3.1 | 3.1 | 1017 | 3.16 | 33.8 | 202 | 43 | 31.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-04-19 13:25 | 61.3 | 39.2 | 0 | 0 | -16.8 | 16.8 | 1017 | 4.77 | 68.4 | 439 | 80 | 27.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-04-19 13:22 | 60.3 | 40.5 | 0 | 0 | -1.3 | 1.3 | 1017 | 9.26 | 26.9 | 170 | 35 | 30.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-04-19 13:18 | 23.7 | 15.1 | 11 | 50.2 | -40.5 | 40.5 | 1017 | -0.08 | 0 | 0 | 50 | 27.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-04-19 13:16 | 59.1 | 41 | 0 | 0 | -0.4 | 0.4 | 1017 | 1.44 | 10.5 | 65 | 12 | 32.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-04-19 13:14 | 61.1 | 39.6 | 0 | 0 | -0.5 | 0.5 | 1017 | 0.04 | 1.8 | 11 | 12 | 30.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-04-19 13:11 | 58.2 | 39.9 | 0 | 1.9 | -0.8 | 0.8 | 1017 | 1.86 | 12.1 | 73 | 25 | 28.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-04-19 13:09 | 57 | 40 | 0.4 | 2.6 | -36.1 | 36.1 | 1017 | 2.64 | 13.9 | 83 | 50 | 38.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-04-19 13:04 | 59.6 | 39.3 | 0 | 1.1 | -21.8 | 21.8 | 1016 | 4.5 | 18.7 | 117 | 45 | 27 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-04-19 13:02 | 60.3 | 40 | 0 | 0 | 1 | -1 | 1016 | 0.28 | 10.2 | 64 | 25 | 29 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-04-19 12:58 | 57.3 | 40.5 | 0 | 2.2 | -2.8 | 2.8 | 1017 | 24.36 | 21.5 | 129 | 42 | 30.1 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-04-19 11:51 | 61.3 | 39.1 | 0 | 0 | -0.1 | 0.1 | 1019 | 0.81 | 7.9 | 51 | 50 | 34.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-04-19 11:49 | 60.9 | 39.4 | 0 | 0 | -17.7 | 17.7 | 1019 | 0 | 0 | 0 | 7 | 23.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-04-19 11:48 | 60 | 39.6 | 0 | 0.4 | -0.9 | 0.9 | 1018 | 9.24 | 27 | 169 | 50 | 30.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-04-19 11:42 | 50.1 | 36.7 | 0 | 13.2 | -0.1 | 0.1 | 1018 | 1.18 | 9.5 | 50 | 25 | 30.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-04-19 11:41 | 58.5 | 38.8 | 0 | 2.7 | -9.2 | 9.2 | 1017 | 17.79 | 37.1 | 227 | 53 | 33.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-04-19 11:37 | 45.4 | 34 | 1.9 | 18.7 | -2 | 2 | 1018 | 17.51 | 9 | 43 | 20 | 36.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-04-19 11:35 | 58.5 | 36 | 0 | 5.5 | -0.2 | 0.2 | 1018 | 0 | 1 | 6 | 5 | 24.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-04-19 11:33 | 45.7 | 36.6 | 0 | 17.7 | -1.2 | 1.2 | 1017 | 0.64 | 15 | 72 | 2 | 28.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-04-19 11:30 | 46.7 | 36.3 | 0 | 17 | -0.1 | 0.1 | 1017 | 2.54 | 13.9 | 68 | 25 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-04-19 11:29 | 61.8 | 39.8 | 0 | 0 | -30.3 | 30.3 | 1017 | 5.3 | 20.4 | 132 | 50 | 23.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-04-19 11:27 | 61 | 39.3 | 0.1 | 0 | -3.6 | 3.6 | 1019 | 2.43 | 48.8 | 311 | 53 | 31.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-04-19 10:36 | 59 | 40.8 | 0 | 0.2 | -0.1 | 0.1 | 1017 | -0.03 | 0 | 0 | 5 | 24.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-04-19 10:35 | 56 | 40.3 | 0 | 3.7 | -43.4 | 43.4 | 1017 | 1.33 | 34.5 | 202 | 57 | 37.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-04-19 10:32 | 27.2 | 28.6 | 0.6 | 43.6 | -1.7 | 1.7 | 1016 | 4.4 | 4.5 | 12 | 5 | 26 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-04-19 10:29 | 59.2 | 41.6 | 0 | 0 | 0 | 0 | 1016 | 0.77 | 7.8 | 48 | 7 | 24.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-04-19 10:27 | 42.2 | 35.4 | 0 | 22.4 | -3.1 | 3.1 | 1016 | 2.23 | 27.5 | 122 | 23 | 36.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-04-19 10:25 | 60.5 | 40.9 | 0 | 0 | -4.6 | 4.6 | 1016 | 13.62 | 32.8 | 208 | 55 | 27.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-04-19 10:23 | 59.4 | 41.4 | 0 | 0 | -20.1 | 20.1 | 1016 | 10.98 | 29.2 | 182 | 55 | 24.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-04-19 10:19 | 42.5 | 35.1 | 0 | 22.4 | -0.4 | 0.4 | 1016 | 0.81 | 16.9 | 75 | 18 | 27.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-04-19 10:18 | 63.8 | 40.2 | 0 | 0 | -3.4 | 3.4 | 1016 | 5.95 | 46.9 | 314 | 50 | 30.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-04-19 10:15 | 47.4 | 38.2 | 0 | 14.4 | -0.7 | 0.7 | 1016 | 17.21 | 2 | 9 | 5 | 23.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-04-19 10:13 | 63.9 | 40.2 | 0 | 0 | -3 | 3 | 1017 | 2.46 | 48.1 | 322 | 50 | 46.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-04-19 10:07 | 58.8 | 40.2 | 0 | 1 | -1 | 1 | 1017 | 5.76 | 21.4 | 132 | 30 | 24.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-04-19 09:58 | 41.3 | 33.6 | 0 | 25.1 | -1.9 | 1.9 | 1017 | 0.81 | 16.8 | 73 | 20 | 29.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-04-19 09:55 | 60.1 | 40.3 | 0 | 0 | -1.2 | 1.2 | 1017 | 0.66 | 15.7 | 98 | 25 | 22.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-04-19 09:52 | 52.3 | 38.3 | 0.3 | 9.1 | -0.2 | 0.2 | 1017 | 0.24 | 9.3 | 51 | 20 | 26.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-04-19 09:50 | 59.9 | 42 | 0 | 0 | 0.3 | -0.3 | 1017 | 0.14 | 3.3 | 20 | 12 | 23.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-04-19 09:48 | 53.6 | 38.5 | 0.4 | 7.5 | -0.2 | 0.2 | 1017 | 1.62 | 11.3 | 63 | 20 | 22.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-04-19 09:44 | 57.5 | 39 | 0.1 | 3.4 | -5.6 | 5.6 | 1018 | 16.28 | 35.7 | 215 | 50 | 29.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-04-19 09:40 | 56.4 | 38.5 | 0.3 | 4.8 | -3.3 | 3.3 | 1018 | 9.25 | 26.8 | 158 | 30 | 31.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-04-19 09:36 | 60.3 | 39.5 | 0.1 | 0.1 | -8.7 | 8.7 | 1018 | 13.85 | 33 | 208 | 40 | 29.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-04-18 09:57 | 63.4 | 39.6 | 0 | 0 | -4.1 | 4.1 | 1017 | 31.81 | 50.8 | 338 | 50 | 25.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-04-18 09:55 | 30.3 | 19.7 | 10.1 | 39.9 | -82.7 | 82.7 | 1017 | -0.11 | 0 | 0 | 99 | 21.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-04-18 09:53 | 63.4 | 39.7 | 0 | 0 | -6.3 | 6.3 | 1017 | 16.7 | 36.7 | 243 | 50 | 26.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-04-18 09:51 | 62.7 | 41.7 | 0.1 | 0 | -0.2 | 0.2 | 1016 | >>>> | 0 | 0 | 25 | 31.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A454 | 2017-04-18 09:41 | 38 | 74.3 | 0 | >>>> | -0.5 | 0.5 | 1016 | -0.02 | 0 | 0 | 3 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A452 | 2017-04-18 09:31 | 20.9 | 88.5 | 0.2 | 0 | -0.7 | 0.7 | 1016 | -0.01 | 0 | 0 | 2 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 3 - section A | BHW3A451 | 2017-04-18 09:24 | 16.3 | 72.9 | 0 | 10.8 | -13 | 13 | 1017 | -0.14 | 0 | 0 | 1 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-04-07 11:24 | 53.9 | 33.7 | 1.2 | 11.2 | -93.9 | 93.9 | 1015 | -0.12 | 0 | 0 | 50 | 25.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-04-07 11:23 | 53.7 | 35 | 0 | 11.3 | -90.5 | 90.5 | 1015 | 0.58 | 1.6 | 9 | 15 | 23.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-04-07 11:21 | 42.8 | 32.9 | 0 | 24.3 | -32.8 | 32.8 | 1015 | 1.11 | 9.1 | 41 | 15 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-04-07 11:20 | 50.1 | 35 | 0 | 14.9 | -8 | 8 | 1015 | 12.17 | 7.7 | 40 | 15 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-04-07 11:19 | 38.5 | 31.3 | 0.4 | 29.8 | -34 | 34 | 1015 | 0.41 | 5.5 | 22 | 10 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-04-07 11:17 | 18.3 | 15.6 | 9.8 | 56.3 | -1.3 | 1.3 | 1015 | 8.63 | 6.4 | 12 | 5 | 23.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-04-07 11:16 | 58 | 36.2 | 0 | 5.8 | -92.5 | 92.5 | 1015 | 1.96 | 3 | 18 | 99 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-04-07 11:14 | 6.1 | 4 | 15.9 | 74 | -3.2 | 3.2 | 1015 | 0 | 0 | 0 | 0 | 26.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-04-07 11:13 | 49.7 | 34.8 | 0 | 15.5 | -92.5 | 92.5 | 1015 | 0 | 0 | 0 | 40 | 25.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B011 | 2017-04-07 11:11 | 57 | 38.1 | 0 | 4.9 | 0.2 | -0.2 | 1015 | 0 | 0.3 | 2 | 3 | 25 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-04-07 11:09 | 49.7 | 35.9 | 0 | 14.4 | -92.5 | 92.5 | 1015 | 0.91 | 16.7 | 86 | 99 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-04-07 11:06 | 36.8 | 26.9 | 4.2 | 32.1 | -93.8 | 93.8 | 1015 | -0.11 | 0 | 0 | 25 | 26.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-04-07 11:04 | 0.8 | 0.5 | 15.4 | 83.3 | -10.7 | 10.7 | 1015 | -0.69 | 0 | 0 | 0 | 24.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-04-07 11:03 | 35.3 | 23.1 | 6.8 | 34.8 | 0.4 | -0.4 | 1015 | -0.03 | 0 | 0 | 0 | 24.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-04-07 11:02 | 52.8 | 36.1 | 0 | 11.1 | -22.2 | 22.2 | 1015 | 0.12 | 3 | 16 | 5 | 24.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-04-07 11:00 | 47 | 34.4 | 0 | 18.6 | -19.8 | 19.8 | 1015 | 4.6 | 18.8 | 92 | 10 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-04-07 10:58 | 0.2 | 0.1 | 17.4 | 82.3 | 0.1 | -0.1 | 1015 | 0.03 | 0 | 0 | 0 | 25.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-04-07 10:57 | 47.2 | 32.7 | 1.8 | 18.3 | -92 | 92 | 1015 | 0.08 | 2.3 | 11 | 5 | 25.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-04-07 10:55 | 60.9 | 39.2 | 0 | 0 | -94.8 | 94.8 | 1015 | 0.17 | 3.5 | 22 | 20 | 24.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-04-07 10:54 | 43.8 | 34.4 | 0 | 21.8 | -1.7 | 1.7 | 1015 | 1.34 | 10.1 | 46 | 15 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-04-07 10:53 | 50.5 | 35.6 | 0 | 13.9 | -28.8 | 28.8 | 1015 | 1.72 | 10.3 | 54 | 25 | 24.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-04-07 10:51 | 45.5 | 32.7 | 1.5 | 20.3 | -96 | 96 | 1015 | 0.18 | 3.1 | 15 | 40 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-04-07 10:50 | 56.8 | 36.8 | 0 | 6.4 | -94.4 | 94.4 | 1014 | 0.53 | 5.6 | 33 | 99 | 23.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-04-07 10:09 | 55.7 | 39 | 0 | 5.3 | -3.2 | 3.2 | 1016 | 7.06 | 23.6 | 137 | 50 | 25.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-04-07 10:07 | 60.6 | 41 | 0 | 0 | -7 | 7 | 1016 | -0.07 | 0 | 0 | 99 | 25 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-04-07 10:05 | 57.4 | 40.2 | 0 | 2.4 | -0.3 | 0.3 | 1016 | 0.24 | 9.5 | 57 | 20 | 24.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-04-07 10:03 | 53.8 | 37.5 | 1.6 | 7.1 | -2.6 | 2.6 | 1016 | 0.18 | 1.8 | 10 | 5 | 25.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-04-07 10:01 | 59.9 | 41.5 | 0 | 0 | -0.9 | 0.9 | 1016 | 1.8 | 11.8 | 74 | 20 | 32.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-04-07 10:00 | 61.9 | 39.9 | 0 | 0 | -39.6 | 39.6 | 1016 | 0.69 | 7.3 | 47 | 50 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-04-07 09:59 | 0.3 | 0.2 | 17.2 | 82.3 | -1.3 | 1.3 | 1016 | -0.11 | 0 | 0 | 0 | 22.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-04-07 09:57 | 62.1 | 40.1 | 0 | 0 | -0.6 | 0.6 | 1016 | 0.07 | 2.3 | 15 | 15 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-04-07 09:56 | 55.9 | 39.7 | 0 | 4.4 | -8.4 | 8.4 | 1016 | 1.19 | 20.5 | 120 | 40 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-04-07 09:55 | 57 | 39.8 | 0 | 3.2 | -1.3 | 1.3 | 1016 | 2.14 | 12.9 | 77 | 20 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-04-07 09:53 | 60.1 | 41.8 | 0 | 0 | -47.4 | 47.4 | 1016 | -0.18 | 0 | 0 | 99 | 23.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-04-07 09:52 | 57.9 | 40.4 | 0.6 | 1.1 | -36.1 | 36.1 | 1016 | 1.83 | 11.8 | 71 | 40 | 25.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-04-07 09:50 | 13.7 | 10.6 | 13.1 | 62.6 | 0 | 0 | 1016 | -0.06 | 0 | 0 | 0 | 21.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-04-07 09:49 | 0.1 | 0.1 | 18.1 | 81.7 | -1.3 | 1.3 | 1015 | -0.01 | 0 | 0 | 0 | 21.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-04-07 09:44 | 61.7 | 39.8 | 0 | 0 | -61.7 | 61.7 | 1015 | 0.56 | 13.9 | 90 | 99 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-04-07 09:43 | 53.2 | 37.4 | 0.2 | 9.2 | -47.3 | 47.3 | 1015 | 3.37 | 15.8 | 88 | 40 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-04-07 09:41 | 62.3 | 39.4 | 0 | 0 | -65 | 65 | 1015 | 1.08 | 9 | 59 | 99 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-04-07 09:40 | 57 | 39.7 | 0.6 | 2.7 | -1.2 | 1.2 | 1015 | 8.48 | 25.4 | 152 | 40 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-04-07 09:38 | 60.4 | 39.8 | 0 | 0 | -26.4 | 26.4 | 1015 | 5.29 | 20.3 | 128 | 50 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-04-07 09:37 | 53.5 | 37.2 | 1.3 | 8 | -7.2 | 7.2 | 1015 | 1.74 | 11.7 | 65 | 10 | 24.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-04-07 09:35 | 45 | 34.5 | 1.6 | 18.9 | -2.6 | 2.6 | 1015 | 1.4 | 10.4 | 49 | 10 | 25 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-04-07 09:32 | 61.8 | 40.7 | 0 | 0 | -2.1 | 2.1 | 1015 | 0.7 | 16.1 | 104 | 20 | 25.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-04-07 09:31 | 61.5 | 39.5 | 0 | 0 | -36.5 | 36.5 | 1015 | 1.12 | 20 | 129 | 40 | 28.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-04-07 09:29 | 58.6 | 39 | 0 | 2.4 | -1.2 | 1.2 | 1015 | 1.81 | 25.9 | 159 | 25 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-04-07 09:28 | 54.2 | 38.4 | 0 | 7.4 | -44.4 | 44.4 | 1015 | 3.52 | 56.7 | 322 | 99 | 33 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-04-07 09:27 | 55.6 | 37.9 | 0 | 6.5 | -22.8 | 22.8 | 1015 | 1.69 | 24.2 | 141 | 40 | 37 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-04-07 09:25 | 59.2 | 39.4 | 0 | 1.4 | -47 | 47 | 1014 | 0.55 | 13.8 | 86 | 80 | 28.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-04-07 09:24 | 49.3 | 38.2 | 0 | 12.5 | -6.8 | 6.8 | 1015 | 17.68 | 36.2 | 187 | 40 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-04-07 09:22 | 54 | 39.5 | 0.2 | 6.3 | -39.2 | 39.2 | 1014 | 0.4 | 11.7 | 66 | 80 | 27.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-04-07 08:49 | 53.8 | 36.3 | 0.6 | 9.3 | -1.9 | 1.9 | 1015 | 3.92 | 4.4 | 25 | 10 | 23.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-04-07 08:47 | 53.1 | 39.3 | 0 | 7.6 | -1.1 | 1.1 | 1015 | 0.41 | 2.7 | 15 | 20 | 28.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-04-07 08:46 | 37.3 | 29 | 3.6 | 30.1 | -0.2 | 0.2 | 1015 | 0.29 | 2.3 | 9 | 3 | 26.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-04-07 08:44 | 55.2 | 39.1 | 0 | 5.7 | -28 | 28 | 1015 | 16.78 | 76.4 | 442 | 99 | 32.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-04-07 08:43 | 57.1 | 39.3 | 0 | 3.6 | -3.8 | 3.8 | 1015 | 3.2 | 33.9 | 203 | 40 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-04-07 08:42 | 51.2 | 39 | 0 | 9.8 | -1.5 | 1.5 | 1015 | 2.63 | 13.9 | 75 | 25 | 38 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-04-07 08:40 | 56.4 | 38.8 | 0.1 | 4.7 | -2.8 | 2.8 | 1015 | 4.72 | 19.2 | 113 | 25 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-04-07 08:38 | 52.9 | 38.8 | 0.5 | 7.8 | -0.2 | 0.2 | 1015 | 2.08 | 12.6 | 70 | 10 | 30.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-04-07 08:36 | 61.3 | 40 | 0 | 0 | -16.5 | 16.5 | 1015 | 5.22 | 71.3 | 458 | 70 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-04-07 08:35 | 58.9 | 40.7 | 0 | 0.4 | -1.1 | 1.1 | 1015 | 9.99 | 27.8 | 171 | 20 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-04-07 08:33 | 54.2 | 37.5 | 0.4 | 7.9 | -4 | 4 | 1015 | 7.01 | 49.9 | 283 | 50 | 34.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-04-07 08:32 | 54.9 | 40.2 | 0 | 4.9 | -2.9 | 2.9 | 1015 | 2.97 | 32.4 | 186 | 30 | 33 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-04-07 08:30 | 56.9 | 37.5 | 0.8 | 4.8 | -2 | 2 | 1014 | 8.33 | 25.7 | 153 | 25 | 27.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-04-07 08:27 | 54.4 | 39.8 | 0 | 5.8 | 0 | 0 | 1014 | 1.71 | 5.7 | 32 | 15 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-04-07 08:26 | 52.8 | 40.2 | 0 | 7 | -2.2 | 2.2 | 1014 | 2.47 | 13.5 | 75 | 20 | 38.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-04-07 08:24 | 53.9 | 41.1 | 0 | 5 | -23.8 | 23.8 | 1014 | 18.54 | 128.2 | 724 | 90 | 43.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-04-07 08:23 | 45.7 | 38 | 0 | 16.3 | -2.5 | 2.5 | 1014 | 0.63 | 6.9 | 33 | 5 | 25.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-04-07 08:21 | 48.7 | 36.5 | 2.4 | 12.4 | -2 | 2 | 1014 | 1.39 | 22 | 112 | 15 | 33 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-04-07 08:19 | 51.5 | 39.9 | 0 | 8.6 | -3.3 | 3.3 | 1014 | 1.44 | 22.1 | 119 | 25 | 41 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-04-07 08:18 | 49.9 | 38.4 | 0 | 11.7 | -11 | 11 | 1014 | 13.27 | 67.2 | 351 | 50 | 38.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-04-07 08:16 | 61.5 | 43 | 0 | 0 | 0.4 | -0.4 | 1014 | 2.12 | 6.4 | 41 | 20 | 26.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-04-07 08:14 | 57 | 39.6 | 0 | 3.4 | -5.5 | 5.5 | 1014 | 17.08 | 36.4 | 218 | 50 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-04-07 08:13 | 52.3 | 39 | 0 | 8.7 | -28 | 28 | 1014 | 0.6 | 14.3 | 78 | 25 | 34.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-04-07 08:12 | 53.4 | 37.8 | 0.1 | 8.7 | -8.7 | 8.7 | 1014 | 4.56 | 41 | 229 | 40 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-04-07 08:10 | 40 | 31.5 | 2.6 | 25.9 | -0.5 | 0.5 | 1014 | 16.35 | 8.9 | 37 | 10 | 22.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-04-07 08:08 | 44.2 | 37.7 | 0 | 18.1 | -0.5 | 0.5 | 1013 | 20.45 | 9.7 | 45 | 12 | 36.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-04-06 15:00 | 51.1 | 35.5 | 0 | 13.4 | -0.6 | 0.6 | 1016 | 2.49 | 13.9 | 74 | 99 | 31.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-04-06 14:57 | 59.3 | 37.7 | 0 | 3 | 0 | 0 | 1016 | 0.17 | 3.6 | 22 | 25 | 32.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-04-06 14:55 | 56.4 | 37.5 | 0 | 6.1 | 0 | 0 | 1016 | -0.28 | 0 | 0 | 50 | 24.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-04-06 14:53 | 63.8 | 39.3 | 0 | 0 | 0 | 0 | 1016 | 1 | 8.8 | 59 | 50 | 36.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-04-06 14:50 | 60.5 | 37.8 | 0.3 | 1.4 | 0.1 | -0.1 | 1016 | 0.15 | 3.3 | 21 | 50 | 35.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-04-06 14:48 | 55 | 36.3 | 0.4 | 8.3 | 0 | 0 | 1016 | 0.24 | 4.3 | 24 | 50 | 40 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-04-06 14:46 | 59.9 | 38.2 | 0.8 | 1.1 | -0.1 | 0.1 | 1016 | 0.82 | 8 | 50 | 50 | 34.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-04-06 14:37 | 64.5 | 40.8 | 0 | 0 | 0.8 | -0.8 | 1016 | 2.22 | 28.3 | 192 | 99 | 38.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-04-06 14:36 | 63.9 | 41.2 | 0 | 0 | 1.1 | -1.1 | 1016 | 1.66 | 11.4 | 76 | 99 | 36 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-04-06 14:34 | 62.8 | 41.5 | 0 | 0 | 0.3 | -0.3 | 1016 | 2.56 | 14 | 92 | 99 | 39.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-04-06 14:33 | 62.7 | 41.7 | 0 | 0 | 1.9 | -1.9 | 1016 | 2.54 | 14 | 92 | 99 | 35.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-04-06 14:21 | 55 | 39.4 | 0 | 5.6 | -3.2 | 3.2 | 1014 | 17.24 | 36.1 | 208 | 50 | 36.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-04-06 14:20 | 55.9 | 40.6 | 0 | 3.5 | -1.3 | 1.3 | 1014 | 9.72 | 27.1 | 158 | 40 | 36.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-04-06 14:19 | 60.6 | 41.6 | 0 | 0 | -37.8 | 37.8 | 1014 | 0.25 | 9.2 | 58 | 99 | 32.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-04-06 14:17 | 58 | 40 | 0 | 2 | -20.1 | 20.1 | 1014 | 12.19 | 30.1 | 183 | 50 | 39.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-04-06 14:16 | 62 | 39.2 | 0 | 0 | -28.9 | 28.9 | 1014 | 13.26 | 67.6 | 439 | 99 | 44.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-04-06 14:14 | 54.9 | 39 | 0 | 6.1 | -22 | 22 | 1014 | 12.3 | 64.8 | 373 | 70 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-04-06 14:13 | 60.7 | 40.9 | 0 | 0 | -27.5 | 27.5 | 1014 | 14.09 | 113.3 | 720 | 99 | 43.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-04-06 14:12 | 52.8 | 37.5 | 0.2 | 9.5 | -1.9 | 1.9 | 1014 | 15.09 | 33.7 | 186 | 40 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-04-06 14:10 | 53.5 | 37.4 | 0.5 | 8.6 | -37.9 | 37.9 | 1014 | 0.08 | 2.5 | 14 | 99 | 34.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-04-06 14:00 | 55.7 | 38.2 | 0 | 6.1 | -0.1 | 0.1 | 1015 | 6.68 | 22.9 | 134 | 15 | 28 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-04-06 13:59 | 54.4 | 38.8 | 0 | 6.8 | -1.8 | 1.8 | 1015 | 15.43 | 34.3 | 195 | 40 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-04-06 13:57 | 60.1 | 37.8 | 0 | 2.1 | -31 | 31 | 1015 | 9.04 | 57.1 | 360 | 99 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-04-06 13:56 | 61.3 | 38.8 | 0 | 0 | 0 | 0 | 1015 | 2.45 | 13.9 | 89 | 15 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-04-06 13:55 | 58.6 | 39.5 | 0 | 1.9 | 0 | 0 | 1015 | 2.32 | 13.3 | 82 | 15 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-04-06 13:54 | 62 | 38.4 | 0.2 | 0 | -25.5 | 25.5 | 1015 | 10.02 | 28.1 | 183 | 99 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-04-06 13:52 | 63.6 | 39.5 | 0 | 0 | -37.9 | 37.9 | 1015 | 1.05 | 19.4 | 129 | 50 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-04-06 13:51 | 54.7 | 38.5 | 0 | 6.8 | -0.6 | 0.6 | 1015 | 3.71 | 16.8 | 96 | 20 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-04-06 13:49 | 60.7 | 38.4 | 0 | 0.9 | -3.6 | 3.6 | 1015 | 5.49 | 20.9 | 133 | 20 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-04-06 13:48 | 56.6 | 37.7 | 0 | 5.7 | -6.5 | 6.5 | 1015 | 13.81 | 70.3 | 417 | 50 | 35.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-04-06 13:46 | 55.3 | 37.2 | 0 | 7.5 | -4 | 4 | 1014 | 14.61 | 33.7 | 195 | 40 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-04-06 12:51 | 56.3 | 40.2 | 0 | 3.5 | -33.4 | 33.4 | 1015 | 12.74 | 106.9 | 631 | 99 | 41.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-04-06 12:49 | 60.2 | 41.8 | 0 | 0 | 3.8 | -3.8 | 1015 | -0.03 | 0 | 0 | 0 | 33.2 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-04-06 12:48 | 59.1 | 42.8 | 0 | 0 | -42.2 | 42.2 | 1015 | 0.93 | 8.2 | 50 | 99 | 38 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-04-06 12:47 | 1 | 0.6 | 17.8 | 80.6 | -0.6 | 0.6 | 1015 | -0.02 | 0 | 0 | 0 | 27.5 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-04-06 12:46 | 61 | 40.4 | 0 | 0 | -8.6 | 8.6 | 1015 | 5.08 | 42.9 | 274 | 50 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-04-06 12:44 | 51.2 | 38 | 0 | 10.8 | -1.3 | 1.3 | 1015 | 3.69 | 16.5 | 88 | 15 | 39.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-04-06 12:43 | 49.3 | 36.1 | 1.7 | 12.9 | -28.4 | 28.4 | 1013 | 0.1 | 5.8 | 30 | 20 | 30.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-04-06 12:42 | 58 | 40.2 | 0 | 1.8 | -37.8 | 37.8 | 1015 | 0.27 | 9.5 | 58 | 99 | 38.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-04-06 12:40 | 53.6 | 38.2 | 0 | 8.2 | -33.9 | 33.9 | 1015 | 9.4 | 91.8 | 516 | 99 | 41.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-04-06 12:39 | 54 | 40.1 | 0 | 5.9 | -0.6 | 0.6 | 1015 | 2.27 | 13.2 | 75 | 25 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-04-06 12:29 | 8.4 | 5.2 | 16.1 | 70.3 | -2 | 2 | 1014 | -0.09 | 0 | 0 | 0 | 29.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-04-06 12:28 | 0.3 | 0.1 | 17.8 | 81.8 | -18.5 | 18.5 | 1014 | -0.09 | 0 | 0 | 0 | 27.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-04-06 12:27 | 40.7 | 29.1 | 5.6 | 24.6 | -41.7 | 41.7 | 1014 | 0.21 | 3.9 | 16 | 99 | 30.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-04-06 12:26 | 59.6 | 41.1 | 0.2 | 0 | -37.8 | 37.8 | 1014 | 0.34 | 10.8 | 67 | 40 | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-04-06 12:24 | 4.9 | 3 | 16.8 | 75.3 | 0.1 | -0.1 | 1014 | -0.03 | 0 | 0 | 99 | 29 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-04-06 12:22 | 30.3 | 19.5 | 11.3 | 38.9 | -44.6 | 44.6 | 1014 | 0.04 | 1.6 | 5 | 99 | 27.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-04-06 12:21 | 58 | 40.6 | 0.2 | 1.2 | -1.9 | 1.9 | 1014 | 8.34 | 25.4 | 154 | 20 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-04-06 12:19 | 55.7 | 39.3 | 0.1 | 4.9 | -6.7 | 6.7 | 1014 | 1.87 | 26 | 151 | 25 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-04-06 12:17 | 60.4 | 41.2 | 0 | 0 | -5.6 | 5.6 | 1014 | 8.96 | 26.5 | 168 | 30 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-04-06 12:16 | 60.7 | 40.7 | 0 | 0 | -39.6 | 39.6 | 1014 | 3.55 | 56.7 | 360 | 99 | 40.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-04-06 12:14 | 62.9 | 40.9 | 0 | 0 | -0.2 | 0.2 | 1014 | 0.88 | 17.8 | 117 | 20 | 37 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-04-06 12:13 | 53 | 51 | 0 | 0 | -11.2 | 11.2 | 1013 | 1.44 | 21.6 | 120 | 25 | 34.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-04-06 12:11 | 59 | 42 | 0.1 | 0 | -1.1 | 1.1 | 1013 | 0.16 | 7.5 | 46 | 10 | 28.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-04-06 12:09 | 8.1 | 5.2 | 16.3 | 70.4 | -41.3 | 41.3 | 1013 | -0.13 | 0 | 0 | 99 | 27.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-04-06 12:08 | 60.4 | 40.9 | 0 | 0 | -21.9 | 21.9 | 1013 | 13.31 | 68 | 431 | 70 | 38.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-04-06 12:07 | 58.6 | 42.2 | 0 | 0 | -18.6 | 18.6 | 1013 | 16.54 | 75.4 | 462 | 80 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-04-06 12:05 | 58.2 | 43.9 | 0 | 0 | -24.9 | 24.9 | 1013 | 10.83 | 60.8 | 371 | 80 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-04-06 12:04 | 59.4 | 42.1 | 0 | 0 | -17.9 | 17.9 | 1013 | 18.68 | 80.9 | 504 | 80 | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-04-06 10:58 | 61.1 | 39.2 | 0.1 | 0 | -1.6 | 1.6 | 1016 | 0.98 | 4.3 | 28 | 99 | 32.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-04-06 10:56 | 60.8 | 39.4 | 0 | 0 | -0.4 | 0.4 | 1016 | 0.29 | 4.8 | 30 | 50 | 33.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-04-06 10:54 | 54.2 | 37.7 | 0 | 8.1 | -1.9 | 1.9 | 1016 | 1.11 | 19.5 | 110 | 99 | 46.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-04-06 10:46 | 61.5 | 38.7 | 0 | 0 | -31.7 | 31.7 | 1016 | 0.42 | 12.2 | 78 | 99 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-04-06 10:45 | 38.2 | 21.5 | 6.4 | 33.9 | -0.3 | 0.3 | 1016 | -0.2 | 0 | 0 | 0 | 25.7 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-04-06 10:43 | 53.9 | 35.6 | 0 | 10.5 | -10.4 | 10.4 | 1016 | 2.95 | 32.8 | 185 | 40 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-04-06 10:42 | 35 | 22.3 | 7.2 | 35.5 | -0.7 | 0.7 | 1016 | -0.17 | 0 | 0 | 0 | 24.8 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-04-06 10:40 | 52.2 | 35.8 | 0 | 12 | -2.5 | 2.5 | 1016 | -0.03 | 0 | 0 | 5 | 25.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-04-06 10:39 | 2.7 | 9.1 | 11.9 | 76.3 | 0 | 0 | 1015 | -0.14 | 0 | 0 | 0 | 24.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-04-06 10:37 | 61.5 | 39.2 | 0 | 0 | -17.9 | 17.9 | 1015 | 2.22 | 28.6 | 184 | 25 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-04-06 10:36 | 61.6 | 39.6 | 0 | 0 | -33.1 | 33.1 | 1016 | 4.54 | 18.4 | 119 | 99 | 38.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-04-06 10:34 | 58.6 | 38.8 | 0 | 2.6 | -0.6 | 0.6 | 1016 | 7.84 | 24.4 | 150 | 40 | 41.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-04-06 10:32 | 52.5 | 35.9 | 0.3 | 11.3 | -20.4 | 20.4 | 1015 | 6.16 | 75.2 | 414 | 80 | 41 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-04-06 10:30 | 42.8 | 33.2 | 0.4 | 23.6 | -15.8 | 15.8 | 1015 | 2.51 | 13.6 | 61 | 20 | 33.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-04-06 10:28 | 51 | 42.6 | 0.1 | 6.3 | -3.5 | 3.5 | 1015 | 2.79 | 14.3 | 76 | 25 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-04-06 10:27 | 50.7 | 45.4 | 0 | 3.9 | -27.8 | 27.8 | 1015 | 0.24 | 1 | 5 | 25 | 25.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-04-06 10:25 | 49.2 | 36.6 | 0 | 14.2 | -0.3 | 0.3 | 1015 | 0.15 | 1.6 | 8 | 5 | 25.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-04-06 10:23 | 37.1 | 40.2 | 0 | 22.7 | -7.4 | 7.4 | 1015 | -0.02 | 0 | 0 | 15 | 27.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-04-06 10:21 | 43 | 41.3 | 0.3 | 15.4 | -10.3 | 10.3 | 1015 | 0.66 | 14.9 | 67 | 25 | 26.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-04-06 10:20 | 41.1 | 40.2 | 0.2 | 18.5 | -0.1 | 0.1 | 1015 | 5.68 | 5.1 | 22 | 10 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-04-06 10:18 | 0 | 0 | 17.4 | 82.6 | 0 | 0 | 1015 | -0.11 | 0 | 0 | 0 | 25.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-04-06 10:16 | 47.1 | 40.2 | 0 | 12.7 | -4.2 | 4.2 | 1014 | 2.28 | 28.1 | 139 | 25 | 27.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-04-06 10:10 | 42.7 | 38.4 | 0 | 18.9 | 0.6 | -0.6 | 1014 | 0.96 | 8.4 | 37 | 10 | 28 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-04-06 10:06 | 35.6 | 29.9 | 0.2 | 34.3 | -0.4 | 0.4 | 1013 | 1.87 | 11.9 | 44 | 5 | 28 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2017-04-05 14:08 | 0.4 | 0.1 | 18.1 | 81.4 | -41.1 | 41.1 | 1014 | 0.01 | 1.8 | 0 | 0 | 27.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-04-05 14:07 | 61.6 | 41.5 | 0 | 0 | -40.8 | 40.8 | 1014 | 7.95 | 86.6 | 559 | 99 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2017-04-05 14:05 | 40.8 | 28.4 | 6.1 | 24.7 | -46.7 | 46.7 | 1014 | 0.01 | 1 | 4 | 99 | 28.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-04-05 14:04 | 61.2 | 40.6 | 0 | 0 | -44.7 | 44.7 | 1014 | -0.04 | 0 | 0 | 99 | 29.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-04-05 14:02 | 61.1 | 39.7 | 0 | 0 | 0 | 0 | 1014 | -0.02 | 0 | 0 | 0 | 28.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-04-05 14:01 | 50.2 | 36.9 | 0 | 12.9 | -1.5 | 1.5 | 1014 | 0.45 | 12.6 | 66 | 15 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-04-05 14:00 | 56.4 | 38.5 | 0.3 | 4.8 | -1 | 1 | 1015 | 5.93 | 21.2 | 125 | 25 | 39.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-04-05 13:58 | 60.9 | 40.6 | 0 | 0 | -46.3 | 46.3 | 1015 | 0.97 | 18 | 115 | 99 | 42.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2017-04-05 13:57 | 60.6 | 39.6 | 0 | 0 | -44.1 | 44.1 | 1015 | 0.03 | 1.4 | 9 | 99 | 35.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-04-05 13:56 | 61 | 40.4 | 0 | 0 | -46.6 | 46.6 | 1016 | 0.39 | 11.4 | 73 | 99 | 40.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-04-05 13:52 | 59.3 | 40.7 | 0 | 0 | 0 | 0 | 1016 | 0.57 | 6.6 | 41 | 8 | 31.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-04-05 13:50 | 53.6 | 39.6 | 0 | 6.8 | -27.2 | 27.2 | 1016 | 27.34 | 96.4 | 542 | 50 | 37.4 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-04-05 13:24 | 59.6 | 39.6 | 0 | 0.8 | 0.1 | -0.1 | 1017 | 0.39 | 5.5 | 34 | 8 | 30.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-04-05 13:19 | 57.9 | 38.3 | 0 | 3.8 | -9.2 | 9.2 | 1017 | 18.44 | 37.7 | 229 | 50 | 34.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-04-05 13:18 | 48 | 35.2 | 0.1 | 16.7 | -3.4 | 3.4 | 1017 | 2.29 | 28.1 | 141 | 40 | 39.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-04-05 13:16 | 50.5 | 35.6 | 0 | 13.9 | -4.8 | 4.8 | 1017 | 2.9 | 31.9 | 169 |  | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-04-05 13:15 | 58.6 | 37.7 | 0 | 3.7 | -70.6 | 70.6 | 1017 | 2 | 26.1 | 160 | 99 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-04-05 13:14 | 52.5 | 36.6 | 0 | 10.9 | -2.3 | 2.3 | 1017 | 5.49 | 20.9 | 115 | 25 | 23.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-04-05 13:13 | 56.4 | 38.1 | 0 | 5.5 | 0 | 0 | 1017 | 7.67 | 6.1 | 36 | 20 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-04-05 13:12 | 52.9 | 36.9 | 0 | 10.2 | -0.3 | 0.3 | 1017 | 1.94 | 6 | 33 |  | 34.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-04-05 13:10 | 50.2 | 35.8 | 0.2 | 13.8 | -0.6 | 0.6 | 1017 | 10.59 | 7.1 | 37 | 20 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-04-05 13:06 | 49 | 35.4 | 0 | 15.6 | -10.6 | 10.6 | 1017 | 12.86 | 66.4 | 341 | 50 | 41.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-04-05 13:05 | 49 | 34.9 | 0.2 | 15.9 | -40.9 | 40.9 | 1017 | 2.6 | 48.7 | 249 | 99 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-04-05 13:03 | 60.1 | 39.8 | 0 | 0.1 | 0.5 | -0.5 | 1017 | -0.04 | 0 | 0 | 20 | 35.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-04-05 13:01 | 51.4 | 36.5 | 0 | 12.1 | -3.2 | 3.2 | 1017 | 3.73 | 36.3 | 195 | 50 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-04-05 13:00 | 50.6 | 36.6 | 0 | 12.8 | -8.2 | 8.2 | 1017 | 3.32 | 34.2 | 181 | 50 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-04-05 12:59 | 46.8 | 33.3 | 0.5 | 19.4 | -0.2 | 0.2 | 1017 | 0.18 | 3.7 | 18 | 5 | 29.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-04-05 12:57 | 2.3 | 1.3 | 17.2 | 79.2 | 0 | 0 | 1017 | -0.03 | 0 | 0 | 0 | 30.3 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-04-05 12:55 | 62.7 | 37.9 | 0 | 0 | 0.8 | -0.8 | 1017 | -0.12 | 0 | 0 | 5 | 34.8 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-04-05 12:53 | 53 | 36.3 | 0.3 | 10.4 | -2.1 | 2.1 | 1017 | 4.74 | 18.9 | 105 | 50 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-04-05 12:52 | 55 | 38.3 | 0.2 | 6.5 | -8.3 | 8.3 | 1017 | 5.09 | 42.2 | 243 | 50 | 37.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-04-05 12:50 | 60.1 | 40.4 | 0 | 0 | 2.5 | -2.5 | 1017 | -0.04 | 0 | 0 | 20 | 31.6 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-04-05 12:48 | 51.2 | 36.8 | 0 | 12 | -0.9 | 0.9 | 1017 | 6.03 | 21.6 | 115 | 40 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-04-05 12:38 | 54 | 39.3 | 0.5 | 6.2 | -6.4 | 6.4 | 1016 | 4.86 | 18.9 | 107 | 40 | 40.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-04-05 12:36 | 2.4 | 2 | 17.1 | 78.5 | -51.9 | 51.9 | 1016 | -0.32 | 0 | 0 | 40 | 29.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-04-05 12:35 | 55.6 | 39.7 | 0 | 4.7 | -21.1 | 21.1 | 1016 | 15.01 | 33.7 | 196 | 50 | 30 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-04-05 12:33 | 60.3 | 40.9 | 0 | 0 | 0.3 | -0.3 | 1016 | -0.1 | 0 | 0 | 20 | 26.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-04-05 12:32 | 61.2 | 39.9 | 0 | 0 | -37.8 | 37.8 | 1016 | 2.14 | 12.8 | 82 | 50 | 26.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-04-05 12:31 | 56.2 | 38.4 | 0 | 5.4 | -4.1 | 4.1 | 1016 | 2.42 | 48.2 | 284 | 50 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-04-05 12:29 | 55.2 | 39.4 | 0 | 5.4 | -0.3 | 0.3 | 1016 | 1.13 | 9.3 | 54 | 20 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-04-05 12:28 | 51.7 | 35.9 | 1.1 | 11.3 | -4.7 | 4.7 | 1015 | 9.41 | 26.8 | 145 | 50 | 34.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-04-05 11:35 | 53.9 | 38.6 | 0.4 | 7.1 | -3.5 | 3.5 | 1016 | 2.13 | 26.8 | 151 | 50 | 48.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-04-05 11:31 | 59.3 | 40.8 | 0 | 0 | 0.3 | -0.3 | 1016 | 0.85 | 4 | 25 | 10 | 25.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-04-05 11:29 | 50.3 | 38.2 | 0 | 11.5 | -5.2 | 5.2 | 1016 | 0.22 | 8.9 | 46 | 20 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-04-05 11:28 | 51.8 | 38.4 | 0 | 9.8 | -2.8 | 2.8 | 1016 | 2.02 | 26.7 | 145 | 25 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-04-05 11:27 | 50.8 | 38.4 | 0 | 10.8 | -0.1 | 0.1 | 1016 | 0.11 | 2.9 | 15 | 5 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-04-05 11:21 | 56.5 | 39.8 | 0 | 3.7 | -4 | 4 | 1016 | 12.17 | 30.5 | 180 | 40 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-04-05 11:19 | 60.6 | 41.4 | 0 | 0 | -4.7 | 4.7 | 1016 | -0.05 | 0 | 0 | 5 | 25.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-04-05 11:17 | 57.4 | 40.4 | 0 | 2.2 | -2.5 | 2.5 | 1016 | 26.37 | 22.4 | 134 | 25 | 31.6 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-04-05 11:16 | 49.9 | 38.8 | 0 | 11.3 | -0.1 | 0.1 | 1016 | 1.66 | 11.2 | 58 | 10 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-04-05 11:15 | 56.9 | 39.5 | 0.7 | 2.9 | -46 | 46 | 1016 | 0.07 | 8.2 | 49 | 50 | 26.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-04-05 11:14 | 45 | 37.9 | 0 | 17.1 | -0.2 | 0.2 | 1015 | 4.29 | 17.5 | 82 | 20 | 43.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-04-05 11:10 | 61 | 41 | 0 | 0 | 0.9 | -0.9 | 1015 | -0.16 | 0 | 0 | 5 | 33.2 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-04-05 11:09 | 56 | 39.8 | 0 | 4.2 | -43.5 | 43.5 | 1015 | 0.85 | 27.6 | 162 | 70 | 37.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-04-05 11:08 | 49.7 | 36.8 | 0 | 13.5 | -0.9 | 0.9 | 1015 | 11.65 | 29.5 | 154 | 40 | 37.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-04-05 11:07 | 47.5 | 36.2 | 0 | 16.3 | -0.1 | 0.1 | 1015 | 0.54 | 13.8 | 68 | 15 | 33.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-04-05 11:05 | 53 | 39.2 | 0 | 7.8 | -1.5 | 1.5 | 1015 | 12.39 | 7.7 | 43 | 15 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-04-05 11:04 | 54.5 | 40.2 | 0 | 5.3 | -35.6 | 35.6 | 1015 | 7.95 | 23.6 | 135 | 50 | 48.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-04-05 11:03 | 51.8 | 39 | 0 | 9.2 | -7.2 | 7.2 | 1015 | 1.08 | 19.2 | 104 | 25 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-04-05 11:01 | 51.9 | 39.1 | 0 | 9 | -15.9 | 15.9 | 1015 | 14.31 | 32.1 | 174 | 40 | 44.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-04-05 11:00 | 55.4 | 39.7 | 0.9 | 4 | -7.1 | 7.1 | 1015 | 2.56 | 3.5 | 20 | 5 | 30.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-04-05 10:58 | 22.3 | 25.5 | 2 | 50.2 | -3.8 | 3.8 | 1015 | 30.25 | 11.7 | 27 | 5 | 34.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-04-05 10:46 | 56.2 | 39.5 | 0 | 4.3 | -42.3 | 42.3 | 1015 | -0.46 | 0 | 0 | 25 | 29.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-04-05 10:44 | 58.4 | 41.1 | 0 | 0.5 | 0.1 | -0.1 | 1015 | 0.45 | 5.9 | 36 | 10 | 26.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-04-05 10:43 | 41.4 | 35.4 | 0 | 23.2 | -3.7 | 3.7 | 1015 | 2.87 | 31.1 | 135 | 20 | 38.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-04-05 10:41 | 55.2 | 39.6 | 0 | 5.2 | -34.1 | 34.1 | 1015 | 9.14 | 90.4 | 523 | 90 | 42.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-04-05 10:40 | 60.4 | 40.9 | 0 | 0 | -4 | 4 | 1015 | 13.13 | 32.1 | 203 | 40 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-04-05 10:39 | 59.4 | 41.1 | 0 | 0 | -17.6 | 17.6 | 1015 | 10.48 | 28.5 | 177 | 40 | 26.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-04-05 10:38 | 47.5 | 35.2 | 0 | 17.3 | -0.2 | 0.2 | 1015 | 0.32 | 10.7 | 53 | 15 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-04-05 10:36 | 63.5 | 40.1 | 0 | 0 | -3 | 3 | 1015 | 5.26 | 44 | 293 | 40 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-04-05 10:35 | 54.6 | 38.9 | 0 | 6.5 | -17 | 17 | 1015 | 1.7 | 38.8 | 222 | 40 | 49.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-04-05 10:34 | 46.6 | 36.2 | 0.5 | 16.7 | -4 | 4 | 1014 | 5.66 | 43.7 | 213 | 40 | 43.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-04-05 10:32 | 50.5 | 37.3 | 0.1 | 12.1 | -1.2 | 1.2 | 1014 | 2.02 | 12.5 | 66 | 15 | 25 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-04-05 10:30 | 53.4 | 39.4 | 0 | 7.2 | 0 | 0 | 1014 | 2.05 | 12.3 | 69 | 20 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-04-05 10:29 | 56.4 | 41.8 | 0 | 1.8 | -24.5 | 24.5 | 1014 | 2.35 | 3.3 | 19 | 99 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-04-05 10:27 | 52.8 | 39.6 | 0 | 7.6 | -1.3 | 1.3 | 1014 | 13.52 | 31.2 | 172 | 25 | 49.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-04-05 10:26 | 63.7 | 39.9 | 0 | 0 | -2.6 | 2.6 | 1014 | 2.06 | 44 | 294 | 50 | 47.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-04-05 10:25 | 54.5 | 40.1 | 0 | 5.4 | -0.2 | 0.2 | 1014 | 7.92 | 12 | 68 | 20 | 41.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-04-05 10:24 | 53.6 | 38.5 | 0 | 7.9 | -1.2 | 1.2 | 1014 | 1.02 | 18.8 | 106 | 40 | 37.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-04-05 10:22 | 38.9 | 35.5 | 0.8 | 24.8 | -1.7 | 1.7 | 1014 | 31.81 | 2.6 | 10 | 5 | 26.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-04-05 09:12 | 57.3 | 39.9 | 0 | 2.8 | -1 | 1 | 1015 | 5.14 | 20.1 | 121 | 40 | 26.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-04-05 09:10 | 1.8 | 1.6 | 17 | 79.6 | 0 | 0 | 1015 | -0.28 | 0 | 0 |  | 23.5 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-04-05 09:09 | 30.1 | 20.8 | 9.4 | 39.7 | 0.4 | -0.4 | 1015 | -0.28 | 0 | 0 | 0 | 23 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-04-05 09:08 | 0.1 | 0.1 | 17.8 | 82 | 0 | 0 | 1015 | -0.27 | 0 | 0 | 0 | 24.1 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-04-05 09:06 | 50.9 | 39.7 | 0 | 9.4 | -71.1 | 71.1 | 1015 | 0.53 | 6 | 32 | 99 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-04-05 09:05 | 36.8 | 31.3 | 1.8 | 30.1 | -5.3 | 5.3 | 1015 | 2.47 | 29.1 | 112 | 25 | 33.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-04-05 09:03 | 51 | 37.4 | 0 | 11.6 | -25.9 | 25.9 | 1015 | 13.05 | 67.5 | 361 | 60 | 29.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-04-05 09:02 | 38.1 | 33 | 0 | 28.9 | -2.8 | 2.8 | 1015 | -0.07 | 0 | 0 | 20 | 24.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-04-05 09:00 | 49.9 | 39.1 | 0 | 11 | -0.7 | 0.7 | 1015 | 1.13 | 19.9 | 104 | 25 | 30.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-04-05 08:58 | 48.8 | 37.6 | 0 | 13.6 | -7.6 | 7.6 | 1015 | 2.13 | 27.4 | 140 | 40 | 28 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-04-05 08:57 | 58.1 | 40 | 0 | 1.9 | -1.8 | 1.8 | 1015 | 0.46 | 12.9 | 79 | 25 | 24.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-04-05 08:55 | 61.3 | 41.6 | 0 | 0 | 0.2 | -0.2 | 1015 | -0.07 | 0 | 0 | 18 | 25.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-04-05 08:53 | 53.4 | 39.3 | 0 | 7.3 | -0.7 | 0.7 | 1015 | 0.3 | 10.3 | 57 | 25 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-04-05 08:51 | 60.2 | 42.3 | 0 | 0 | 0.2 | -0.2 | 1015 | 0.23 | 4.2 | 26 | 8 | 25 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-04-05 08:49 | 61.4 | 41.5 | 0 | 0 | 0.2 | -0.2 | 1015 | 0.75 | 7.7 | 49 | 20 | 24 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-04-05 07:46 | 57.5 | 40.1 | 0 | 2.4 | -6.3 | 6.3 | 1014 | 15.24 | 34.4 | 207 | 40 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-04-05 07:44 | 50.3 | 39 | 0.1 | 10.6 | -15.3 | 15.3 | 1014 | 23.62 | 41.6 | 219 | 99 | 36.3 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-04-05 07:42 | 34.6 | 30.1 | 3.3 | 32 | -1.1 | 1.1 | 1014 | -0.23 | 0 | 0 | 15 | 19.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-04-05 07:40 | 46.4 | 36 | 1.1 | 16.5 | -0.4 | 0.4 | 1014 | -0.13 | 0 | 0 | 15 | 30.2 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-04-05 07:38 | 50.9 | 39.8 | 0.4 | 8.9 | -34.8 | 34.8 | 1014 | 4.3 | 37.4 | 199 | 50 | 43.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-04-05 07:33 | 49.4 | 36.3 | 1.9 | 12.4 | -4.7 | 4.7 | 1014 | 13.06 | 31.4 | 162 | 20 | 33.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-04-05 07:31 | 52.9 | 38.9 | 0 | 8.2 | -16.2 | 16.2 | 1014 | 11.21 | 29.1 | 161 | 40 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-04-05 07:28 | 60.3 | 41 | 0 | 0 | -8.5 | 8.5 | 1015 | 13.31 | 32.2 | 203 | 25 | 30.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-03-28 15:01 | 39.3 | 26.1 | 6.2 | 28.4 | -1.5 | 1.5 | 1005 | 0 | 0 | 0 | 99 | 29.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-03-28 14:57 | 59.6 | 40.8 | 0 | 0 | 0 | 0 | 1006 | 0.21 | 4 | 25 | 10 | 31.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-03-28 14:52 | 57.2 | 40.1 | 0 | 2.7 | -4.6 | 4.6 | 1007 | 12.69 | 30.9 | 185 | 45 | 39.3 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-03-28 14:48 | 58.4 | 38.5 | 0 | 3.1 | -17.1 | 17.1 | 1006 | 4.2 | 38.6 | 236 | 50 | 34.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-03-28 14:43 | 57.2 | 36.2 | 0.4 | 6.2 | -1.6 | 1.6 | 1006 | 4.46 | 4.7 | 28 | 10 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-03-28 14:42 | 58.9 | 38.3 | 0 | 2.8 | -2.4 | 2.4 | 1006 | 2.68 | 31.2 | 192 | 45 | 33 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-03-28 14:40 | 58.9 | 38.1 | 0 | 3 | -2.6 | 2.6 | 1006 | 4.69 | 19.2 | 119 | 22 | 30.3 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-03-28 14:37 | 61.6 | 38.8 | 0 | 0 | -13.2 | 13.2 | 1006 | 4.37 | 65.4 | 423 | 75 | 29.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-03-28 14:34 | 43.8 | 35.6 | 0 | 20.6 | -2.2 | 2.2 | 1006 | 1.51 | 10.7 | 49 | 10 | 28.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-03-28 14:32 | 58.8 | 38.3 | 0 | 2.9 | -4 | 4 | 1006 | 14.85 | 34.2 | 210 | 45 | 30.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-03-28 14:30 | 62.2 | 40.9 | 0 | 0 | 0.2 | -0.2 | 1006 | 3.57 | 4.2 | 27 | 15 | 27.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-03-28 14:28 | 59.6 | 42.6 | 0 | 0 | 0.3 | -0.3 | 1004 | 4.05 | 4.4 | 27 | 15 | 33.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-03-28 14:22 | 39.8 | 28.1 | 5.7 | 26.4 | -39.6 | 39.6 | 1004 | -0.31 | 0 | 0 | 20 | 30.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-03-28 14:20 | 60.4 | 41.3 | 0 | 0 | -3.3 | 3.3 | 1004 | 5.95 | 21.5 | 136 | 25 | 30.2 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-03-28 14:18 | 60.4 | 40.7 | 0 | 0 | -31.6 | 31.6 | 1004 | 2.13 | 44.1 | 279 | 99 | 41.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-03-28 14:16 | 61.8 | 40.7 | 0 | 0 | 0.5 | -0.5 | 1004 | 0.28 | 10 | 64 | 25 | 36.5 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-03-28 14:14 | 50.1 | 50.3 | 0 | 0 | -6.9 | 6.9 | 1004 | 1.15 | 19.3 | 101 | 0 | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-03-28 14:12 | 59.7 | 41.5 | 0.1 | 0 | -37 | 37 | 1004 | 0.26 | 9.5 | 59 | 42 | 34.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-03-28 14:09 | 60.1 | 40.8 | 0 | 0 | -18.8 | 18.8 | 1004 | 10.61 | 61.2 | 385 | 75 | 34.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-03-28 14:08 | 59.3 | 42 | 0 | 0 | -16.3 | 16.3 | 1004 | 16.59 | 76.3 | 474 | 80 | 34.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-03-28 13:43 | 60.1 | 37.7 | 0 | 2.2 | -1.7 | 1.7 | 1008 | 1.37 | 10.4 | 66 | 25 | 30.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-03-28 13:41 | 60.3 | 39.1 | 0 | 0.6 | -0.2 | 0.2 | 1007 | 0.17 | 3.6 | 23 | 50 | 35.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-03-28 13:37 | 57.5 | 38.7 | 0 | 3.8 | -2.3 | 2.3 | 1007 | 5.84 | 21 | 127 | 57 | 40.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-03-28 13:34 | 58.7 | 39.6 | 0 | 1.7 | -0.2 | 0.2 | 1007 | 0.08 | 5.4 | 33 | 17 | 42.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-03-28 13:31 | 55.4 | 37.7 | 1 | 5.9 | -1.8 | 1.8 | 1007 | 0.13 | 1.5 | 9 | 5 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-03-28 13:29 | 60 | 41 | 0 | 0 | 0.1 | -0.1 | 1006 | 0.72 | 7.4 | 47 | 18 | 34.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-03-28 13:27 | 57.5 | 39.8 | 0.4 | 2.3 | -35.9 | 35.9 | 1007 | 2.68 | 14 | 84 | 55 | 39.2 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-03-28 13:25 | 58.4 | 38.6 | 0.1 | 2.9 | -2.4 | 2.4 | 1005 | 0.44 | 12.7 | 78 | 22 | 30.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-03-28 13:16 | 61 | 38.5 | 0 | 0.5 | -28.6 | 28.6 | 1006 | 0.45 | 12.7 | 81 | 45 | 28.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-03-28 13:14 | 60.6 | 39.7 | 0 | 0 | -18.1 | 18.1 | 1005 | 0.08 | 5.4 | 34 | 18 | 26.7 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-03-28 13:12 | 60.1 | 39.1 | 0 | 0.8 | -23.2 | 23.2 | 1006 | 4.01 | 17.7 | 111 | 55 | 26.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-03-28 13:09 | 44.8 | 35.1 | 0.8 | 19.3 | -3 | 3 | 1005 | 2.29 | 13.2 | 62 | 15 | 26.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-03-28 13:05 | 52.4 | 38.2 | 0.7 | 8.7 | -5 | 5 | 1005 | 2.46 | 28.8 | 158 | 40 | 47.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-03-28 13:03 | 50 | 38 | 0 | 12 | -1.3 | 1.3 | 1005 | 0.43 | 12.4 | 65 | 15 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-03-28 13:02 | 51.4 | 38.5 | 0 | 10.1 | -3.1 | 3.1 | 1004 | 2.19 | 27.7 | 149 | 25 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-03-28 11:35 | 46.2 | 34.3 | 1.6 | 17.9 | -5.1 | 5.1 | 1005 | 15.42 | 33.6 | 163 | 25 | 42.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-03-28 11:32 | 60.8 | 40.7 | 0 | 0 | -44.9 | 44.9 | 1005 | 2.09 | 26.4 | 168 | 99 | 44.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-03-28 11:30 | 60.6 | 40.9 | 0 | 0 | -48.6 | 48.6 | 1005 | -0.08 | 0 | 0 | 99 | 34.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-03-28 11:28 | 63 | 41 | 0 | 0 | -47.9 | 47.9 | 1005 | -0.13 | 0 | 0 | 99 | 22.1 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-03-28 11:26 | 58.1 | 40.9 | 0 | 1 | -2 | 2 | 1005 | 19.92 | 19.4 | 118 | 45 | 31.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-03-28 11:23 | 47.5 | 38.3 | 0 | 14.2 | -0.1 | 0.1 | 1005 | 1.69 | 11.3 | 56 | 25 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-03-28 11:22 | 49.4 | 39.4 | 0 | 11.2 | 0.1 | -0.1 | 1006 | 4.38 | 17.8 | 92 | 25 | 43 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-03-28 11:17 | 41.8 | 32.7 | 2 | 23.5 | -1 | 1 | 1006 | 2.57 | 14 | 61 | 20 | 26.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-03-28 11:15 | 35.2 | 29.8 | 2.3 | 32.7 | -11.3 | 11.3 | 1006 | 7.01 | 48.7 | 180 | 40 | 35.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-03-28 11:11 | 54.7 | 38.3 | 0 | 7 | -0.1 | 0.1 | 1008 | -0.01 | 0 | 0 | 12 | 27 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-03-28 10:38 | 47.3 | 36.1 | 0 | 16.6 | -65.2 | 65.2 | 1007 | 4.12 | 36.7 | 182 | 99 | 33.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-03-28 10:37 | 30.7 | 29.9 | 0.1 | 39.3 | -0.9 | 0.9 | 1006 | 1.78 | 11.4 | 36 | 5 | 31.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-03-28 10:30 | 48.2 | 36.5 | 0.1 | 15.2 | -5.1 | 5.1 | 1006 | 4.54 | 39.7 | 200 | 40 | 36 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-03-28 10:28 | 25.4 | 26 | 1.7 | 46.9 | -2.8 | 2.8 | 1006 | 1.84 | 11.6 | 30 | 5 | 29.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-03-28 10:24 | 42.4 | 34.3 | 0.2 | 23.1 | -3 | 3 | 1005 | 12.65 | 30.8 | 137 | 20 | 30.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-03-28 10:19 | 53.2 | 39.2 | 1 | 6.6 | -50.5 | 50.5 | 1005 | -0.08 | 0 | 0 | 30 | 26.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-03-28 10:17 | 33.4 | 32.3 | 0.1 | 34.2 | 0.3 | -0.3 | 1004 | 0.99 | 8.5 | 30 | 5 | 28.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-03-28 10:12 | 11.6 | 9.3 | 12.8 | 66.3 | -34.8 | 34.8 | 1004 | 0.47 | 5.8 | 7 | 0 | 27.9 | Open/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-03-28 10:10 | 43.6 | 35 | 0 | 21.4 | -1.6 | 1.6 | 1004 | 16.53 | 34.9 | 159 | 35 | 37.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-03-28 10:07 | 40.5 | 34.1 | 0 | 25.4 | -0.5 | 0.5 | 1004 | 0.94 | 18 | 76 | 10 | 34.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-03-28 10:04 | 47.4 | 38.8 | 0.4 | 13.4 | -2.8 | 2.8 | 1006 | 12 | 7.5 | 37 | 15 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-03-27 07:52 | 58.7 | 42.3 | 0 | 0 | -39.6 | 39.6 | 994 | -0.38 | 0 | 0 | 20 | 28.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-03-27 07:49 | 47.5 | 36.5 | 0 | 16 | -4 | 4 | 994 | 3.55 | 34.8 | 173 | 25 | 39.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-03-27 07:47 | 60.7 | 41.3 | 0 | 0 | -2.4 | 2.4 | 994 | 9.67 | 27.5 | 175 | 45 | 29.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-03-27 07:44 | 45.7 | 36.6 | 0 | 17.7 | 0 | 0 | 994 | 0.63 | 14.9 | 71 | 15 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-03-27 07:43 | 63.3 | 40.5 | 0 | 0 | 3.3 | -3.3 | 994 | 0.26 | 9.8 | 65 | 40 | 27.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-03-27 07:40 | 61.1 | 41.8 | 0 | 0 | 0.3 | -0.3 | 994 | 6.38 | 21.7 | 139 | 30 | 49.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-03-27 07:38 | 65.3 | 40.4 | 0 | 0 | 3.8 | -3.8 | 997 | 0.2 | 14 | 96 | 40 | 41.6 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-03-22 16:27 | 51.2 | 36.9 | 0 | 11.9 | -0.2 | 0.2 | 1009 | 1.437 | 10.5 |  | 99 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-03-22 16:25 | 57.8 | 38.4 | 0 | 3.8 | 0.2 | -0.2 | 1009 | -0.022 | 0 |  | 20 | 27.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-03-22 16:22 | 63.9 | 40 | 0 | 0 | -0.1 | 0.1 | 1008 | 1.117 | 10.1 |  | 40 | 32.1 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-03-22 16:19 | 58.8 | 38 | 0.1 | 3.1 | -0.4 | 0.4 | 1009 | 1.161 | 9.1 |  | 40 | 31.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-03-22 16:17 | 53.4 | 36.4 | 0.4 | 9.8 | 0.2 | -0.2 | 1008 | 1.265 | 9.4 |  | 40 | 38 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-03-22 16:15 | 61.3 | 38.9 | 0.2 | 0 | -0.2 | 0.2 | 1008 | 0.8 | 7.5 |  | 40 | 31.9 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-03-22 16:10 | 65.2 | 41.8 | 0.1 | 0 | 0.2 | -0.2 | 1008 | -2.455 | 0 |  | 99 | 26.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-03-22 16:09 | 64.6 | 42.2 | 0 | 0 | -1.1 | 1.1 | 1008 | 2.458 | 13.1 |  | 99 | 24.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-03-22 16:08 | 62.6 | 42.6 | 0 | 0 | 0.8 | -0.8 | 1008 | 1.728 | 11.9 |  | 70 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-03-22 16:06 | 62.6 | 42.5 | 0 | 0 | 1.7 | -1.7 | 1008 | 6.282 | 22.6 |  | 99 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-03-22 15:15 | 58.4 | 41.9 | 0 | 0 | -11.1 | 11.1 | 1007 | 0.29 | 10.3 | 63.6 | 5 | 20 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-03-22 15:13 | 55.7 | 39.4 | 0 | 4.9 | -6.5 | 6.5 | 1006 | 2.32 | 29.5 | 172.4 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-03-22 15:11 | 59 | 42.4 | 0 | 0 | -6.7 | 6.7 | 1006 | 3.5 | 16.7 | 103.8 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-03-22 15:09 | 57.9 | 42.3 | 0 | 0 | -4.8 | 4.8 | 1007 | 6.77 | 23.3 | 141.6 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-03-22 15:07 | 60 | 41.8 | 0 | 0 | -36.8 | 36.8 | 1007 | 2.81 | 52.3 | 329.4 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-03-22 15:05 | 58.5 | 40.3 | 0 | 1.2 | 0.2 | -0.2 | 1006 | 0.48 | 13.5 | 83 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-03-22 15:04 | 36.3 | 49.3 | 0 | 14.4 | -4.5 | 4.5 | 1007 | 1.77 | 24.1 | 92 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-03-22 15:02 | 59.7 | 41.6 | 0 | 0 | -39.6 | 39.6 | 1006 | 3.61 | 36.2 | 227.1 | 99 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-03-22 15:00 | 40.8 | 29.5 | 5.5 | 24.2 | -45.4 | 45.4 | 1006 | 0.5 | 6.1 | 26.5 | 99 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-03-22 14:58 | 43.5 | 33.4 | 4.3 | 18.8 | -42.4 | 42.4 | 1006 | 0.24 | 4.2 | 19.3 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-03-22 14:55 | 57.9 | 42.7 | 0 | 0 | -35.7 | 35.7 | 1006 | 0.48 | 13.1 | 79.7 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-03-22 14:54 | 9.4 | 6.6 | 17.8 | 66.2 | -42.7 | 42.7 | 1006 | -0.58 | 0 | 0 | 99 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-03-22 14:51 | 56.1 | 40.6 | 0 | 3.3 | -2.2 | 2.2 | 1006 | 9 | 26.9 | 158.5 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-03-22 14:48 | 57.6 | 40.1 | 0 | 2.3 | -23.5 | 23.5 | 1007 | 13.33 | 70.2 | 423.9 | 80 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-03-22 14:44 | 54.7 | 42.4 | 0 | 2.9 | -22 | 22 | 1006 | 14.23 | 71.7 | 411 | 70 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-03-22 14:43 | 55.1 | 44.4 | 0 | 0.5 | -25.7 | 25.7 | 1006 | 13.03 | 68.1 | 393.4 | 70 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-03-22 14:41 | 57 | 42.2 | 0 | 0.8 | -17.2 | 17.2 | 1007 | 17.76 | 80.7 | 482.9 | 80 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-03-22 14:34 | 55.3 | 38.9 | 0 | 5.8 | -7 | 7 | 1008 | 17.43 | 37.5 | 217.3 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-03-22 14:32 | 48.4 | 36.8 | 0 | 14.8 | -15.2 | 15.2 | 1007 | -24.54 | 56.8 | 288.2 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-03-22 14:30 | 34.9 | 30.5 | 2.5 | 32.1 | -0.8 | 0.8 | 1008 | 0.14 | 3.3 | 12.1 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-03-22 14:28 | 59.5 | 39.7 | 0 | 0.8 | 0.1 | -0.1 | 1007 | 0.12 | 1.5 | 9.6 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-03-22 14:26 | 51.6 | 39.8 | 0.1 | 8.5 | -29.2 | 29.2 | 1009 | 5.92 | 46.1 | 249.4 | 50 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-03-22 14:25 | 61.8 | 40.1 | 0 | 0 | -3.1 | 3.1 | 1008 | 2.24 | 6.6 | 42 | 99 | 27.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-03-22 14:22 | 61.5 | 40.6 | 0 | 0 | -0.7 | 0.7 | 1008 | 0.38 | 5.4 | 35 | 40 | 28.8 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-03-22 14:20 | 53.4 | 38.4 | 0 | 8.2 | -1.9 | 1.9 | 1007 | 1.34 | 21.4 | 120 | 99 | 44.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-03-22 14:17 | 61.8 | 40 | 0 | 0 | -33.7 | 33.7 | 1008 | 2.95 | 32.4 | 210 | 99 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-03-22 14:15 | 6.9 | 4 | 16 | 73.1 | -0.3 | 0.3 | 1008 | -0.2 | 0 | 0 | 0 | 23.4 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-03-22 14:14 | 52.9 | 36.6 | 0 | 10.5 | -10.4 | 10.4 | 1008 | 3.2 | 33.9 | 188 | 40 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2017-03-22 14:13 | 43.5 | 34.4 | 3.8 | 18.3 | 0.3 | -0.3 | 1006 | -0.18 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-03-22 14:13 | 20.1 | 13.2 | 13.3 | 53.4 | -0.9 | 0.9 | 1008 | 0.52 | 6.3 | 13 | 0 | 18.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-03-22 14:11 | 59.5 | 43.1 | 0 | 0 | -42.3 | 42.3 | 1007 | 9.41 | 95 | 592.5 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-03-22 14:11 | 48.2 | 34.6 | 0.8 | 16.4 | -7.7 | 7.7 | 1008 | 1.55 | 5.4 | 27 | 3 | 22.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2017-03-22 14:09 | 29.7 | 22.4 | 10.4 | 37.5 | -49.3 | 49.3 | 1006 | 0.08 | 2.4 | 7.4 | 99 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-03-22 14:09 | 0.7 | 2.9 | 17 | 79.4 | 0 | 0 | 1008 | -0.02 | 0 | 0 | 0 | 18.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-03-22 14:08 | 64.9 | 41.7 | 0 | 0 | -50.8 | 50.8 | 1007 | 0.38 | 11.8 | 80.2 | 90 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-03-22 14:07 | 22.1 | 23 | 5.8 | 49.1 | 0.4 | -0.4 | 1007 | -0.47 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-03-22 14:07 | 61.9 | 40.6 | 0 | 0 | -22.8 | 22.8 | 1008 | 0.67 | 15.6 | 101 | 25 | 23.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-03-22 14:06 | 61.9 | 41.1 | 0 | 0 | -33.4 | 33.4 | 1008 | 7.07 | 22.9 | 148 | 99 | 39.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-03-22 14:05 | 50 | 37.4 | 0 | 12.6 | -1.4 | 1.4 | 1007 | 0.62 | 15.2 | 79.6 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-03-22 14:05 | 58.3 | 40.2 | 0 | 1.5 | -1 | 1 | 1008 | 8.76 | 26 | 158 | 40 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-03-22 14:03 | 45.2 | 35.5 | 1.5 | 17.8 | -4.9 | 4.9 | 1006 | 16.41 | 37.1 | 176.1 | 50 | 0 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-03-22 14:03 | 52 | 37.2 | 0.2 | 10.6 | -21.6 | 21.6 | 1008 | 5.34 | 69.4 | 378 | 90 | 42.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-03-22 14:02 | 59.4 | 41.1 | 0 | 0 | -49 | 49 | 1007 | 1.34 | 22 | 137 | 70 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-03-22 14:02 | 43.6 | 35.1 | 0 | 21.3 | -9.9 | 9.9 | 1007 | 6.25 | 21.4 | 97 | 25 | 36.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2017-03-22 14:00 | 40.2 | 29.7 | 6 | 24.1 | -47.6 | 47.6 | 1007 | -0.24 | 0 | 0 | 99 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-03-22 14:00 | 61.5 | 39.2 | 0 | 0 | -2.3 | 2.3 | 1008 | 1.61 | 11.3 | 73 | 15 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-03-22 13:58 | 58.4 | 40.8 | 0 | 0.8 | -41.8 | 41.8 | 1007 | 3.19 | 34 | 208.3 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-03-22 13:58 | 61.2 | 41.2 | 0 | 0 | -23.8 | 23.8 | 1007 | 0.4 | 1.3 | 8 | 40 | 26.8 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-03-22 13:57 | 50.8 | 31.8 | 0 | 17.4 | -1.5 | 1.5 | 1008 | 0.18 | 1.9 | 10 | 5 | 21.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-03-22 13:55 | 55.1 | 39.3 | 0 | 5.6 | -8.5 | 8.5 | 1008 | 0.02 | 1.3 | 7 | 10 | 23.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-03-22 13:54 | 58.3 | 41.3 | 0 | 0.4 | -16 | 16 | 1007 | 0.33 | 18 | 110.2 | 15 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-03-22 13:52 | 57.5 | 42 | 0 | 0.5 | -0.2 | 0.2 | 1007 | 1.3 | 10.2 | 61.6 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-03-22 13:52 | 58.7 | 39.2 | 0.3 | 1.8 | -8.1 | 8.1 | 1008 | 0.19 | 8.3 | 51 | 20 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-03-22 13:50 | 44.1 | 34.9 | 0 | 21 | -4.8 | 4.8 | 1007 | 4.27 | 39.5 | 182.9 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-03-22 13:50 | 53.2 | 38.2 | 0.1 | 8.5 | -0.4 | 0.4 | 1007 | 6.28 | 5.5 | 31 | 10 | 26.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-03-22 13:48 | 53.9 | 39.8 | 0.1 | 6.2 | -41 | 41 | 1006 | 8.46 | 90 | 508.6 | 80 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-03-22 13:48 | 8.3 | 5.1 | 16.7 | 69.9 | -0.2 | 0.2 | 1007 | -0.07 | 0 | 0 | 0 | 22.2 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-03-22 13:47 | 54.9 | 38.4 | 0.1 | 6.6 | -4 | 4 | 1007 | 2.84 | 32.1 | 185 | 40 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-03-22 13:46 | 58 | 40.7 | 0 | 1.3 | -3.9 | 3.9 | 1007 | 11.03 | 29.9 | 181.7 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-03-22 13:45 | 55.7 | 41.1 | 0.1 | 3.1 | -19.9 | 19.9 | 1007 | 11.97 | 30.7 | 179.2 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-03-22 13:43 | 34.5 | 34.2 | 0 | 31.3 | 0 | 0 | 1007 | 1.27 | 21.2 | 76.9 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-03-22 13:40 | 59.5 | 39 | 0 | 1.5 | 2.6 | -2.6 | 1006 | 0.92 | 18.8 | 117.5 | 5 | 20 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-03-22 13:37 | 56.7 | 40 | 0 | 3.3 | -22.1 | 22.1 | 1007 | 2.46 | 49.2 | 292.8 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-03-22 13:31 | 58.6 | 40.3 | 0 | 1.1 | -3.7 | 3.7 | 1007 | 22.42 | 92.1 | 566.4 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-03-22 13:31 | 58.8 | 39.6 | 0.5 | 1.1 | -2.4 | 2.4 | 1007 | 0.45 | 6 | 37 | 99 | 19.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-03-22 13:29 | 54.7 | 37.5 | 0 | 7.8 | -1.7 | 1.7 | 1007 | 18.49 | 38.8 | 222.5 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-03-22 13:28 | 59.6 | 40.8 | 0 | 0 | -0.2 | 0.2 | 1007 | 0.18 | 8.1 | 51 | 20 | 20.4 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-03-22 13:27 | 49.3 | 38.4 | 0 | 12.3 | -0.4 | 0.4 | 1006 | 19.1 | 38.9 | 201.5 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-03-22 13:26 | 57.4 | 41.7 | 0 | 0.9 | -31.6 | 31.6 | 1007 | -4.76 | 0 | 0 | 99 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-03-22 13:26 | 58.5 | 40.1 | 0 | 1.4 | -2.8 | 2.8 | 1007 | 7.12 | 23.2 | 142 | 40 | 38.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-03-22 13:24 | 59.3 | 42.2 | 0 | 0 | 0.1 | -0.1 | 1007 | 7.83 | 25.2 | 156.8 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-03-22 13:22 | 60 | 40.7 | 0 | 0 | 3.4 | -3.4 | 1007 | 1.91 | 44.2 | 278 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-03-22 13:22 | 57.6 | 41.1 | 0 | 1.3 | 0.05 | -0.1 | 1009.8 | 0.16 | 3.4 |  | 20 | 29.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-03-22 13:20 | 54.7 | 40.4 | 0 | 4.9 | -0.5 | 0.5 | 1007 | 9.99 | 14 | 80.5 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-03-22 13:20 | 53.9 | 40.3 | 0 | 5.8 | -25.55 | 25.6 | 1009.9 | 35.26 | 104.5 |  | 70 | 36.5 | Orifice Plate Change RequiredSurging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-03-22 13:20 | 61.1 | 41.6 | 0 | 0 | -2 | 2 | 1007 | 0.41 | 2.8 | 18 | 5 | 19.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-03-22 13:18 | 50.2 | 38.5 | 0 | 11.3 | -1 | 1 | 1006 | 1.77 | 25.5 | 134.5 |  | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-03-22 13:18 | 60.9 | 42.1 | 0 | 0 | 0.6 | -0.6 | 1007 | 1.83 | 12 | 76 | 20 | 28.6 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-03-22 13:17 | 62.3 | 40.2 | 0 | 0 | -40.9 | 40.9 | 1007 | 0.12 | 3 | 19 | 40 | 26.7 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-03-22 13:16 | 57.4 | 43.5 | 0 | 0 | -0.9 | 0.9 | 1006 | -28.22 | 3 | 18 | 10 | 20 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-03-22 13:15 | 0.1 | 0.1 | 17.9 | 81.9 | -4 | 4 | 1007 | -0.62 | 0 | 0 | 5 | 17.5 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-03-22 13:14 | 62.4 | 40.5 | 0 | 0 | -0.5 | 0.5 | 1007 | -0.05 | 0 | 0 | 20 | 20.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-03-22 13:12 | 56.8 | 40.1 | 0 | 3.1 | -7.9 | 7.9 | 1007 | 1.21 | 20.6 | 123 | 40 | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-03-22 13:11 | 57.5 | 40.2 | 0 | 2.3 | -1.1 | 1.1 | 1007 | 2.1 | 12.8 | 77 | 15 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-03-22 13:09 | 60 | 41.8 | 0 | 0 | -40.5 | 40.5 | 1007 | -0.07 | 0 | 0 | 99 | 25.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-03-22 13:08 | 59.9 | 41.7 | 0 | 0 | -37.3 | 37.3 | 1007 | 1.75 | 11.3 | 71 | 40 | 38.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-03-22 13:06 | 20 | 15.7 | 10.4 | 53.9 | -0.6 | 0.6 | 1007 | -0.13 | 0 | 0 | 0 | 22.9 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-03-22 13:05 | 60.7 | 40 | 0 | 0 | -2.3 | 2.3 | 1007 | 0.31 | 10.7 | 68 | 15 | 29 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-03-22 11:39 | 58.9 | 41.5 | 0 | 0 | -17.4 | 17.4 | 1007 | 1.17 | 9.6 | 59.7 | 5 | 20 | Shut/Open
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-03-22 11:37 | 51.9 | 38.9 | 0.2 | 9 | -48.5 | 48.5 | 1007 | 3.7 | 59.2 | 322 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-03-22 11:35 | 42.5 | 35.2 | 0 | 22.3 | -2.3 | 2.3 | 1007 | 17.64 | 37.2 | 165.7 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-03-22 11:34 | 40.3 | 34.2 | 0 | 25.5 | -0.8 | 0.8 | 1007 | 3.18 | 34 | 143.6 | 30 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-03-22 11:32 | 57 | 41.8 | 0 | 1.2 | -1.3 | 1.3 | 1007 | 11.98 | 7.8 | 46.6 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-03-22 11:30 | 48.3 | 39.1 | 0 | 12.6 | -36.5 | 36.5 | 1007 | 8.5 | 25.4 | 128.6 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-03-22 11:29 | 49.4 | 39.6 | 0 | 11 | -8.3 | 8.3 | 1006 | 1.66 | 24.6 | 127.3 | 20 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-03-22 11:27 | 49.5 | 38.3 | 0 | 12.2 | -17 | 17 | 1006 | 15.97 | 35.3 | 183.5 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-03-22 11:26 | 50.6 | 38.9 | 1.6 | 8.9 | -8 | 8 | 1007 | 2.78 | 3.7 | 19.7 | 10 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-03-22 11:23 | 46.7 | 37.6 | 0 | 15.7 | -3.8 | 3.8 | 1007 | 27.37 | 11.6 | 57 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-03-22 11:23 | 51.4 | 40.5 | 0.3 | 7.8 | -0.06 | 0.1 | 1009.9 | 0.05 | 4.1 |  | 20 | 25.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-03-22 11:23 | 54.2 | 40.4 | 0 | 5.4 | -3.5 | 3.5 | 1007 | 16.3 | 35 | 198 | 40 | 35.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-03-22 11:22 | 53.1 | 40.9 | 0 | 6 | -1.8 | 1.8 | 1007 | 10.41 | 60.2 | 335 | 40 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-03-22 11:21 | 46.5 | 38.4 | 1.3 | 13.8 | -1.44 | 1.4 | 1009.9 | 0.39 | 11.3 |  | 40 | 32.5 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-03-22 11:21 | 53.1 | 40.9 | 0 | 6 | -1.8 | 1.8 | 1007 | 10.41 | 60.2 | 335 | 40 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-03-22 11:20 | 60.9 | 42.6 | 0 | 0 | -39.9 | 39.9 | 1006 | -0.02 | 0 | 0 | 99 | 27.8 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-03-22 11:19 | 57.3 | 41.3 | 0 | 1.4 | -0.07 | 0.1 | 1009.8 | 0.2 | 3.9 |  | 20 | 25.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-03-22 11:18 | 43.6 | 36 | 0 | 20.4 | -13.7 | 13.7 | 1009 | 14.32 | 71.8 | 328.2 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-03-22 11:18 | 36.6 | 35.3 | 3 | 25.1 | -1.44 | 1.4 | 1009.9 | 2.8 | 14.4 |  | 30 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-03-22 11:18 | 57.5 | 41 | 0 | 1.5 | -12.3 | 12.3 | 1007 | 11.48 | 29.3 | 176 | 50 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-03-22 11:16 | 44.4 | 36.1 | 0.1 | 19.4 | -49.3 | 49.3 | 1008 | 4.08 | 61.6 | 286.9 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-03-22 11:16 | 62.8 | 42.6 | 0 | 0 | -23.4 | 23.4 | 1007 | 14.68 | 70.8 | 466 | 99 | 44.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-03-22 11:15 | 52.9 | 40.2 | 0 | 6.9 | -2.19 | 2.2 | 1009.9 | 4.98 | 19.3 |  | 30 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K093 | 2017-03-22 11:14 | 49.9 | 37 | 1.4 | 11.7 | -0.6 | 0.6 | 1008 | -1.38 | 0 | 0 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-03-22 11:14 | 54.5 | 39.9 | 0 | 5.6 | -22.1 | 22.1 | 1006 | 13.23 | 66.9 | 382 | 70 | 40.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-03-22 11:13 | 60.6 | 41.7 | 0 | 0 | -32.4 | 32.4 | 1007 | 14.28 | 113.3 | 719 | 99 | 44.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-03-22 11:12 | 51.5 | 39.9 | 0 | 8.6 | -2.86 | 2.9 | 1009.9 | 0.81 | 16.4 |  | 30 | 27.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-03-22 11:11 | 46.6 | 36.9 | 0.2 | 16.3 | -5.8 | 5.8 | 1008 | 5.39 | 44.4 | 216.9 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-03-22 11:11 | 44.6 | 35.6 | 0.7 | 19.1 | -2.7 | 2.7 | 1007 | 19.54 | 37.8 | 176 | 40 | 40 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-03-22 11:09 | 49.2 | 37.8 | 0 | 13 | -10.2 | 10.2 | 1008 | 4.12 | 38.8 | 200.7 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-03-22 11:09 | 45.9 | 38.8 | 0 | 15.3 | -8.61 | 8.6 | 1009.9 | 2.49 | 28.6 |  | 30 | 30.4 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-03-22 11:08 | 4.6 | 5.7 | 17.2 | 72.5 | -2.8 | 2.8 | 1009 | 1.46 | 10.6 | 5.1 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-03-22 11:08 | 58.3 | 41.9 | 0.2 | 0 | -37.4 | 37.4 | 1007 | 0.29 | 4.6 | 28 | 99 | 28.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-03-22 11:07 | 50.5 | 40.9 | 0 | 8.6 | -78.12 | 78.1 | 1009.8 | 0.67 | 6.8 |  | 100 | 31.8 | Blocked- Investigation RequiredSurging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-03-22 11:06 | 39.2 | 31.4 | 3.1 | 26.3 | 0 | 0 | 1008 | 0.07 | 1.1 | 4.7 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-03-22 11:05 | 34.5 | 34.1 | 3.5 | 27.9 | -12.15 | 12.2 | 1009.9 | 7.26 | 48.2 |  | 50 | 35.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-03-22 11:03 | 32.8 | 30.6 | 0.3 | 36.3 | 0.3 | -0.3 | 1008 | -0.33 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-03-22 11:03 | 49.4 | 39.4 | 0 | 11.2 | -28.07 | 28.1 | 1009.9 | 13.7 | 66 |  | 60 | 31.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-03-22 11:02 | 35.4 | 36.1 | 0 | 28.5 | -3.83 | 3.8 | 1009.8 | 0.42 | 11.8 |  | 30 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-03-22 11:01 | 43.5 | 34.8 | 0.8 | 20.9 | -2.9 | 2.9 | 1009 | 4.8 | 19.4 | 88.7 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-03-22 11:00 | 44.7 | 39.6 | 0 | 15.7 | -2.73 | 2.7 | 1009.8 | 1.5 | 22.2 |  | 30 | 32.1 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-03-22 10:59 | 51.8 | 39 | 0.2 | 9 | -9.8 | 9.8 | 1008 | 6.26 | 48 | 260.5 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-03-22 10:59 | 54.8 | 39 | 0 | 6.2 | -0.6 | 0.6 | 1007 | 6.87 | 23.1 | 132 | 15 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-03-22 10:58 | 37.9 | 36.6 | 0 | 25.5 | -0.1 | 0.1 | 1009 | -0.05 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-03-22 10:58 | 53.8 | 39.7 | 0 | 6.5 | -2.3 | 2.3 | 1007 | 15.99 | 34.6 | 195 | 40 | 37 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-03-22 10:57 | 0.1 | 0.3 | 22.5 | 77.1 | -1.12 | 1.1 | 1009.8 | 0.01 | 0.7 |  | 0 | 21.1 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-03-22 10:56 | 30.8 | 25.2 | 10.8 | 33.2 | 0.06 | -0.1 | 1009.9 | 0 | -0.4 |  | 0 | 20.6 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-03-22 10:56 | 62.1 | 39.2 | 0 | 0 | -34.1 | 34.1 | 1007 | 10.06 | 60.1 | 391 | 99 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-03-22 10:55 | 42.6 | 35.4 | 0 | 22 | -5 | 5 | 1008 | 12.36 | 31.1 | 138.9 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-03-22 10:55 | 55.4 | 38.6 | 0 | 6 | -0.1 | 0.1 | 1007 | 2.89 | 14.9 | 86 | 20 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-03-22 10:54 | 1.8 | 3 | 21.6 | 73.6 | -0.51 | 0.5 | 1009.9 | -0.08 | -2.4 |  | 0 | 20 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-03-22 10:53 | 53.2 | 39.3 | 0 | 7.5 | -0.4 | 0.4 | 1007 | 2.56 | 13.8 | 77 | 15 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-03-22 10:52 | 63.1 | 39.5 | 0 | 0 | -21 | 21 | 1007 | 7.32 | 24 | 159 | 99 | 28.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-03-22 10:51 | 52.2 | 40.5 | 0.5 | 6.8 | -8.1 | 8.1 | 1007 | 6.35 | 22.3 | 122.5 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-03-22 10:50 | 58.3 | 39.5 | 0 | 2.2 | -10.7 | 10.7 | 1007 | 5.07 | 42.4 | 259 | 40 | 36 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-03-22 10:49 | 48.6 | 33.8 | 3.5 | 14.1 | -48.6 | 48.6 | 1008 | 1.15 | 9.4 | 48 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-03-22 10:48 | 51.6 | 38.8 | 0 | 9.6 | -0.7 | 0.7 | 1007 | 4.18 | 17.6 | 95 | 25 | 38.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-03-22 10:47 | 51.8 | 40.2 | 0 | 8 | -20.9 | 20.9 | 1008 | 15.49 | 34.7 | 188.8 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-03-22 10:44 | 27.4 | 31.7 | 0 | 40.9 | -0.4 | 0.4 | 1007 | 0.79 | 7.7 | 22.2 | 5 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-03-22 10:42 | 56.6 | 39.3 | 0.3 | 3.8 | -41.3 | 41.3 | 1008 | 2.74 | 14.6 | 86.8 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-03-22 10:42 | 59 | 38.7 | 0 | 2.3 | -1.6 | 1.6 | 1007 | 3.94 | 4.4 | 27 | 5 | 25.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-03-22 10:40 | 55.1 | 39.7 | 0 | 5.2 | -4.3 | 4.3 | 1007 | 2.59 | 50.8 | 293.8 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-03-22 10:40 | 50.1 | 39.9 | 0.2 | 9.8 | -4.88 | 4.9 | 1010.7 | 5.75 | 20.6 |  | 30 | 27.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-03-22 10:40 | 53.5 | 39.3 | 0 | 7.2 | -0.4 | 0.4 | 1007 | 2.67 | 7 | 39 | 15 | 31.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-03-22 10:39 | 51.4 | 38.4 | 0 | 10.2 | -0.1 | 0.1 | 1007 | 0 | 0 | 0 | 10 | 27.4 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-03-22 10:38 | 42.4 | 36.6 | 0.9 | 20.1 | 0.3 | -0.3 | 1007 | -0.08 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-03-22 10:38 | 44.3 | 37.8 | 1.1 | 16.8 | -0.82 | 0.8 | 1009.9 | 8.14 | 6 |  | 30 | 30.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-03-22 10:37 | 46.8 | 38.7 | 0.3 | 14.2 | -2.69 | 2.7 | 1010.4 | 2.61 | 6.8 |  | 20 | 27.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-03-22 10:37 | 55.3 | 39.1 | 0 | 5.6 | -28.5 | 28.5 | 1007 | 18.06 | 78.9 | 457 | 99 | 35.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-03-22 10:35 | 42.9 | 37.8 | 1.1 | 18.2 | -2.27 | 2.3 | 1009.9 | 9.69 | 6.6 |  | 30 | 32.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-03-22 10:35 | 58.7 | 39.6 | 0 | 1.7 | -3 | 3 | 1007 | 2.27 | 28.5 | 175 | 25 | 34.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-03-22 10:34 | 52.3 | 39.4 | 0 | 8.3 | -1.1 | 1.1 | 1007 | 3.16 | 15.3 | 84 | 20 | 39.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-03-22 10:33 | 39.5 | 37.8 | 0 | 22.7 | -79.81 | 79.8 | 1010.7 | 2.88 | 29.7 |  | 100 | 29.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-03-22 10:33 | 60.6 | 39.8 | 0 | 0 | -3.4 | 3.4 | 1007 | 5.32 | 20.4 | 129 | 25 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-03-22 10:31 | 47.7 | 38.4 | 0 | 13.9 | -6.24 | 6.2 | 1010.9 | 3.2 | 32.1 |  | 40 | 36.5 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-03-22 10:31 | 46.1 | 34.8 | 2.2 | 16.9 | 0 | 0 | 1007 | 5.43 | 20.2 | 97 | 5 | 35 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-03-22 10:30 | 44.3 | 38.3 | 0.3 | 17.1 | -4.42 | 4.4 | 1009.9 | 1.69 | 23.3 |  | 30 | 39.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-03-22 10:29 | 62.5 | 40.5 | 0 | 0 | -15.2 | 15.2 | 1007 | 4.13 | 63.2 | 414 | 55 | 31.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-03-22 10:28 | 53.6 | 39.6 | 0 | 6.8 | -11.02 | 11 | 1010.7 | 20.08 | 37.8 |  | 40 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-03-22 10:27 | 29.4 | 34.5 | 0.1 | 36 | -0.82 | 0.8 | 1010.1 | 1.73 | 11.3 |  | 30 | 31.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-03-22 10:26 | 59.4 | 41 | 0 | 0 | -0.9 | 0.9 | 1007 | 11.36 | 29.6 | 184 | 20 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-03-22 10:25 | 55.1 | 38.2 | 0.2 | 6.5 | -3.9 | 3.9 | 1007 | 7.5 | 51.4 | 297 | 50 | 37.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-03-22 10:23 | 55.3 | 40.2 | 0 | 4.5 | -2.7 | 2.7 | 1007 | 3.01 | 32.5 | 188 | 40 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-03-22 10:22 | 58 | 38 | 0.7 | 3.3 | -1.7 | 1.7 | 1006 | 8.15 | 25.3 | 154 | 25 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-03-22 10:19 | 49.4 | 36.9 | 1.2 | 12.5 | -5.6 | 5.6 | 1007 | 9.3 | 27.2 | 140.9 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-03-22 10:14 | 58.3 | 40.3 | 0 | 1.4 | -1.2 | 1.2 | 1010.1 | 1.3 | 9.8 |  | 40 | 28.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-03-22 10:13 | 53.4 | 37.5 | 0 | 9.1 | -24.8 | 24.8 | 1008 | 1.2 | 21 | 117.9 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-03-22 10:12 | 57.7 | 40.5 | 0 | 1.8 | -0.45 | 0.5 | 1010.7 | 2.26 | 12.9 |  | 60 | 32 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-03-22 10:11 | 59.3 | 39.2 | 0 | 1.5 | -33.7 | 33.7 | 1008 | 0.41 | 12.3 | 76.5 | 50 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-03-22 10:10 | 58.7 | 39.8 | 0 | 1.5 | 0.21 | -0.2 | 1010.1 | 2.5 | 13.7 |  | 50 | 26.5 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-03-22 10:08 | 41 | 32.9 | 8.6 | 17.5 | -13.25 | 13.3 | 1010.3 | 1.69 | 11.3 |  | 100 | 19.4 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-03-22 10:07 | 56 | 39.5 | 0 | 4.5 | -42.9 | 42.9 | 1008 | 0.12 | 6.4 | 38 | 80 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-03-22 10:05 | 52.9 | 38.2 | 0.2 | 8.7 | -1.5 | 1.5 | 1008 | 1.51 | 23.7 | 131.8 | 30 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-03-22 10:04 | 54.2 | 40 | 0 | 5.8 | -5.2 | 5.2 | 1010.3 | 13.01 | 30.6 |  | 50 | 34.1 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-03-22 10:03 | 52.9 | 38.4 | 0 | 8.7 | -41.5 | 41.5 | 1008 | 1.94 | 43.2 | 239.5 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-03-22 10:03 | 50.2 | 36.1 | 0.4 | 13.3 | -16.61 | 16.6 | 1011.1 | 11 | 28.1 |  | 50 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-03-22 10:01 | 52.3 | 40.5 | 0 | 7.2 | -45.5 | 45.5 | 1007 | -0.24 | 0 | 0 | 80 | 20 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-03-22 09:59 | 57.4 | 39.4 | 0.2 | 3 | -9.12 | 9.1 | 1011.1 | 12.92 | 30.6 |  | 40 | 31.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-03-22 09:41 | 49.2 | 39 | 0 | 11.8 | -4.1 | 4.1 | 1008 | 18.63 | 38.3 | 197.7 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-03-22 09:39 | 58.9 | 40.5 | 0 | 0.6 | -19.2 | 19.2 | 1008 | 0.02 | 2.4 | 15.1 | 5 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-03-22 09:39 | 53.3 | 39.7 | 0 | 7 | -0.3 | 0.3 | 1006 | 2.51 | 6.7 | 37 | 15 | 39.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-03-22 09:37 | 52 | 40 | 0 | 8 | -1.8 | 1.8 | 1006 | 2.97 | 14.8 | 80 | 20 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-03-22 09:36 | 44.5 | 36.8 | 0 | 18.7 | -4.4 | 4.4 | 1008 | 2.23 | 13.2 | 61.6 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-03-22 09:35 | 55.9 | 39.6 | 0 | 4.5 | -9 | 9 | 1008 | 1.39 | 10.5 | 61.9 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-03-22 09:35 | 38.6 | 35.8 | 0 | 25.6 | -3.2 | 3.2 | 1006 | 2.49 | 13.5 | 54 | 15 | 28.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-03-22 09:34 | 46.4 | 37.5 | 0.2 | 15.9 | -89.06 | 89.1 | 1011.1 | 1.18 | 9 |  | 50 | 24.4 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-03-22 09:33 | 58.2 | 39.4 | 0.1 | 2.3 | -69.9 | 69.9 | 1008 | 1.92 | 26.1 | 159.3 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-03-22 09:33 | 47.8 | 36.8 | 2.2 | 13.2 | -2.7 | 2.7 | 1006 | 1.58 | 23.1 | 116 | 25 | 41.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-03-22 09:32 | 12.2 | 23.9 | 9.4 | 54.5 | -3.67 | 3.7 | 1011.1 | -0.01 | -0.1 |  | 0 | 21.8 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-03-22 09:31 | 57.7 | 40.3 | 0 | 2 | -21.2 | 21.2 | 1007 | 5.53 | 21 | 127.1 | 2 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-03-22 09:31 | 49.5 | 39.6 | 0 | 10.9 | -3.7 | 3.7 | 1006 | 1.72 | 24.1 | 125 | 20 | 41.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-03-22 09:30 | 21.1 | 19.6 | 12.1 | 47.2 | -97.36 | 97.4 | 1010.7 | 0.63 | 6.6 |  | 50 | 20.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-03-22 09:30 | 49.8 | 38.6 | 0 | 11.6 | -11.9 | 11.9 | 1006 | 14.22 | 69.4 | 362 | 50 | 39.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-03-22 09:29 | 56.5 | 39.8 | 0 | 3.7 | -51.2 | 51.2 | 1008 | 0.36 | 5.2 | 31 | 10 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-03-22 09:28 | 54.4 | 36.8 | 0.1 | 8.7 | -80.44 | 80.4 | 1011.1 | 11.17 | 6.9 |  | 100 | 23.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-03-22 09:28 | 54.9 | 41.6 | 0 | 3.5 | -0.2 | 0.2 | 1006 | 2.85 | 7.3 | 42 | 10 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-03-22 09:27 | 55 | 40.6 | 1.2 | 3.2 | -1.8 | 1.8 | 1008 | 9.12 | 27 | 156 | 50 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-03-22 09:27 | 33.6 | 33.6 | 2.9 | 29.9 | -8.98 | 9 | 1011.1 | 1.63 | 2.7 |  | 30 | 21.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-03-22 09:27 | 57.5 | 40 | 0 | 2.5 | -5 | 5 | 1006 | 15.71 | 34.8 | 210 | 40 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-03-22 09:25 | 51.3 | 39 | 0 | 9.7 | -15.7 | 15.7 | 1006 | 1.83 | 25 | 134 | 25 | 36.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-03-22 09:24 | 57.3 | 38.8 | 0 | 3.9 | -67.1 | 67.1 | 1008 | 4.97 | 19.5 | 117.2 | 99 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-03-22 09:24 | 35.6 | 35.4 | 0.6 | 28.4 | -28.39 | 28.4 | 1010.9 | 0.5 | 6.1 |  | 30 | 24 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-03-22 09:24 | 52.7 | 38.2 | 0.1 | 9 | -9.6 | 9.6 | 1006 | 5.11 | 43.4 | 240 | 40 | 18.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-03-22 09:23 | 39.6 | 33.3 | 0 | 27.1 | -74.55 | 74.6 | 1011.1 | 0.62 | 1.6 |  | 30 | 22.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-03-22 09:22 | 48.7 | 38.3 | 0 | 13 | -94.84 | 94.8 | 1010.9 | 1.71 | 22.8 |  | 100 | 27 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-03-22 09:22 | 39.4 | 31.9 | 2.7 | 26 | -0.9 | 0.9 | 1006 | 23.6 | 10.7 | 44 | 5 | 20.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-03-22 09:21 | 50.2 | 39.4 | 0 | 10.4 | -0.8 | 0.8 | 1008 | 1.03 | 4.4 | 23.6 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-03-22 09:20 | 49.6 | 37.6 | 0 | 12.8 | -8.49 | 8.5 | 1010.4 | 10.43 | 6.9 |  | 30 | 24 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-03-22 09:20 | 40.6 | 36.6 | 0 | 22.8 | -0.7 | 0.7 | 1005 | 12.27 | 7.5 | 32 | 5 | 33.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-03-22 09:19 | 45.3 | 38.5 | 0 | 16.2 | -2.2 | 2.2 | 1007 | 0.43 | 12.4 | 59 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-03-22 09:19 | 41 | 35.2 | 0 | 23.8 | -33.44 | 33.4 | 1011.1 | 0.82 | 7.8 |  | 30 | 23.4 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-03-22 09:17 | 46.5 | 38.7 | 0 | 14.8 | -4.1 | 4.1 | 1008 | 2.08 | 27.4 | 134 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-03-22 09:16 | 44.7 | 37.2 | 0.1 | 18 | -3.2 | 3.2 | 1007 | 0.43 | 5.8 | 27.2 | 5 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-03-22 09:15 | 45.5 | 37.3 | 0.1 | 17.1 | -73.81 | 73.8 | 1010.9 | 0.27 | 4.4 |  | 30 | 19.4 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-03-22 09:15 | 54.5 | 41.3 | 0 | 4.2 | -31.6 | 31.6 | 1005 | 12.92 | 106.9 | 611 | 99 | 41.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-03-22 09:14 | 41.2 | 32 | 4.7 | 22.1 | -2 | 2 | 1005 | 9.16 | 6.7 | 29 | 0 | 20.3 | Damaged
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-03-22 09:13 | 46.7 | 35.4 | 0.1 | 17.8 | -20.82 | 20.8 | 1011.1 | 4.42 | 18 |  | 30 | 27 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-03-22 09:10 | 61.1 | 42.7 | 0 | 0 | -39 | 39 | 1005 | 3.32 | 15.8 | 101 | 99 | 27.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-03-22 09:09 | 47.5 | 35.6 | 0.8 | 16.1 | -99.15 | 99.2 | 1010.7 | 1.65 | 10.6 |  | 100 | 23.9 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-03-22 09:09 | 58.2 | 41.2 | 0 | 0.6 | -7.2 | 7.2 | 1005 | 7.82 | 53.8 | 328 | 40 | 20.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-03-22 09:07 | 34.3 | 30.3 | 9 | 26.4 | -0.03 | 0 | 1010.3 | -0.02 | -0.3 |  | 10 | 18.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-03-22 09:07 | 43.6 | 37 | 0 | 19.4 | -3.9 | 3.9 | 1005 | 9.2 | 25.6 | 117 | 20 | 42.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-03-22 09:06 | 49.8 | 39.3 | 0.1 | 10.8 | -5.9 | 5.9 | 1007 | 13.13 | 32.1 | 167.8 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-03-22 09:06 | 52.1 | 38 | 0 | 9.9 | -7.22 | 7.2 | 1010.9 | 0.59 | 6.7 |  | 20 | 19.9 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-03-22 09:05 | 49.8 | 38.4 | 1.4 | 10.4 | -28.3 | 28.3 | 1005 | 0 | 0 | 0 | 20 | 25.6 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-03-22 09:04 | 52.7 | 41.2 | 0 | 6.1 | 0.1 | -0.1 | 1007 | -0.09 | 0 | 0 | 0 | 20 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-03-22 09:04 | 47.1 | 35.2 | 0.7 | 17 | -7.27 | 7.3 | 1009.9 | 0.27 | 0.4 |  | 0 | 21.6 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-03-22 09:03 | 57.7 | 41.4 | 0 | 0.9 | -44.1 | 44.1 | 1005 | 1.19 | 19.9 | 120 | 99 | 39.5 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-03-22 09:02 | 20.8 | 20.8 | 13.1 | 45.3 | -91.37 | 91.4 | 1009.9 | 0.16 | 3.3 |  | 50 | 19.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-03-22 09:01 | 57.3 | 41.4 | 0 | 1.3 | -2.5 | 2.5 | 1007 | 20.33 | 20 | 120.6 | 20 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-03-22 09:01 | 54.1 | 39.8 | 0 | 6.1 | -34 | 34 | 1005 | 10.38 | 95.9 | 543 | 99 | 43 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-03-22 09:00 | 35.7 | 31.2 | 8.8 | 24.3 | -96.42 | 96.4 | 1010.4 | 0.36 | 5 |  | 40 | 19.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-03-22 09:00 | 49.4 | 39.7 | 0.5 | 10.4 | -2.5 | 2.5 | 1005 | 3.01 | 14.6 | 75 | 25 | 47.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-03-22 08:59 | 43.8 | 38.5 | 0 | 17.7 | -0.1 | 0.1 | 1007 | 1.7 | 11.5 | 52.8 | 10 | 20 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-03-22 08:58 | 57.5 | 40.8 | 0 | 1.7 | -50.7 | 50.7 | 1007 | 0.07 | 8 | 48.6 | 60 | 20 | Surge
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-03-22 08:55 | 49.8 | 39.8 | 0 | 10.4 | 0 | 0 | 1007 | 4.61 | 19.7 | 102.9 | 15 | 0 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-03-22 08:53 | 49.2 | 37.6 | 0 | 13.2 | -28.07 | 28.1 | 1010.4 | 0.82 | 7.7 |  | 30 | 25.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-03-22 08:50 | 41.3 | 35.9 | 0.2 | 22.6 | -2.38 | 2.4 | 1010.1 | 1.44 | 10.4 |  | 30 | 26.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-03-07 13:48 | 51.4 | 38.5 | 0 | 10.1 | -0.9 | 0.9 | 1009 | 2.43 | 13.4 | 72 | 20 | 40 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-03-07 13:47 | 38.3 | 34.8 | 0 | 26.9 | -2.1 | 2.1 | 1009 | 3.67 | 16.4 | 65 | 20 | 31.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-03-07 13:45 | 49 | 37.2 | 0 | 13.8 | -10.3 | 10.3 | 1009 | 13.77 | 68.5 | 352 | 70 | 40 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-03-07 13:44 | 49.7 | 38.6 | 0 | 11.7 | -2.6 | 2.6 | 1009 | 1.3 | 20.9 | 109 | 25 | 42.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-03-07 13:42 | 52.4 | 37.8 | 1.3 | 8.5 | -1.5 | 1.5 | 1009 | 1.13 | 19.8 | 109 | 25 | 37.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-03-07 13:40 | 65.6 | 41.5 | 0 | 0 | 0.5 | -0.5 | 1009 | 1.09 | 2.3 | 16 | 15 | 30.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-03-07 13:37 | 48.1 | 39.2 | 0 | 12.7 | 0 | 0 | 1009 | 12.52 | 7.6 | 38 | 15 | 36.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-03-06 13:19 | 57 | 41.7 | 0.4 | 0.9 | 0.5 | -0.5 | 1008 | 4.74 | 4.7 | 28 | 22 | 31.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-03-06 13:17 | 42 | 35.5 | 0 | 22.5 | -4.8 | 4.8 | 1008 | 15.9 | 33.7 | 148 | 20 | 44 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-03-06 13:15 | 51.7 | 40.2 | 0.2 | 7.9 | -1.2 | 1.2 | 1007 | 3.02 | 14.7 | 79 | 40 | 48 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-03-06 13:11 | 34.3 | 25.3 | 6.3 | 34.1 | -0.1 | 0.1 | 1007 | -0.21 | 0 | 0 | 0 | 28.6 | Shut/Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-03-06 13:09 | 43 | 34.6 | 0.3 | 22.1 | -2.3 | 2.3 | 1007 | 0.53 | 13.4 | 60 | 10 | 36.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-03-06 13:07 | 61.5 | 40.3 | 0 | 0 | -41.4 | 41.4 | 1009 | 1.27 | 20.8 | 134 | 60 | 41.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-03-06 11:20 | 53.4 | 38.9 | 1 | 6.7 | -52.3 | 52.3 | 1007 | -0.19 | 0 | 0 | 70 | 27.9 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-03-06 11:19 | 47.2 | 38.2 | 0 | 14.6 | -0.2 | 0.2 | 1007 | 2.21 | 12.8 | 63 | 18 | 33.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-03-06 11:17 | 48.8 | 38.6 | 0 | 12.6 | -0.1 | 0.1 | 1007 | 4.9 | 18.8 | 96 | 23 | 44.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-03-06 11:13 | 46 | 37.2 | 0 | 16.8 | -4.5 | 4.5 | 1007 | 2.58 | 29.9 | 144 | 43 | 31.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-03-06 11:12 | 38.8 | 34.8 | 0 | 26.4 | -1.2 | 1.2 | 1007 | 1.27 | 9.7 | 39 | 5 | 26.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-03-06 11:10 | 41.5 | 35.5 | 0.3 | 22.7 | -1.2 | 1.2 | 1007 | 2.78 | 7.2 | 31 | 5 | 25.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-03-06 11:08 | 42.8 | 36.4 | 0.2 | 20.6 | -2.9 | 2.9 | 1007 | 0.95 | 18.2 | 81 | 20 | 26.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-03-06 11:00 | 42.2 | 33.9 | 2.2 | 21.7 | -0.6 | 0.6 | 1007 | 0.2 | 8.3 | 36 | 10 | 26.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-03-06 10:55 | 41.8 | 33.3 | 2.5 | 22.4 | -2.6 | 2.6 | 1007 | 0.2 | 8.3 | 36 | 20 | 33.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-03-06 10:51 | 41.5 | 36.7 | 0 | 21.8 | -1.5 | 1.5 | 1007 | 1.49 | 10.5 | 45 | 10 | 27.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-03-06 10:48 | 44.9 | 36.3 | 0 | 18.8 | -4.1 | 4.1 | 1007 | 1.21 | 20.5 | 96 | 20 | 29.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-03-06 10:47 | 44.8 | 36.5 | 0 | 18.7 | -11.3 | 11.3 | 1007 | 3.27 | 33.6 | 157 | 35 | 31.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-03-06 10:44 | 34.2 | 29.4 | 3.9 | 32.5 | -21.7 | 21.7 | 1007 | 15.82 | 72.5 | 260 | 40 | 37 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-03-06 10:42 | 39.2 | 33.7 | 0.6 | 26.5 | -7.4 | 7.4 | 1006 | 0.98 | 18.5 | 76 | 20 | 27.1 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-03-06 10:01 | 46.6 | 36.7 | 0.4 | 16.3 | -5.9 | 5.9 | 1007 | 5.26 | 42.5 | 208 | 45 | 36.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-03-06 09:58 | 35.4 | 31 | 0.5 | 33.1 | -2.3 | 2.3 | 1007 | 0.17 | 7.6 | 28 | 5 | 27.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-03-06 09:56 | 34.5 | 35 | 0 | 30.5 | -1.8 | 1.8 | 1007 | 0.67 | 15 | 54 | 10 | 31.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-03-06 09:54 | 44.6 | 35.5 | 0.2 | 19.7 | -3.2 | 3.2 | 1007 | 14.74 | 33.3 | 156 | 40 | 30.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-03-06 09:52 | 45.2 | 36.6 | 0 | 18.2 | -14.2 | 14.2 | 1006 | 15.43 | 71.6 | 339 | 65 | 42.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-03-06 09:48 | 19.8 | 26 | 1.8 | 52.4 | -0.7 | 0.7 | 1006 | 3.61 | 16 | 33 | 10 | 31.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-03-06 09:46 | 41.5 | 34.1 | 2 | 22.4 | -1.7 | 1.7 | 1005 | 2.61 | 14 | 61 | 15 | 28.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-03-06 09:40 | 49.3 | 39.7 | 0 | 11 | -39.3 | 39.3 | 1005 | 8.79 | 24.5 | 126 | 45 | 49 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-03-06 09:38 | 47.6 | 38.3 | 0.2 | 13.9 | -10.7 | 10.7 | 1005 | 1.74 | 24.1 | 120 | 20 | 42.3 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-03-06 09:35 | 48.3 | 38.9 | 0 | 12.8 | -19.2 | 19.2 | 1005 | 16.62 | 34.2 | 173 | 40 | 46 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-03-06 09:32 | 35.8 | 33.7 | 0.1 | 30.4 | -1.5 | 1.5 | 1005 | 2.14 | 26.9 | 101 | 25 | 34.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-03-06 09:29 | 38.8 | 34.1 | 0.7 | 26.4 | -3.1 | 3.1 | 1005 | 23.35 | 10.3 | 42 | 35 | 39.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-03-02 07:58 | 22.8 | 26.1 | 1.4 | 49.7 | -5.5 | 5.5 | 1009 | 4.45 | 38.7 | 92 |  | 30.7
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-03-01 08:38 | 63.1 | 39.8 | 0 | 0 | -4 | 4 | 1010 | 5.63 | 21 | 139 | 55 | 35 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-03-01 08:35 | 31.2 | 33.3 | 0 | 35.5 | -1.5 | 1.5 | 1010 | 1.28 | 20.8 | 68 | 20 | 29.1 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-03-01 08:32 | 58.3 | 41.6 | 0 | 0.1 | -13.4 | 13.4 | 1010 | 10.32 | 28.1 | 172 | 50 | 28.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-03-01 08:30 | 39.4 | 35 | 0 | 25.6 | -6.7 | 6.7 | 1009 | 5.52 | 42.8 | 176 | 40 | 40.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-03-01 08:27 | 59.8 | 41.6 | 0 | 0 | -3.1 | 3.1 | 1010 | 6.57 | 22.6 | 141 | 40 | 29.7 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-03-01 08:21 | 39.1 | 32.6 | 2.5 | 25.8 | -3.3 | 3.3 | 1010 | 1.61 | 10.9 | 44 | 10 | 31.8 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-03-01 08:17 | 36.6 | 31 | 3.1 | 29.3 | -2 | 2 | 1011 | 2.1 | 6.1 | 23 | 10 | 38.6 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X163 | 2017-02-28 15:11 | 41.3 | 33.1 | 1.9 | 23.7 | -4.4 | 4.4 | 1011 | 2.92 | 30.9 | 133 | 40 | 49.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C404 | 2017-02-28 15:08 | 60 | 38.7 | 0 | 1.3 | -2.3 | 2.3 | 1011 | 20.44 | 40.3 | 253 | 50 | 29.5 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BHW2C403 | 2017-02-28 15:05 | 31.2 | 21.1 | 8.3 | 39.4 | -84.1 | 84.1 | 1011 | -0.01 | 0 | 0 | 99 | 38.3 | Blocked-Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C394 | 2017-02-28 15:04 | 59.6 | 38.8 | 0 | 1.6 | -3.8 | 3.8 | 1011 | 9.94 | 27.9 | 174 | 35 | 31.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section C | BGW2C355 | 2017-02-28 15:02 | 58.9 | 40.8 | 0 | 0.3 | -25.2 | 25.2 | 1011 | 18.67 | 37.3 | 230 | 45 | 36.7 | Change Orife Plate Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-02-28 13:57 | 31.6 | 29.7 | 0.4 | 38.3 | -1.9 | 1.9 | 1011 | 1.38 | 10.2 | 34 | 20 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y325 | 2017-02-20 14:35 | 51.2 | 42 | 0 | 6.8 | -4.03 | 4 | 1006.9 | 20.432 | 37.97 |  | 40 | 38.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y318 | 2017-02-20 14:34 | 49.6 | 41.4 | 0 | 9 | -14.3 | 14.3 | 1007.4 | 16.267 | 71.28 |  | 80 | 40.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y311 | 2017-02-20 14:32 | 42.2 | 38.6 | 1.4 | 17.8 | -3.07 | 3.1 | 1007.3 | 22.805 | 40.06 |  | 60 | 39 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y315 | 2017-02-20 14:30 | 55.4 | 42.9 | 0.1 | 1.6 | -29.02 | 29 | 1007.4 | 17.029 | 106.8 |  | 100 | 43.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y322 | 2017-02-20 14:28 | 56.1 | 43.4 | 0 | 0.5 | -31.96 | 32 | 1007.3 | 12.349 | 61.32 |  | 100 | 43.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y332 | 2017-02-20 14:26 | 49.3 | 42.8 | 0 | 7.9 | -3.24 | 3.2 | 1007.3 | 11.991 | 29.32 |  | 50 | 35.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y449 | 2017-02-20 14:23 | 49 | 41.7 | 0 | 9.3 | -4.3 | 4.3 | 1007.3 | 19.089 | 36.87 |  | 50 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y329 | 2017-02-20 14:22 | 50.9 | 39.7 | 0.5 | 8.9 | -41.53 | 41.5 | 1007.3 | 0.593 | 13.78 |  | 100 | 27.2 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Y | BGW2Y271 | 2017-02-20 14:20 | 34.5 | 31.1 | 8.1 | 26.3 | -43.74 | 43.7 | 1007.3 | 0.249 | 4.21 |  | 100 | 28.3 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P288 | 2017-02-20 14:11 | 46 | 39.4 | 1.9 | 12.7 | -0.07 | 0.1 | 1007.4 | 6.247 | 10.31 |  | 30 | 35.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P280 | 2017-02-20 14:09 | 51.7 | 40.3 | 0.5 | 7.5 | -3.9 | 3.9 | 1007.4 | 7.606 | 49.4 |  | 50 | 37.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P269 | 2017-02-20 14:07 | 54.2 | 39.9 | 0.8 | 5.1 | -2.03 | 2 | 1007.6 | 8.69 | 25.17 |  | 30 | 31.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P272 | 2017-02-20 14:05 | 51.4 | 41.5 | 0 | 7.1 | -2.84 | 2.8 | 1007.4 | 3.105 | 31.69 |  | 40 | 35.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P283 | 2017-02-20 14:04 | 55 | 42.1 | 0.2 | 2.7 | -1.43 | 1.4 | 1007.4 | 10.994 | 28.14 |  | 40 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P286 | 2017-02-20 14:02 | 58.1 | 41.1 | 0 | 0.8 | -12.93 | 12.9 | 1007.7 | 4.506 | 56.74 |  | 50 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P334 | 2017-02-20 14:01 | 49.6 | 40.8 | 0 | 9.6 | 0.75 | -0.8 | 1008.2 | 1.771 | 11.4 |  | 30 | 31.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P333 | 2017-02-20 13:59 | 46.4 | 38.3 | 1.5 | 13.8 | -0.19 | 0.2 | 1007.4 | 0.536 | 6.3 |  | 20 | 28.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P447 | 2017-02-20 13:57 | 49.5 | 38.4 | 1.4 | 10.7 | -1.81 | 1.8 | 1007.3 | 3.656 | 4.08 |  | 20 | 25.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P290 | 2017-02-20 13:55 | 54.6 | 40.8 | 0.4 | 4.2 | -2.84 | 2.8 | 1007.3 | 5.333 | 19.72 |  | 30 | 31.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P293 | 2017-02-20 13:53 | 54.4 | 41.2 | 0.3 | 4.1 | -3.51 | 3.5 | 1007.4 | 2.825 | 30.32 |  | 40 | 33.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P291 | 2017-02-20 13:52 | 49.4 | 40.8 | 0.1 | 9.7 | -2.42 | 2.4 | 1007.3 | 2.697 | 13.86 |  | 30 | 39.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section P | BGW2P295 | 2017-02-20 13:50 | 52.2 | 40.7 | 0 | 7.1 | -30.28 | 30.3 | 1007.4 | 19.716 | 78.36 |  | 100 | 35.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X166 | 2017-02-20 13:37 | 54.8 | 41.4 | 0 | 3.8 | -0.5 | 0.5 | 1008.5 | 0.371 | 10.89 |  | 20 | 41.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X159 | 2017-02-20 13:34 | 55.5 | 40.6 | 0 | 3.9 | -3.19 | 3.2 | 1008.2 | 5.733 | 20.18 |  | 30 | 39.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X160 | 2017-02-20 13:30 | 45.1 | 34.7 | 10 | 10.2 | -3.49 | 3.5 | 1008.4 | 0.242 | 4.28 |  | 100 | 21.5 | DamagedSurging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X167 | 2017-02-20 13:24 | 52.6 | 40.4 | 0.3 | 6.7 | -0.76 | 0.8 | 1008.4 | 0.062 | 4.46 |  | 100 | 40.2 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X162 | 2017-02-20 13:21 | 58.4 | 40.8 | 0 | 0.8 | -0.78 | 0.8 | 1008.4 | 0.441 | 5.68 |  | 30 | 32.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X161 | 2017-02-20 13:18 | 58.1 | 40.2 | 0 | 1.7 | -1.08 | 1.1 | 1008.5 | 0.404 | 2.65 |  | 100 | 29.6 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K115 | 2017-02-20 13:08 | 33.9 | 36.6 | 0.2 | 29.3 | -0.72 | 0.7 | 1008.1 | 3.116 | 14.94 |  | 30 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K117 | 2017-02-20 13:04 | 33.5 | 34.4 | 0.1 | 32 | -4.5 | 4.5 | 1007.4 | 9.31 | 25.71 |  | 30 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R274 | 2017-02-20 11:11 | 51 | 40.3 | 0 | 8.7 | -1.04 | 1 | 1007.3 | 2.546 | 6.66 |  | 30 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R409 | 2017-02-20 11:09 | 47 | 40.6 | 0 | 12.4 | -2.48 | 2.5 | 1007.3 | 3.074 | 14.8 |  | 40 | 39 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BHW2R410 | 2017-02-20 11:08 | 50.2 | 41.8 | 0 | 8 | -27.97 | 28 | 1007.3 | 15.797 | 103.01 |  | 80 | 43.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R277 | 2017-02-20 11:06 | 37.4 | 39.4 | 0 | 23.2 | -3.3 | 3.3 | 1006.6 | 4.256 | 17.68 |  | 30 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R192 | 2017-02-20 11:04 | 55.4 | 41.9 | 0 | 2.7 | 0.49 | -0.5 | 1007.3 | 3.437 | 7.73 |  | 30 | 29.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R197 | 2017-02-20 11:02 | 47.6 | 40.1 | 0 | 12.3 | -11.34 | 11.3 | 1007.4 | 14.835 | 68.32 |  | 60 | 39.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R201 | 2017-02-20 11:00 | 47.5 | 40.8 | 0.1 | 11.6 | -3.73 | 3.7 | 1007.4 | 1.953 | 24.92 |  | 30 | 40.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R437 | 2017-02-20 10:58 | 46.3 | 38.4 | 3 | 12.3 | -2.86 | 2.9 | 1006.6 | 1.793 | 24.06 |  | 30 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R436 | 2017-02-20 10:55 | 54.2 | 40 | 0 | 5.8 | -4.95 | 5 | 1007.3 | 15.752 | 33.75 |  | 30 | 31.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R202 | 2017-02-20 10:54 | 50.2 | 40.1 | 0 | 9.7 | -30.28 | 30.3 | 1007.4 | 0.944 | 17.31 |  | 30 | 33.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R384 | 2017-02-20 10:52 | 50.6 | 39 | 0.4 | 10 | -9.71 | 9.7 | 1007.3 | 5.14 | 41.21 |  | 30 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R208 | 2017-02-20 10:50 | 47.2 | 38.8 | 1.9 | 12.1 | -0.22 | 0.2 | 1007.3 | 1.515 | 2.65 |  | 20 | 21.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section R | BGW2R207 | 2017-02-20 10:48 | 43.6 | 40.3 | 0 | 16.1 | -0.46 | 0.5 | 1006.3 | 12.406 | 7.39 |  | 30 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S385 | 2017-02-20 10:33 | 55 | 40.8 | 0 | 4.2 | -5.39 | 5.4 | 1006 | 7.795 | 50.89 |  | 50 | 25.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S281 | 2017-02-20 10:31 | 57 | 41.4 | 0.2 | 1.4 | -40.8 | 40.8 | 1006.2 | 1.59 | 10.68 |  | 100 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BHW2S411 | 2017-02-20 10:29 | 55.8 | 42.4 | 0 | 1.8 | -43.53 | 43.5 | 1006.2 | 1.242 | 19.72 |  | 100 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S206 | 2017-02-20 10:27 | 42 | 36.1 | 5.7 | 16.2 | -0.53 | 0.5 | 1006.2 | 4.981 | 4.77 |  | 20 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S216 | 2017-02-20 10:25 | 50.8 | 40.8 | 0.3 | 8.1 | -34.59 | 34.6 | 1006.2 | 15.894 | 103.16 |  | 90 | 41.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S211 | 2017-02-20 10:23 | 42.3 | 38.4 | 0 | 19.3 | -6.04 | 6 | 1007.3 | 17.259 | 34.68 |  | 40 | 42.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S212 | 2017-02-20 10:19 | 0.4 | 4 | 19.7 | 75.9 | -42.58 | 42.6 | 1006.9 | 0.264 | 9.31 |  | 10 | 20 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S217 | 2017-02-20 10:17 | 18.9 | 18.9 | 16.6 | 45.6 | -46.05 | 46.1 | 1006.3 | 0.023 | 2.75 |  | 100 | 20 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S223 | 2017-02-20 10:15 | 50.9 | 40.3 | 0 | 8.8 | -35.12 | 35.1 | 1006.2 | 14.886 | 100.04 |  | 100 | 40.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section S | BGW2S222 | 2017-02-20 10:13 | 47.9 | 40.2 | 0.7 | 11.2 | -2.04 | 2 | 1006.2 | 3.342 | 15.24 |  | 40 | 46.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U399 | 2017-02-20 09:56 | 54.8 | 39.5 | 0.7 | 5 | -28.91 | 28.9 | 1006 | 11.277 | 59.72 |  | 60 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U351 | 2017-02-20 09:54 | 15.3 | 18.3 | 17.7 | 48.7 | -0.5 | 0.5 | 1006 | -0.016 | -1.08 |  | 0 | 33.1 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U352 | 2017-02-20 09:52 | 56.1 | 42 | 0 | 1.9 | -17.66 | 17.7 | 1005.1 | 17.17 | 73.85 |  | 60 | 33.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U353 | 2017-02-20 09:50 | 53.4 | 43.9 | 0 | 2.7 | -26.5 | 26.5 | 1005.8 | 12.669 | 63.17 |  | 70 | 34.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BHW2U354 | 2017-02-20 09:48 | 53.8 | 42.5 | 0 | 3.7 | -21.77 | 21.8 | 1005.8 | 19.789 | 78.56 |  | 70 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U284 | 2017-02-20 09:46 | 57.5 | 40 | 0.4 | 2.1 | -38.69 | 38.7 | 1006 | 0.445 | 11.86 |  | 30 | 32.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U440 | 2017-02-20 09:44 | 12.1 | 14.2 | 17.9 | 55.8 | -43.11 | 43.1 | 1005.7 | 0.143 | 3.24 |  | 100 | 19 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U391 | 2017-02-20 09:42 | 55.2 | 39.9 | 0.6 | 4.3 | -3.14 | 3.1 | 1004.9 | 8.833 | 25.3 |  | 30 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U226 | 2017-02-20 09:40 | 20.6 | 20.5 | 14.9 | 44 | -45.42 | 45.4 | 1005.5 | 0.121 | 2.96 |  | 100 | 19.7 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U439 | 2017-02-20 09:38 | 29.6 | 25.1 | 11 | 34.3 | -47.95 | 48 | 1005.1 | 0.442 | 5.64 |  | 100 | 21.7 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U241 | 2017-02-20 09:36 | 9.5 | 11.8 | 18.8 | 59.9 | -47.11 | 47.1 | 1005.4 | 0.249 | 9.05 |  | 100 | 17.2 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U251 | 2017-02-20 09:35 | 37.1 | 54 | 0 | 8.9 | -4.36 | 4.4 | 1006 | 2.039 | 25.75 |  | 30 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U245 | 2017-02-20 09:33 | 57.6 | 40.7 | 0 | 1.7 | -0.57 | 0.6 | 1004.9 | 0.54 | 13.33 |  | 20 | 31 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U232 | 2017-02-20 09:31 | 57.7 | 41.2 | 0 | 1.1 | -37.01 | 37 | 1005.5 | 4.615 | 55.93 |  | 60 | 39.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U227 | 2017-02-20 09:30 | 56.8 | 40.7 | 0 | 2.5 | -5.3 | 5.3 | 1005.8 | 6.851 | 22.4 |  | 30 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U238 | 2017-02-20 09:28 | 56.4 | 41.2 | 0 | 2.4 | -1.25 | 1.3 | 1004.9 | -0.02 | -1.23 |  | 0 | 24 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U398 | 2017-02-20 09:25 | 52.5 | 39.7 | 0.5 | 7.3 | -7.72 | 7.7 | 1004.9 | 2.423 | 28.68 |  | 40 | 19.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section U | BGW2U243 | 2017-02-20 09:23 | 56.9 | 39.2 | 0.2 | 3.7 | -0.78 | 0.8 | 1004.7 | -0.018 | -2.46 |  | 0 | 26.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X164 | 2017-02-20 09:05 | 58.6 | 38.6 | 0.1 | 2.7 | -73.18 | 73.2 | 1006 | 0.393 | 11.08 |  | 100 | 24.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X441 | 2017-02-20 09:03 | 58 | 39.4 | 0 | 2.6 | -21.77 | 21.8 | 1006 | 3.229 | 32.49 |  | 30 | 26.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X158 | 2017-02-20 09:01 | 58.3 | 38.4 | 0 | 3.3 | -52.26 | 52.3 | 1006 | 1.851 | 11.49 |  | 20 | 23 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X157 | 2017-02-20 08:59 | 56.9 | 37.1 | 1.2 | 4.8 | -67.29 | 67.3 | 1005.8 | 1.756 | 11.15 |  | 100 | 20.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X443 | 2017-02-20 08:57 | 53.7 | 37.6 | 2 | 6.7 | -1.83 | 1.8 | 1005.1 | 9.755 | 26.47 |  | 20 | 35 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X239 | 2017-02-20 08:55 | 36.9 | 32.2 | 7.4 | 23.5 | -50.68 | 50.7 | 1006.2 | 0.434 | 11.9 |  | 70 | 19 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X247 | 2017-02-20 08:53 | 48.7 | 39.2 | 0 | 12.1 | -4.82 | 4.8 | 1006.2 | 27.786 | 44.42 |  | 50 | 34.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X264 | 2017-02-20 08:51 | 59 | 39.7 | 0 | 1.3 | -26.08 | 26.1 | 1004.9 | 0.249 | 9.07 |  | 30 | 22.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X425 | 2017-02-20 08:49 | 42.9 | 37 | 0.6 | 19.5 | -5.14 | 5.1 | 1005.7 | 2.508 | 13.65 |  | 30 | 25.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X446 | 2017-02-17 14:37 | 52.9 | 42 | 0.8 | 4.3 | -7.9 | 7.9 | 1003.3 | 1.657 | 11.01 |  | 30 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X254 | 2017-02-17 14:35 | 50.2 | 39.6 | 0.1 | 10.1 | -24.5 | 24.5 | 1003.6 | 1.347 | 9.71 |  | 40 | 37.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V413 | 2017-02-17 14:30 | 39.3 | 36 | 5.4 | 19.3 | -0.42 | 0.4 | 1002.2 | 0.113 | 2.85 |  | 10 | 34.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V414 | 2017-02-17 14:28 | 50.7 | 37.1 | 0.7 | 11.5 | -47.21 | 47.2 | 1002.4 | 0.113 | 5.92 |  | 70 | 32.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V244 | 2017-02-17 14:26 | 10.5 | 11 | 16.1 | 62.4 | -47.21 | 47.2 | 1001.1 | 0.165 | 3.4 |  | 100 | 29.5 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V415 | 2017-02-17 14:23 | 56.1 | 42.9 | 0.1 | 0.9 | -38.06 | 38.1 | 1001.1 | 15.064 | 100.85 |  | 100 | 36.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V267 | 2017-02-17 14:22 | 1 | 2.4 | 20.3 | 76.3 | -1.19 | 1.2 | 1001.7 | 0.018 | 2.4 |  | 0 | 30.7 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V379 | 2017-02-17 14:19 | 42.1 | 40.5 | 0.3 | 17.1 | -2.43 | 2.4 | 1002.1 | 0.85 | 16.57 |  | 30 | 34.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V390 | 2017-02-17 14:17 | 50.4 | 41.9 | 0.1 | 7.6 | -7.03 | 7 | 1002.2 | 13.872 | 31.1 |  | 40 | 40.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V262 | 2017-02-17 14:16 | 56.1 | 43.5 | 0.2 | 0.2 | -25.55 | 25.6 | 1001.1 | 14.991 | 67.08 |  | 70 | 47.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BGW2V255 | 2017-02-17 14:14 | 54.2 | 39.8 | 0.2 | 5.8 | -46.47 | 46.5 | 1002.2 | 0.189 | 3.63 |  | 100 | 30.9 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section V | BHW2V407 | 2017-02-17 14:12 | 1.5 | 2.5 | 14.3 | 81.7 | -42.37 | 42.4 | 1002.2 | 3.565 | 32.93 |  | 50 | 40.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X393 | 2017-02-17 13:26 | 58.3 | 41.7 | 0 | 0 | -19.45 | 19.5 | 1002.4 | 0.313 | 10.08 |  | 30 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X249 | 2017-02-17 13:23 | 38.1 | 33.1 | 5.2 | 23.6 | -39.74 | 39.7 | 1002.4 | 1.979 | 25.09 |  | 70 | 27.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X259 | 2017-02-17 13:21 | 53.6 | 41.2 | 0.4 | 4.8 | -1.38 | 1.4 | 1003.5 | 1.643 | 23.32 |  | 30 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section X | BGW2X258 | 2017-02-17 13:20 | 51.9 | 41.2 | 0 | 6.9 | -41.43 | 41.4 | 1003.3 | 3.455 | 48.84 |  | 100 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W256 | 2017-02-17 13:10 | 56.2 | 43.7 | 0 | 0.1 | 3.63 | -3.6 | 1002.4 | 0.022 | 4.03 |  | 10 | 30 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W261 | 2017-02-17 13:07 | 50.3 | 42.3 | 0 | 7.4 | -4.86 | 4.9 | 1002.2 | 13.118 | 30.55 |  | 30 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W246 | 2017-02-17 13:05 | 54.5 | 43.5 | 0 | 2 | -2.21 | 2.2 | 1002.4 | 19.522 | 18.22 |  | 30 | 30.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W392 | 2017-02-17 13:03 | 48 | 42 | 0 | 10 | -0.33 | 0.3 | 1002.4 | 2.509 | 13.43 |  | 30 | 35.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W242 | 2017-02-17 13:02 | 42.8 | 37.8 | 4.2 | 15.2 | -50.79 | 50.8 | 1002.4 | 0.166 | 10.77 |  | 60 | 25.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section W | BGW2W257 | 2017-02-17 12:58 | 38.6 | 40 | 0 | 21.4 | -0.22 | 0.2 | 1002.4 | 4.498 | 17.74 |  | 30 | 43.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N144 | 2017-02-17 11:19 | 40.1 | 40 | 0.9 | 19 | -1.42 | 1.4 | 1002.5 | 2.873 | 7.07 |  | 20 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N143 | 2017-02-17 11:17 | 40.2 | 40.2 | 0.1 | 19.5 | -3.39 | 3.4 | 1003.6 | 2.56 | 28.96 |  | 30 | 30.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N146 | 2017-02-17 11:15 | 44.6 | 40.7 | 0 | 14.7 | -5.11 | 5.1 | 1003 | 2.533 | 28.65 |  | 30 | 33.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section N | BGW2N145 | 2017-02-17 11:13 | 38.1 | 39.8 | 0 | 22.1 | -1.75 | 1.8 | 1003.3 | 1.038 | 8.74 |  | 20 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H064 | 2017-02-17 10:52 | 40 | 37.6 | 2.6 | 19.8 | -0.7 | 0.7 | 1003.5 | 0.262 | 9.31 |  | 30 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H402 | 2017-02-17 10:50 | 39.3 | 37 | 3.2 | 20.5 | -4.03 | 4 | 1003.6 | 1.117 | 18.99 |  | 30 | 35.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H059 | 2017-02-17 10:47 | 40.9 | 40.4 | 0 | 18.7 | -0.86 | 0.9 | 1002.5 | 1.23 | 9.52 |  | 30 | 28.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H424 | 2017-02-17 10:45 | 38.1 | 36.3 | 2.8 | 22.8 | -1.28 | 1.3 | 1003.6 | 2.503 | 13.59 |  | 40 | 27.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H423 | 2017-02-17 10:43 | 50.8 | 40.5 | 0 | 8.7 | -2.67 | 2.7 | 1003.5 | 5.396 | 19.87 |  | 30 | 29.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H363 | 2017-02-17 10:42 | 44.2 | 39.7 | 0 | 16.1 | -4.5 | 4.5 | 1003.6 | 1.589 | 22.89 |  | 30 | 28.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H365 | 2017-02-17 10:40 | 44.7 | 39.8 | 0 | 15.5 | -11.32 | 11.3 | 1003.5 | 3.13 | 31.85 |  | 40 | 31.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H058 | 2017-02-17 10:38 | 56.8 | 42.2 | 0 | 1 | -70.87 | 70.9 | 1003.6 | 0.736 | 7.04 |  | 100 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H362 | 2017-02-17 10:37 | 35.5 | 35.9 | 3.5 | 25.1 | -25.23 | 25.2 | 1003.5 | 17.557 | 73.85 |  | 60 | 37 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H366 | 2017-02-17 10:34 | 49.9 | 40.1 | 0 | 10 | -25.34 | 25.3 | 1003.5 | 11.163 | 59.85 |  | 70 | 28.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H360 | 2017-02-17 10:32 | 38.8 | 38.2 | 0.4 | 22.6 | -7.24 | 7.2 | 1003.5 | 0.989 | 18.04 |  | 40 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H361 | 2017-02-17 10:30 | 45.9 | 39.4 | 0.1 | 14.6 | -2.09 | 2.1 | 1003.5 | 0.864 | 16.79 |  | 30 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H412 | 2017-02-17 10:28 | 0.1 | 0.1 | 21.4 | 78.4 | -1.64 | 1.6 | 1003.5 | -0.016 | -1.08 |  | 0 | 26.8 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H102 | 2017-02-17 10:25 | 25.2 | 23.5 | 12.2 | 39.1 | -0.03 | 0 | 1003 | 0.086 | 2.52 |  | 10 | 28.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section H | BGW2H422 | 2017-02-17 10:24 | 7.1 | 9.5 | 17.3 | 66.1 | -0.92 | 0.9 | 1003.5 | 1.736 | 11.33 |  | 0 | 27.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I445 | 2017-02-17 09:58 | 50.8 | 40.3 | 0.2 | 8.7 | -4.89 | 4.9 | 1003.6 | 4.991 | 19.15 |  | 30 | 27.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I370 | 2017-02-17 09:56 | 47.4 | 39.6 | 0.6 | 12.4 | -0.41 | 0.4 | 1003.6 | 6.849 | 5.51 |  | 30 | 31.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I368 | 2017-02-17 09:55 | 49 | 39.4 | 0.3 | 11.3 | -2.37 | 2.4 | 1003.6 | 1.558 | 5.19 |  | 20 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I367 | 2017-02-17 09:53 | 41.5 | 37.8 | 1.3 | 19.4 | -2.04 | 2 | 1003.5 | 10.422 | 6.78 |  | 30 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I081 | 2017-02-17 09:51 | 49.9 | 39.9 | 0 | 10.2 | -71.39 | 71.4 | 1003.3 | 3.342 | 31.97 |  | 100 | 29.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I371 | 2017-02-17 09:49 | 47.8 | 39.5 | 0 | 12.7 | -5.9 | 5.9 | 1003.6 | 3.214 | 32.09 |  | 60 | 36.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I369 | 2017-02-17 09:48 | 46.2 | 39.6 | 0.3 | 13.9 | -4.23 | 4.2 | 1003.6 | 1.979 | 25.1 |  | 50 | 39.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I396 | 2017-02-17 09:46 | 55.5 | 40.5 | 0 | 4 | -10.32 | 10.3 | 1003.5 | 19.009 | 36.74 |  | 30 | 33.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section I | BGW2I442 | 2017-02-17 09:45 | 32.8 | 35.8 | 0.1 | 31.3 | -0.95 | 1 | 1003.6 | 1.616 | 10.84 |  | 30 | 32.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K094 | 2017-02-17 09:35 | 45.6 | 38.8 | 0 | 15.6 | -13.56 | 13.6 | 1003.6 | 14.755 | 67.79 |  | 70 | 40.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K095 | 2017-02-17 09:33 | 46.2 | 37.6 | 2.1 | 14.1 | -47.95 | 48 | 1002.5 | 0.789 | 23.4 |  | 100 | 28.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K111 | 2017-02-17 09:27 | 7.7 | 6.4 | 20.4 | 65.5 | -3.43 | 3.4 | 1003.6 | -0.019 | -2.53 |  | 0 | 20.7 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K426 | 2017-02-17 09:23 | 29.2 | 34.7 | 0.6 | 35.5 | -2.52 | 2.5 | 1003 | 1.681 | 23.52 |  | 30 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K373 | 2017-02-17 09:21 | 49.6 | 40.1 | 0 | 10.3 | -8.97 | 9 | 1003.5 | 3.407 | 33.21 |  | 50 | 32.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K374 | 2017-02-17 09:18 | 45.7 | 38.5 | 0.3 | 15.5 | -6.18 | 6.2 | 1003.3 | 4.562 | 38.21 |  | 50 | 36.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K427 | 2017-02-17 09:16 | 34.2 | 35.7 | 0.3 | 29.8 | -2.53 | 2.5 | 1003.5 | 0.196 | 8.08 |  | 20 | 26.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K428 | 2017-02-17 09:14 | 50.2 | 38.2 | 0.1 | 11.5 | -1.65 | 1.7 | 1002.5 | 11.122 | 28.11 |  | 30 | 37.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K372 | 2017-02-17 09:12 | 51.1 | 40.3 | 0.4 | 8.2 | -10 | 10 | 1003.3 | 5.408 | 41.42 |  | 50 | 37.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K375 | 2017-02-17 09:10 | 34.3 | 36.8 | 0 | 28.9 | -1.69 | 1.7 | 1003.3 | 0.985 | 17.93 |  | 30 | 32.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section K | BGW2K429 | 2017-02-17 09:09 | 42 | 37.8 | 0.2 | 20 | -6.56 | 6.6 | 1003.3 | 12.453 | 29.95 |  | 30 | 31.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J400 | 2017-02-17 08:57 | 52.1 | 40.5 | 0.7 | 6.7 | -8.47 | 8.5 | 1002.4 | 4.165 | 17.15 |  | 30 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J430 | 2017-02-17 08:55 | 12.1 | 14.7 | 18.1 | 55.1 | -42.69 | 42.7 | 1002.4 | 0.468 | 5.83 |  | 30 | 20.4 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J408 | 2017-02-17 08:51 | 54.3 | 40.5 | 0 | 5.2 | -13.35 | 13.4 | 1002.4 | 18.306 | 36.5 |  | 60 | 24.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J087 | 2017-02-17 08:48 | 40.7 | 37.5 | 2.2 | 19.6 | -2.75 | 2.8 | 1002.2 | 1.167 | 9.24 |  | 30 | 29.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J091 | 2017-02-17 08:46 | 52.3 | 39.3 | 0.4 | 8 | -4.39 | 4.4 | 1002.4 | 2.674 | 43.72 |  | 50 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J401 | 2017-02-17 08:44 | 57.1 | 38.4 | 0.6 | 3.9 | -38.69 | 38.7 | 1002.2 | 1.896 | 11.66 |  | 50 | 24.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J089 | 2017-02-17 08:41 | 18.8 | 32.5 | 1.6 | 47.1 | -0.79 | 0.8 | 1002.2 | 3.849 | 16.73 |  | 30 | 31.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section J | BGW2J090 | 2017-02-17 08:38 | 50.1 | 38.1 | 1.6 | 10.2 | -5.89 | 5.9 | 1002.4 | 7.123 | 22.62 |  | 40 | 33.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M397 | 2017-02-17 08:25 | 46.8 | 39.6 | 0.1 | 13.5 | -38.69 | 38.7 | 1000.9 | 8.917 | 24.51 |  | 60 | 41.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M124 | 2017-02-17 08:24 | 46 | 36.9 | 1 | 16.1 | -12 | 12 | 1001.1 | 2.447 | 27.67 |  | 30 | 41.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M381 | 2017-02-16 15:02 | 46.3 | 42.6 | 0 | 11.1 | -18.72 | 18.7 | 1001.1 | 17.433 | 34.39 |  | 30 | 44.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M450 | 2017-02-16 15:01 | 54.4 | 42 | 0.8 | 2.8 | -2.97 | 3 | 1000.9 | 2.88 | 3.58 |  | 20 | 30.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M435 | 2017-02-16 14:59 | 0.5 | 3.4 | 19.4 | 76.7 | -1.05 | 1.1 | 1000.9 | 0.01 | 0.21 |  | 0 | 27.9 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M432 | 2017-02-16 14:57 | 50.6 | 42.6 | 0.6 | 6.2 | -0.69 | 0.7 | 1001.1 | 3.511 | 3.97 |  | 20 | 28.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M131 | 2017-02-16 14:55 | 35.4 | 39.7 | 0.1 | 24.8 | -1.49 | 1.5 | 1001.1 | 1.865 | 24.54 |  | 40 | 35 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M434 | 2017-02-16 14:54 | 37.9 | 39.4 | 0.5 | 22.2 | -2.97 | 3 | 1001.4 | 20.903 | 38.3 |  | 50 | 38.4 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M083 | 2017-02-16 14:52 | 52.5 | 42.8 | 0.1 | 4.6 | -41.01 | 41 | 1001.1 | 2.578 | 41.82 |  | 50 | 37.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section M | BGW2M128 | 2017-02-16 14:50 | 28.2 | 28.9 | 9.9 | 33 | 0.58 | -0.6 | 1001.1 | -0.018 | -1.16 |  | 0 | 28 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BGW2F358 | 2017-02-16 14:23 | 56 | 43.7 | 0 | 0.3 | 0.05 | -0.1 | 1002.4 | 0.219 | 4 |  | 20 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section F | BHW2F416 | 2017-02-16 14:20 | 51.8 | 43.1 | 0.1 | 5 | -22.19 | 22.2 | 1002.2 | 29.103 | 94.93 |  | 70 | 36.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L378 | 2017-02-16 14:14 | 54.8 | 41.1 | 0 | 4.1 | -0.49 | 0.5 | 1001.3 | 6.76 | 21.54 |  | 30 | 49.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L431 | 2017-02-16 14:12 | 57.3 | 42.5 | 0 | 0.2 | -3.02 | 3 | 1001.1 | 3.587 | 49.47 |  | 50 | 47.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L133 | 2017-02-16 14:10 | 51.5 | 42.8 | 0 | 5.7 | -0.47 | 0.5 | 1001.1 | 9.826 | 12.73 |  | 30 | 41.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L134 | 2017-02-16 14:08 | 47.4 | 40.9 | 0 | 11.7 | -1.43 | 1.4 | 1000.9 | 1.556 | 22.29 |  | 40 | 38.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L380 | 2017-02-16 14:07 | 51.8 | 43.5 | 0.1 | 4.6 | 0.11 | -0.1 | 1000.9 | 0.06 | 0.19 |  | 0 | 27.4 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L137 | 2017-02-16 14:05 | 51.6 | 42.3 | 0.2 | 5.9 | -15.35 | 15.4 | 1000.9 | 2.639 | 42.01 |  | 50 | 50 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L359 | 2017-02-16 14:03 | 46.5 | 40.3 | 0.5 | 12.7 | -4.21 | 4.2 | 1002.1 | 6.65 | 45.55 |  | 50 | 44.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L420 | 2017-02-16 14:00 | 49.1 | 41.9 | 0.2 | 8.8 | -1.25 | 1.3 | 1001.1 | 2.587 | 13.77 |  | 30 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L377 | 2017-02-16 13:59 | 47.4 | 41.9 | 0.1 | 10.6 | -0.37 | 0.4 | 1001.4 | 2.794 | 14.05 |  | 30 | 40.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L140 | 2017-02-16 13:57 | 53.2 | 44 | 0 | 2.8 | -34.17 | 34.2 | 1001.1 | 4.12 | 4.18 |  | 100 | 34 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T219 | 2017-02-16 13:41 | 55.8 | 40.7 | 0.4 | 3.1 | -3.43 | 3.4 | 1003.5 | 0.317 | 10.17 |  | 30 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T220 | 2017-02-16 13:38 | 20.3 | 21.6 | 11.5 | 46.6 | 0.02 | 0 | 1003.6 | -0.007 | -1.51 |  | 0 | 26.1 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T224 | 2017-02-16 13:34 | 54.8 | 42.7 | 0.6 | 1.9 | -43.21 | 43.2 | 1003.6 | 3.253 | 15.31 |  | 50 | 21.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T228 | 2017-02-16 13:32 | 53 | 42.8 | 0.1 | 4.1 | -41.53 | 41.5 | 1003.6 | 0.458 | 17.87 |  | 100 | 29.7 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T438 | 2017-02-16 13:30 | 54.8 | 42.1 | 0 | 3.1 | -1.08 | 1.1 | 1003.6 | 2.54 | 13.58 |  | 20 | 32.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T339 | 2017-02-16 13:27 | 54.4 | 42 | 0 | 3.6 | -8.59 | 8.6 | 1003.8 | 1.266 | 20.17 |  | 40 | 35.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T387 | 2017-02-16 13:25 | 58.1 | 39.3 | 0.1 | 2.5 | -0.43 | 0.4 | 1003.6 | 0.177 | 7.52 |  | 20 | 39.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T229 | 2017-02-16 13:23 | 31.6 | 27.2 | 9.2 | 32 | -17.03 | 17 | 1003.6 | 0.058 | 2.05 |  | 10 | 27.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T230 | 2017-02-16 13:20 | 6.7 | 8.2 | 18 | 67.1 | -50.05 | 50.1 | 1003.6 | 1.761 | 11.17 |  | 50 | 25 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T235 | 2017-02-16 13:18 | 55.1 | 41.6 | 0.8 | 2.5 | -0.89 | 0.9 | 1003.6 | 0.272 | 2.16 |  | 10 | 32.8 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section T | BGW2T234 | 2017-02-16 13:16 | 56.4 | 42.4 | 0 | 1.2 | 0.21 | -0.2 | 1003.8 | 1.334 | 9.8 |  | 30 | 36.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q168 | 2017-02-16 13:07 | 56.6 | 42.1 | 0 | 1.3 | -31.44 | 31.4 | 1004.3 | 0.707 | 15.07 |  | 30 | 28.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q444 | 2017-02-16 13:05 | 56 | 40.3 | 0.1 | 3.6 | -2.06 | 2.1 | 1004.7 | 2.411 | 13.21 |  | 30 | 33.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q337 | 2017-02-16 13:03 | 54.8 | 41.6 | 0 | 3.6 | -0.18 | 0.2 | 1004.9 | 6.803 | 5.53 |  | 20 | 28 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q338 | 2017-02-16 13:02 | 57.1 | 41.9 | 0 | 1 | -1.39 | 1.4 | 1004.7 | 0.636 | 14.49 |  | 30 | 29.4 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q214 | 2017-02-16 12:58 | 57.9 | 41.9 | 0 | 0.2 | -3.64 | 3.6 | 1004.6 | 0.738 | 15.5 |  | 30 | 33 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q203 | 2017-02-16 12:56 | 57.5 | 41.9 | 0 | 0.6 | -39.85 | 39.9 | 1004.7 | 4.163 | 35.83 |  | 100 | 37.9 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q382 | 2017-02-16 12:55 | 55.1 | 41.7 | 0 | 3.2 | -1.33 | 1.3 | 1004.6 | 10.111 | 26.92 |  | 30 | 35.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q184 | 2017-02-16 12:53 | 50.7 | 40.1 | 0.4 | 8.8 | -26.81 | 26.8 | 1004.7 | 5.677 | 41.79 |  | 70 | 42.5 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q189 | 2017-02-16 12:51 | 48.3 | 39.6 | 0 | 12.1 | 1.03 | -1 | 1004.7 | 8.835 | 25.18 |  | 50 | 36.1 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q204 | 2017-02-16 12:50 | 55.2 | 41.8 | 0 | 3 | -7.35 | 7.4 | 1004.7 | 0.16 | 3.41 |  | 20 | 30 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q336 | 2017-02-16 12:48 | 31.2 | 34.3 | 1.5 | 33 | -0.24 | 0.2 | 1004.3 | 0.002 | 0.33 |  | 0 | 29.7 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q335 | 2017-02-16 12:44 | 51.5 | 39 | 0 | 9.5 | -4.15 | 4.2 | 1004.7 | 2.832 | 30.36 |  | 40 | 32.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q179 | 2017-02-16 12:42 | 38.2 | 33.4 | 3.9 | 24.5 | -5.67 | 5.7 | 1004.7 | 0.615 | 3.27 |  | 10 | 27.8 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q175 | 2017-02-16 12:39 | 3.5 | 16 | 14.6 | 65.9 | -0.27 | 0.3 | 1004.4 | 0.001 | 0.43 |  | 0 | 29.4 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q209 | 2017-02-16 12:36 | 57.7 | 40.6 | 0.2 | 1.5 | -45.21 | 45.2 | 1004.7 | 2.857 | 29.9 |  | 100 | 31.9 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q185 | 2017-02-16 12:34 | 61.2 | 38.1 | 0 | 0.7 | 0 | 0 | 1004.6 | 0 | 0 |  | 0 | 28.9 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q180 | 2017-02-16 12:31 | 55.5 | 36.7 | 0 | 7.8 | -0.95 | 1 | 1004.4 | 0.376 | 2.56 |  | 20 | 26.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q190 | 2017-02-16 12:30 | 50.3 | 38.6 | 0.1 | 11 | -11.76 | 11.8 | 1004.9 | 3.303 | 32.75 |  | 50 | 30.9 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Q | BGW2Q199 | 2017-02-16 12:28 | 55.5 | 39.3 | 0.1 | 5.1 | -0.02 | 0 | 1004.9 | -0.002 | -0.33 |  | 0 | 31.5 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L417 | 2017-02-16 09:30 | 56.9 | 40.3 | 0 | 2.8 | -2.74 | 2.7 | 1002.5 | 4.475 | 38.03 |  | 50 | 34.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L056 | 2017-02-16 09:28 | 33.1 | 39.2 | 0 | 27.7 | -1.26 | 1.3 | 1003.5 | 1.775 | 24.19 |  | 30 | 29.6 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L082 | 2017-02-16 09:26 | 56.5 | 41.5 | 0 | 2 | -11.41 | 11.4 | 1003.5 | 8.157 | 24.31 |  | 30 | 29.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L053 | 2017-02-16 09:24 | 52.7 | 41.8 | 0 | 5.5 | -2.66 | 2.7 | 1003.5 | 0.023 | 4.14 |  | 10 | 26.5 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L433 | 2017-02-16 09:21 | 53.4 | 41.8 | 0 | 4.8 | -3.74 | 3.7 | 1003.5 | 2.236 | 12.84 |  | 20 | 27.1 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L376 | 2017-02-16 09:19 | 40.3 | 39.3 | 0 | 20.4 | -6.97 | 7 | 1003.5 | 5.767 | 42.67 |  | 40 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L150 | 2017-02-16 09:17 | 53.7 | 41.5 | 0 | 4.8 | -35.43 | 35.4 | 1003.5 | 12.65 | 92.02 |  | 80 | 41.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section L | BGW2L448 | 2017-02-16 09:15 | 57.3 | 41 | 0 | 1.7 | -2.88 | 2.9 | 1003.6 | 6.62 | 22.21 |  | 30 | 23.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G421 | 2017-02-16 09:03 | 54.1 | 40.1 | 0.2 | 5.6 | -7.68 | 7.7 | 1004.9 | 16.77 | 34.71 |  | 30 | 31.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G419 | 2017-02-16 09:01 | 48.5 | 39.5 | 0.3 | 11.7 | -15.98 | 16 | 1004.4 | 72.275 | 69.98 |  | 90 | 36 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G054 | 2017-02-16 08:59 | 50 | 40 | 0.9 | 9.1 | -74.13 | 74.1 | 1003.9 | 0.325 | 9.88 |  | 50 | 35.3 | Blocked- Investigation Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G418 | 2017-02-16 08:57 | 42.7 | 37.4 | 1.9 | 18 | -2.29 | 2.3 | 1004.7 | 3.471 | 15.92 |  | 30 | 30.9 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section G | BGW2G052 | 2017-02-16 08:55 | 42.3 | 36.2 | 2.2 | 19.3 | -3.77 | 3.8 | 1004.9 | 4.086 | 8.35 |  | 30 | 32.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E356 | 2017-02-16 08:31 | 56.4 | 39.6 | 0.4 | 3.6 | -8.99 | 9 | 1004.9 | 14.554 | 32.32 |  | 50 | 31.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E357 | 2017-02-16 08:29 | 52.1 | 38.8 | 1.3 | 7.8 | -5.09 | 5.1 | 1004.9 | 13.434 | 31.01 |  | 50 | 34.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section E | BGW2E395 | 2017-02-16 08:27 | 51.2 | 38.1 | 0.4 | 10.3 | -17.35 | 17.4 | 1003.8 | 12.123 | 29.37 |  | 40 | 32 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A350 | 2017-02-15 14:38 | 55.7 | 44.1 | 0 | 0.2 | 2.82 | -2.8 | 1003.6 | 2.331 | 27.29 |  | 100 | 40.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A349 | 2017-02-15 14:36 | 55.5 | 43.7 | 0 | 0.8 | -3.89 | 3.9 | 1004.6 | 1.341 | 9.89 |  | 100 | 30.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A348 | 2017-02-15 14:34 | 55.3 | 44 | 0 | 0.7 | 2.35 | -2.4 | 1003.6 | 1.594 | 22.5 |  | 70 | 42.3 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section A | BHW2A347 | 2017-02-15 14:33 | 55.6 | 44.3 | 0 | 0.1 | 2.31 | -2.3 | 1004.4 | 3.958 | 16.78 |  | 100 | 40.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z346 | 2017-02-15 14:26 | 57.1 | 42.2 | 0 | 0.7 | 0.09 | -0.1 | 1004.7 | 0.325 | 4.84 |  | 50 | 35.5 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z345 | 2017-02-15 14:23 | 52.6 | 41.5 | 0.2 | 5.7 | 0.06 | -0.1 | 1004.3 | 0.472 | 5.81 |  | 50 | 38.1 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z344 | 2017-02-15 14:21 | 53.5 | 41 | 0.7 | 4.8 | 0.11 | -0.1 | 1004.4 | 0.347 | 5.01 |  | 50 | 34.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z343 | 2017-02-15 14:18 | 57.3 | 42.2 | 0.1 | 0.4 | 0.25 | -0.3 | 1004.7 | 1.05 | 8.69 |  | 50 | 36.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z342 | 2017-02-15 14:14 | 49.1 | 40 | 0.3 | 10.6 | -0.27 | 0.3 | 1004.7 | 1.216 | 9.37 |  | 30 | 35.2 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z341 | 2017-02-15 14:10 | 47.5 | 39.1 | 0.1 | 13.3 | -0.01 | 0 | 1004.3 | 0.359 | 5.08 |  | 30 | 36.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z479 | 2017-02-15 14:06 | 46 | 38.7 | 0.2 | 15.1 | -0.41 | 0.4 | 1005.2 | 0.812 | 7.7 |  | 100 | 32.3 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z317 | 2017-02-15 13:58 | 54.7 | 42 | 0 | 3.3 | -2.83 | 2.8 | 1003.8 | 10.525 | 58.11 |  | 50 | 35.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z306 | 2017-02-15 13:56 | 51.1 | 40.8 | 0 | 8.1 | -3.86 | 3.9 | 1003.6 | 13.243 | 30.84 |  | 40 | 33.1 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z310 | 2017-02-15 13:54 | 51.9 | 41.7 | 0 | 6.4 | -6.45 | 6.5 | 1003.5 | 13.735 | 66.03 |  | 50 | 37.1 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z314 | 2017-02-15 13:53 | 49.2 | 42 | 0 | 8.8 | -0.69 | 0.7 | 1003.6 | 6.843 | 22.06 |  | 30 | 38.4 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z313 | 2017-02-15 13:51 | 55.3 | 41 | 0 | 3.7 | -2.4 | 2.4 | 1003.6 | 2.829 | 14.34 |  | 40 | 31.9 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z320 | 2017-02-15 13:49 | 58.1 | 41.3 | 0 | 0.6 | -24.6 | 24.6 | 1003.5 | 11.273 | 28.31 |  | 100 | 30.2 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z324 | 2017-02-15 13:47 | 58 | 41.8 | 0 | 0.2 | 0.02 | 0 | 1003.6 | 1.394 | 10.07 |  | 40 | 32.8 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z327 | 2017-02-15 13:45 | 56.7 | 41.7 | 0 | 1.6 | -31.96 | 32 | 1003.5 | 7.988 | 50.23 |  | 100 | 31.7 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z321 | 2017-02-15 13:43 | 54.8 | 41.8 | 0 | 3.4 | -0.3 | 0.3 | 1003.5 | 2.375 | 13.02 |  | 30 | 38.5 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z331 | 2017-02-15 13:41 | 52.4 | 41.2 | 0 | 6.4 | -0.31 | 0.3 | 1003.6 | 5.771 | 9.94 |  | 30 | 31.7 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 2 - Section Z | BGW2Z328 | 2017-02-15 13:40 | 50.8 | 41.7 | 0 | 7.5 | -2.13 | 2.1 | 1003.6 | 14.877 | 32.52 |  | 40 | 36.6 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B012 | 2017-02-15 11:55 | 48 | 38.1 | 0.1 | 13.8 | -75.7 | 75.7 | 1004.7 | 1.601 | 10.5 |  | 50 | 26 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B014 | 2017-02-15 11:54 | 54.8 | 37.3 | 0.1 | 7.8 | -4.5 | 4.5 | 1004.9 | -0.091 | -0.23 |  | 0 | 23.8 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B020 | 2017-02-15 11:52 | 34.9 | 30.6 | 8.3 | 26.2 | -81.8 | 81.8 | 1004.3 | 2.217 | 12.23 |  | 70 | 30 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B015 | 2017-02-15 11:49 | 55 | 38.2 | 0.1 | 6.7 | -67.29 | 67.3 | 1004.9 | 17.989 | 8.65 |  | 100 | 28.2 | Orifice Plate Change Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B013 | 2017-02-15 11:47 | 55.4 | 36.5 | 0.1 | 8 | -1.48 | 1.5 | 1004.7 | 0 | 0 |  | 10 | 28.4 | Adjusted Increase
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B016 | 2017-02-15 11:42 | 40.4 | 37.5 | 0 | 22.1 | -33.86 | 33.9 | 1004.7 | 0.094 | 2.6 |  | 20 | 28.5 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B019 | 2017-02-15 11:40 | 50.7 | 38.9 | 0 | 10.4 | -65.51 | 65.5 | 1004.9 | 1.099 | 2.15 |  | 30 | 28.7 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B010 | 2017-02-15 11:39 | 50.6 | 38.9 | 0 | 10.5 | -80.23 | 80.2 | 1004.9 | 1.82 | 23.59 |  | 100 | 28 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B017 | 2017-02-15 11:36 | 47.8 | 37.1 | 0 | 15.1 | -9.76 | 9.8 | 1004.9 | 8.72 | 6.24 |  | 30 | 27.2 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section B | BGW1B018 | 2017-02-15 11:35 | 48.1 | 36.7 | 0.1 | 15.1 | -39.53 | 39.5 | 1004.9 | 0.691 | 7.01 |  | 30 | 27.9 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A006 | 2017-02-15 11:28 | 30.9 | 25.2 | 9.7 | 34.2 | -84.96 | 85 | 1006 | 0.51 | 5.87 |  | 20 | 29 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A007 | 2017-02-15 11:26 | 3.4 | 6 | 20 | 70.6 | -0.09 | 0.1 | 1005.2 | -0.072 | -0.2 |  | 0 | 29.7 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A008 | 2017-02-15 11:24 | 47.3 | 38.7 | 0 | 14 | -17.66 | 17.7 | 1004.9 | 3.418 | 15.71 |  | 30 | 29.4 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1AM01 | 2017-02-15 11:23 | 22.9 | 31.7 | 1.7 | 43.7 | -77.28 | 77.3 | 1004.7 | 1.159 | 8.91 |  | 50 | 26.9 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A001 | 2017-02-15 11:19 | 53.9 | 39.4 | 0.1 | 6.6 | -83.27 | 83.3 | 1004.9 | 2.054 | 11.82 |  | 100 | 27.1 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A268 | 2017-02-15 11:17 | 58.5 | 39.9 | 0 | 1.6 | 0.06 | -0.1 | 1004.9 | 0.005 | 0.15 |  | 10 | 29.6 | OK- No Action Required
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A009 | 2017-02-15 11:14 | 53.4 | 38.4 | 0 | 8.2 | -1.19 | 1.2 | 1006 | 0.008 | 0.75 |  | 20 | 27 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A269 | 2017-02-15 11:11 | 55.4 | 37.9 | 0.1 | 6.6 | -3.86 | 3.9 | 1005.1 | 0.125 | 0.27 |  | 0 | 23.2 | Shut - Shut
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A002 | 2017-02-15 11:08 | 24.1 | 23.1 | 12.5 | 40.3 | -82.43 | 82.4 | 1004.9 | 1.805 | 11.06 |  | 50 | 28.5 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A005 | 2017-02-15 11:06 | 30.2 | 28.1 | 11.2 | 30.5 | -84.96 | 85 | 1004.9 | 1.057 | 8.47 |  | 50 | 27.2 | Adjusted Decrease
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A003 | 2017-02-15 11:04 | 50 | 38 | 0 | 12 | -33.75 | 33.8 | 1004.9 | 0.744 | 7.31 |  | 30 | 26.9 | Surging
Melbourne Regional Landfill | Gas Extraction | Stage 1 - Section A | BGW1A004 | 2017-02-15 11:02 | 46.6 | 32.9 | 0.3 | 20.2 | -1.79 | 1.8 | 1006 | 0.88 | 8.07 |  | 20 | 27.7 | Surging

## Findings
|  | Before | [5 empty] | After | [11 empty] | Map Parameters | Diff | Before
After
|  | Well Station Control Valves | [19 empty] | Diff
ID | DATE | CH4 | CO2 | O2 | BALANCE | REL.PRESSURE |  |  | CH4 | CO2 | O2 | BALANCE | REL.PRESSURE |  | Differential | Selection
BRPOWER1 | 2018-09-07 10:10 | 49.9 | 37.5 | 0.6 | 12 | -159.25 |  |  | 52.5 | 38.4 | 0.2 | 8.9 | -156.55 |  | -2.7 | -2.7
BCV2Q002 | 2018-09-07 10:21 | 48.2 | 35.5 | 0.1 | 16.2 | -67.12 |  |  | 50.2 | 36.3 | 0 | 13.5 | -56.5 |  | -10.62 | -10.62
BCV2T002 | 2018-09-07 10:25 | 45.2 | 34.8 | 0.9 | 19.1 | -69.05 |  |  | 47.2 | 35.6 | 0.6 | 16.6 | -64.59 |  | -4.46 | -4.46
BCV2X001 | 2018-09-07 10:29 | 50.2 | 37.4 | 0.1 | 12.3 | -84.58 |  |  | 52.5 | 38.4 | 0 | 9.1 | -75.84 |  | -8.74 | -8.74
BCV2X002 | 2018-09-07 10:31 | 53.2 | 38.2 | 0.1 | 8.5 | -67.91 |  |  | 55.5 | 39.2 | 0 | 5.3 | -62.75 |  | -5.16 | -5.16
BCV2N001 | 2018-09-07 10:34 | 46.3 | 36.9 | 0 | 16.8 | -89.23 |  |  | 47.5 | 37.6 | 0 | 14.9 | -83.92 |  | -5.31 | -5.31
BCV2W001 | 2018-09-07 10:38 | 42.2 | 34.8 | 0.2 | 22.8 | -69.75 |  |  | 45.9 | 36.2 | 0 | 17.9 | -63.07 |  | -6.68 | -6.68
BCV2S001 | 2018-09-07 10:41 | 48.1 | 37 | 0.2 | 14.7 | -64.49 |  |  | 50.6 | 37.7 | 0.1 | 11.6 | -58.23 |  | -6.26 | -6.26
BCV2R002 | 2018-09-07 10:44 | 46.8 | 36.3 | 0.7 | 16.2 | -63.92 |  |  | 50.2 | 38.2 | 0 | 11.6 | -58.04 |  | -5.88 | -5.88
BCV2P003 | 2018-09-07 10:49 | 56.7 | 38.3 | 0.1 | 4.9 | -63.79 |  |  | 59.1 | 38.9 | 0 | 2 | -57.99 |  | -5.8 | -5.8
BCV2Z002 | 2018-09-07 10:53 | 51.1 | 37.1 | 0 | 11.8 | -61.25 |  |  | 50.3 | 37.2 | 0 | 12.5 | -56.15 |  | -5.1 | -5.1
BCV2Y002 | 2018-09-07 10:56 | 55.2 | 39.9 | 0 | 4.9 | -61.2 |  |  | 56.4 | 40.5 | 0 | 3.1 | -56.22 |  | -4.98 | -4.98
BCV2U002 | 2018-09-07 11:00 | 49.3 | 37.9 | 1.4 | 11.4 | -63.86 |  |  | 50.2 | 38.6 | 1 | 10.2 | -58.61 |  | -5.25 | -5.25
BCV2V001 | 2018-09-07 11:04 | 54 | 40.2 | 0 | 5.8 | -69.21 |  |  | 54 | 40.5 | 0.3 | 5.2 | -63.65 |  | -5.56 | -5.56
BCV2F001 | 2018-09-07 11:08 | 49.1 | 37.6 | 0 | 13.3 | -95.55 |  |  | 53.7 | 38.9 | 0 | 7.4 | -91.74 |  | -3.81 | -3.81
BCV2C001 | 2018-09-07 11:13 | 59.4 | 44 | 0 | 0 | -76.95 |  |  | 58.2 | 44.2 | 0 | 0 | -68.54 |  | -8.41 | -8.41
BCV2E001 | 2018-09-07 11:19 | 49.3 | 35.1 | 0.2 | 15.4 | -94.8 |  |  | 49.8 | 35.5 | 0.1 | 14.6 | -92.75 |  | -2.05 | -2.05
BCV2G002 | 2018-09-07 11:23 | 48.7 | 37.7 | 0.6 | 13 | -91.63 |  |  | 50.6 | 38.7 | 0.2 | 10.5 | -84.58 |  | -7.05 | -7.05
BCV2H002 | 2018-09-07 11:28 | 50.4 | 37.4 | 0.4 | 11.8 | -86.37 |  |  | 51.4 | 37.7 | 0.6 | 10.3 | -84.37 |  | -2 | -2
BCV2I001 | 2018-09-07 11:33 | 37.2 | 28.7 | 5 | 29.1 | -85.72 |  |  | 43.1 | 32.2 | 3.1 | 21.6 | -85.04 |  | -0.68 | -0.68
BCV2J002 | 2018-09-07 11:37 | 36 | 28.3 | 4.8 | 30.9 | -66.4 |  |  | 33.6 | 25.9 | 6.6 | 33.9 | -63.75 |  | -2.65 | -2.65
BCV2K002 | 2018-09-07 11:40 | 46.9 | 36.5 | 0.2 | 16.4 | -66.3 |  |  | 49.4 | 37.2 | 0 | 13.4 | -63.58 |  | -2.72 | -2.72
BCV2M001 | 2018-09-07 11:43 | 48.2 | 37.5 | 0.1 | 14.2 | -71.49 |  |  | 49.7 | 37.9 | 0.1 | 12.3 | -67.89 |  | -3.6 | -3.6
BCV2L002 | 2018-09-07 11:46 | 41.2 | 32.7 | 2.8 | 23.3 | -70.3 |  |  | 42 | 32.8 | 2.8 | 22.4 | -64.62 |  | -5.68 | -5.68
| Ave CH4 | 48.45 |  |  | Ave Vac | -77.505 |  | Ave CH4 | 50.15 |  |  | Ave Vac | -72.4571
|  | Before | [5 empty] | After
Headers
ID | DATE | CH4 | CO2 | O2 | BALANCE | REL.PRESSURE |  |  | CH4 | CO2 | O2 | BALANCE | REL.PRESSURE |  | Differential
BMHSAM02 | 2018-09-07 09:48 | 50 | 37 | 0.8 | 15.2 | -102.49 |  |  | 52.5 | 26.6 | 1 | 12.1 | -100.62 |  | -1.87 | -1.87
BMHSAM016 | 2018-09-07 09:50 | 49.6 | 37 | 0.8 | 15.6 | -96.53 |  |  | 52.1 | 38 | 0.5 | 12.4 | -93.36 |  | -3.17 | -3.17
BMHSAM03 | 2018-09-07 09:53 | 50.4 | 37.1 | 0.5 | 15 | -95.63 |  |  | 52.3 | 37.6 | 0.4 | 12.7 | -93.16 |  | -2.47 | -2.47
BMHSAM04 | 2018-09-07 09:55 | 54.4 | 40.5 | 0.1 | 8 | -93.99 |  |  | 55.5 | 40.7 | 0.1 | 6.7 | -89.6 |  | -4.39 | -4.39
BMHSAM05 | 2018-09-07 09:58 | 49.6 | 36.1 | 0.5 | 16.8 | -95.59 |  |  | 51.2 | 36.8 | 0.4 | 14.6 | -91.43 |  | -4.16 | -4.16
BMHSAM06 | 2018-09-07 10:04 | 45.6 | 34.7 | 1.3 | 21.4 | -88.12 |  |  | 48.3 | 36 | 1 | 17.7 | -83.44 |  | -4.68 | -4.68
BMHSAM07 | 2018-09-07 10:06 | 39.1 | 29.7 | 2.9 | 31.3 | -86.72 |  |  | 42.2 | 31.2 | 2.7 | 26.9 | -83.56 |  | -3.16 | -3.16
BMHSAM08 | 2018-09-07 10:11 | 45.5 | 35 | 0.8 | 21.7 | -74.62 |  |  | 48.3 | 36.6 | 0.6 | 17.5 | -70.29 |  | -4.33 | -4.33
BMHSAM09 | 2018-09-07 10:16 | 52 | 36.2 | 0.6 | 14.2 | -69.97 |  |  | 53.5 | 37.1 | 0.4 | 12 | -65.58 |  | -4.39 | -4.39
BMHSAM15 | 2018-09-07 10:19 | 52.4 | 36.4 | 0.7 | 13.5 | -69.65 |  |  | 53.5 | 37.2 | 0.6 | 11.7 | -65.74 |  | -3.91 | -3.91
BMHSAM10 | 2018-09-07 10:24 | 49.1 | 34.9 | 0.9 | 18.1 | -67.45 |  |  | 49.7 | 35.2 | 0.9 | 17.2 | -63.64 |  | -3.81 | -3.81
BMHSAM11 | 2018-09-07 10:31 | 52.9 | 38.8 | 0.2 | 11.1 | -64.51 |  |  | 53.5 | 37.3 | 0.5 | 11.7 | -59.8 |  | -4.71 | -4.71
BMHSAM12 | 2018-09-07 10:37 | 51.6 | 38.3 | 0.2 | 12.9 | -62.64 |  |  | 52.2 | 38.4 | 0.1 | 12.3 | -58.74 |  | -3.9 | -3.9
BMHSAM13 | 2018-09-07 10:41 | 55.6 | 40 | 0.2 | 7.2 | -62.71 |  |  | 55.9 | 39.9 | 0.3 | 6.9 | -58.49 |  | -4.22 | -4.22
BMHSAM14 | 2018-09-07 10:51 | 49.2 | 36 | 0.5 | 17.3 | -92.15 |  |  | 49.9 | 36 | 0.5 | 16.6 | -84.85 | Surge | -7.3 | -7.3
| Ave CH4 | 49.8 |  |  | Ave Vac | -81.518 |  | Ave CH4 | 51.3733 |  |  | Ave Vac | -77.4867
|  | Before | [5 empty] | After
Surging Flowlines
ID | DATE | CH4 | CO2 | O2 | BALANCE | ADJ-SP | ADJ-DP | ADJ-FLOW | ANSWER 2 | CHOSEN 1 |  | CH4 | CO2 | O2 | BALANCE | ADJ-SP | ADJ-DP | ADJ-FLOW | ANSWER 2 | CHOSEN 1
BGW2G054 | 2018-09-04 10:41 | 48.5 | 36.8 | 0.8 | 13.9 | -71.9 | 10.896 | 58.3 | 0 | Open/Shut |  | 54.7 | 38.5 | 0.7 | 6.1 | -57.1 | 14.959 | 69.6 | 80 | OK- No Action Required
BGW2H059 | 2018-09-04 10:46 | 51.1 | 38.4 | 0 | 10.5 | -0.2 | 1.024 | 8.9 | 0 | Open/Shut |  | 59 | 40.5 | 0 | 0.5 | -0.6 | 1.216 | 9.8 | 15 | OK- No Action Required
BGW2L137 | 2018-09-04 10:49 | 48.6 | 37.2 | 0.2 | 14 | -26.6 | 1.656 | 39.5 | 0 | Open/Shut |  | 55.3 | 38.9 | 0.1 | 5.7 | -22 | 2.084 | 44.8 | 40 | OK- No Action Required
BGW2L417 | 2018-09-04 10:51 | 52.5 | 36.1 | 2.2 | 9.2 | -1.6 | 1.756 | 25.6 | 0 | Open/Shut |  | 61.1 | 40.6 | 0 | 0 | -3.7 | 1.956 | 27.2 | 25 | Surge
BGW2N146 | 2018-09-04 10:59 | 48.1 | 37.6 | 0 | 14.3 | -72.7 | 1.874 | 25.1 | 0 | Open/Shut |  | 49.2 | 37.7 | 0.1 | 13 | -50.3 | 3.672 | 35.4 | 40 | OK- No Action Required
BGW2W256 | 2018-09-04 11:02 | 48.1 | 35.3 | 3 | 13.6 | -42.2 | 1.55 | 37.2 | 0 | Open/Shut |  | 52.3 | 37.7 | 1.9 | 8.1 | -35.1 | 3.11 | 53.6 | 40 | Surge
BGW2X254 | 2018-09-04 11:06 | 50.7 | 36.5 | 0 | 12.8 | -21.5 | -0.031 | 0 | 0 | Open/Shut |  | 51.2 | 36.4 | 0 | 12.4 | -22.5 | 0.484 | 12.9 | 15 | OK- No Action Required
BGW2X443 | 2018-09-04 11:10 | 47.2 | 36.6 | 0 | 16.2 | -24.5 | 7.681 | 23.6 | 0 | Open/Shut |  | 51.7 | 38.2 | 0 | 10.1 | -28.1 | 4.773 | 18.7 | 40 | Surge
BGW2Q338 | 2018-09-04 11:16 | 24.3 | 23.2 | 3.1 | 49.4 | -41.3 | 0.312 | 10.4 | 0 | Open/Shut |  | 27.9 | 24.8 | 2.7 | 44.6 | -35.5 | 0.271 | 9.7 | 10 | Adjusted Decrease
BGW2S385 | 2018-09-04 11:32 | 49.3 | 36.7 | 0 | 14 | -32.9 | 9.921 | 58.8 | 0 | Shut/Open |  | 56.1 | 39.1 | 0 | 4.8 | -19.1 | 11.728 | 65.1 | 50 | Surge
BGW2U251 | 2018-09-04 11:35 | 53.7 | 40.5 | 0 | 5.8 | -64.1 | 2.728 | 29.6 | 0 | Open/Shut |  | 54.6 | 41 | 0 | 4.4 | -54 | 12.729 | 64.1 | 99 | OK- No Action Required
BGW2U245 | 2018-09-04 11:37 | 46.8 | 35.5 | 2 | 15.7 | -30.5 | 4.496 | 38.5 | 0 | 0 |  | 48.9 | 36.5 | 1.6 | 13 | -19.4 | 7.753 | 51 | 50 | Surge
BGW2U399 | 2018-09-04 11:39 | 39.5 | 29.3 | 5.8 | 25.4 | -25.6 | 11.96 | 62.5 | 0 | Open/Shut |  | 46 | 32.9 | 3.7 | 17.4 | -26.2 | 6.283 | 45.5 | 45 | Surge
| Ave CH4 | 46.8 |  |  |  |  | Total Flow | 418 |  |  | Ave CH4 | 51.3846 |  |  |  |  | Total Flow | 507.4
KOP ID | DATE | BEFORE | AFTER | DIFF | Est Ltrs
KOP 2 | 2018-09-07 | 116112 | 116129 | 17 | 102
KOP 3 | 2018-09-07 | 24873 | 24887 | 14 | 84
KOP 4 | 2018-09-07 | 101637 | 101645 | 8 | 48
KOP 5 | 2018-09-07 | 8178 | 8190 | 12 | 72
KOP 6 | 2018-09-07 | 14166 | 14176 | 10 | 60
KOP 7 | 2018-09-07 | 46375 | 46384 | 9 | 54
KOP 8 | 2018-09-07 | 11006 | 11017 | 11 | 66
KOP 9 | 2018-09-07 | 13286 | 13298 | 12 | 72
KOP 10 | 2018-09-07 | 3078 | 3086 | 8 | 48
KOP 11 | 2018-09-07 | 5278 | 5286 | 8 | 48
-3
-2
-8
-4
-2
-3
-3
-5
-5
-4
-7
-5
-4
-11
-5
-5
-2
-2
-3
-4
-4
-5
-3
-4
-4
-4
-7
-5
-4
-4